## PROTOTYPE_FIELDS
{Note} | Default values for prototypes. Blank fields will not be included when given prototype dbf is generated.
Field | FRQ_REVH | POINTIO_1DI_LOOP24VDC2 | Column1 | Column2
PREFIX | ##PREFIX## | ##PREFIX##
DRAWING | ##DRAWING## | ##DRAWING##
PROTOTYPE | S:\Elecdes\prototypes\gen6\MOTORS\FRQ_REVH | S:\Elecdes\prototypes\gen6\INSTRUMENTATION\FRQ_REVH
W1NAME |  | ##W1NAME##
W2NAME |  | ##W2NAME##
X1NAME | ##X1NAME## | ##X1NAME##
X1DESC | ##X1DESC## | ##X1DESC##
X1VDC24
X1VDC0
X1XIO
X1XIOF
X1XIOK
X1V230 | ##X1V230##
X1N230 | ##X1N230##
X1XDB
X1XDBF
X1XDBK
X1XDBQ | ##X1XDBQ##
Q1CATN | ##Q1CATN##
Q1CATD | ##Q1CATD##
Q1NAME1 | ##Q1NAME1##
Q1NAME2 | ##Q1NAME2##
Q1TCATN | ##Q1TCATN##
Q1TCATD | ##Q1TCATD##
Q1TNAME | ##Q1TNAME##
Q1TSETTO | ##Q1TSETTO##
P1NAME | ##P1NAME## | ##P1NAME##
P1RACK | ##P1RACK## | ##P1RACK##
P1SLOT | ##P1SLOT## | ##P1SLOT##
P1CHAN | ##P1CHAN## | ##P1CHAN##
P1MFG | 2 | 2
P1CATN | ##P1CATN## | ##P1CATN##
P1CATD | ##P1CATD## | ##P1CATD##
P1CATD2 | ##P1CATD2## | ##P1CATD2##
P1TAG | ##P1TAG## | ##P1TAG##
P1DESC2 | ##P1DESC2## | ##P1DESC2##
P1DESC3 | ##P1DESC3## | ##P1DESC3##
P1DESC4 | ##P1DESC4## | ##P1DESC4##
P1T1 | ##P1T1## | ##P1T1##
P1T2 | ##P1T2## | ##P1T2##
P1T1TYPE | ##P1T1TYPE## | ##P1T1TYPE##
P1T2TYPE | ##P1T2TYPE## | ##P1T2TYPE##
D1TAG | ##D1TAG## | ##D1TAG##
D1DESC2 | ##D1DESC2## | ##D1DESC2##
D1DESC3 | ##D1DESC3## | ##D1DESC3##
D1DESC4 | ##D1DESC4## | ##D1DESC4##
D1TYPE |  | ##D1TYPE##
D1T1 |  | +
D1T2 |  | -
C1CATN | 1P-2C-F-1 | 1P-2C-F-1
C1CATD | PVC90 2 Core Flex 1mm^2 | PVC90 2 Core Flex 1mm^2
C1TAG | ##C1TAG## | ##C1TAG##
C1CORE1 | RD | BN
C1CORE2 | WH | BU
C1CORE3 | BU
C1CORE4 | BK
C1CORE5 | GN/YL
C2CATN
C2CATD
C2TAG | ##C2TAG##
C2CORE1 | RD
C2CORE2 | WH
C2CORE3 | BU
C2CORE4 | BK
C2CORE5 | GN/YL
C3CATN
C3CATD
C3TAG | ##C3TAG##
C3CORE1 | RD
C3CORE2 | WH
C3CORE3 | BU
C3CORE4 | BK
C3CORE5 | GN/YL
Note on A1: Author: Basic DBF structure outlined on this sheet. Create new prototypes by entering its name into a Column Header.

## TAG_DATA
{Note} | Prototype Mapping |  | Z_DRAWING |  | W_WIRE |  | X_PANEL |  | 24V Connections |  |  |  |  | 230V Connections | [5 empty] | Q_PROTECTION | [7 empty] | P_IO | [14 empty] | P2 | [14 empty] | D_DEVICES | [5 empty] | VSD |  |  |  | Isolator |  |  |  | C_CABLE
Tag | Typical | ProtoName | PREFIX | DRAWING | W1NAME | W2NAME | X1NAME | X1DESC | X1VDC24 | X1VDC0 | X1XIO | X1XIOF | X1XIOK | X1V230 | X1N230 | X1XDB | X1XDBF | X1XDBK | X1XDBQ | Q1CATN | Q1CATD | Q1NAME1 | Q1NAME2 | Q1TCATN | Q1TCATD | Q1TNAME | Q1TSETTO | P1NAME | P1RACK | P1SLOT | P1CHAN | P1CATN | P1CATD | P1CATD2 | P1TAG | P1DESC2 | P1DESC3 | P1DESC4 | P1T1 | P1T2 | P1T1TYPE | P1T2TYPE | P2NAME | P2RACK | P2SLOT | 2CHAN | P2CATN | P2CATD | P2CATD2 | P2TAG | P2DESC2 | P2DESC3 | P2DESC4 | P2T1 | P2T2 | P2T1TYPE | P2T2TYPE | D1TAG | D1DESC2 | D1DESC3 | D1TYPE | D1CATN | D1CATD | D1VNAME1 | D1VNAME2 | D1VCATN | D1VCATD | D1ICATD | D1ICATN | D1KW | Column4 | C1TAG | C2TAG | C3TAG | Notes
0 | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
<001> | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <001> | ELECTRICAL ROOM | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | <001> | ELECTRICAL ROOM |  | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
<002> | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <002> | PLC-CABINET | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | <002> | PLC-CABINET |  | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
<003> | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <003> | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | <003> | STEAM TO EXISTING HEADER |  | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
<004> | #N/A | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-300._L0 | [23 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <004> | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | <004> | FUEL SILO CROSS CONVEYOR |  | <ExcelError> | [10 empty] | <004>/01 | <004>/02 | <004>/03
<005> | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <005> | SAND TRANSMITTER | 230 VAC FEED |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | <005> | SAND TRANSMITTER |  | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1BL200 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1BL200_ISOLATOR | SOOTBLOWER 1 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1BL201_ISOLATOR | SOOTBLOWER 2 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1BL200 | SOOTBLOWER 1 ISOLATOR |  | BLOWER | [10 empty] | #N/A | #N/A | #N/A
BB1BL201 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1BL201_ISOLATOR | SOOTBLOWER 2 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1BL202_ISOLATOR | SOOTBLOWER 3 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1BL201 | SOOTBLOWER 2 ISOLATOR |  | BLOWER | [10 empty] | #N/A | #N/A | #N/A
BB1BL202 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1BL202_ISOLATOR | SOOTBLOWER 3 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1BL203_ISOLATOR | SOOTBLOWER 4 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1BL202 | SOOTBLOWER 3 ISOLATOR |  | BLOWER | [10 empty] | #N/A | #N/A | #N/A
BB1BL203 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1BL203_ISOLATOR | SOOTBLOWER 4 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1BL204_ISOLATOR | SOOTBLOWER 5 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1BL203 | SOOTBLOWER 4 ISOLATOR |  | BLOWER | [10 empty] | #N/A | #N/A | #N/A
BB1BL204 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1BL204_ISOLATOR | SOOTBLOWER 5 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1BL205_ISOLATOR | SOOTBLOWER 6 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1BL204 | SOOTBLOWER 5 ISOLATOR |  | BLOWER | [10 empty] | #N/A | #N/A | #N/A
BB1BL205 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1BL205_ISOLATOR | SOOTBLOWER 6 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1BL206_ISOLATOR | SOOTBLOWER 7 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1BL205 | SOOTBLOWER 6 ISOLATOR |  | BLOWER | [10 empty] | #N/A | #N/A | #N/A
BB1BL206 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1BL206_ISOLATOR | SOOTBLOWER 7 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM815_ISOLATOR | FLY ASH CONTAINER SCREW I | SOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1BL206 | SOOTBLOWER 7 ISOLATOR |  | BLOWER | [10 empty] | #N/A | #N/A | #N/A
BB1BU500 | BURNER | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1BU500_DO_IF1 | BURNER DIGITAL OUTPUT | INTERFACE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1BU500_DO_IF2 | BURNER DIGITAL OUTPUT | INTERFACE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1BU500 | BURNER DIGITAL OUTPUT | INTERFACE 1 | BURNER | [10 empty] | #N/A | #N/A | #N/A
BB1CP002 | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CP002 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1CV001 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV001_SETPOINT | MAKE-UP WATER CONTROL | VALVE SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV001_POSITION | MAKE-UP WATER CONTROL | VALVE POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV001 | MAKE-UP WATER CONTROL | VALVE SETPOINT | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV002 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV002_SETPOINT | FEED WATER CONTROL VALVE | SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV002_POSITION | FEED WATER CONTROL VALVE | POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV002 | FEED WATER CONTROL VALVE | SETPOINT | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV003 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV003_OPEN | CONTINUOUS BLOW DOWN | VALVE OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV003_CLOSE | CONTINUOUS BLOW DOWN | VALVE CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV003 | CONTINUOUS BLOW DOWN | VALVE OPEN | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV004 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV004_SETPOINT | PRIMARY AIR PREHEATER | CONTROL VALVE SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV004_POSITION | PRIMARY AIR PREHEATER | CONTROL VALVE POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV004 | PRIMARY AIR PREHEATER | CONTROL VALVE SETPOINT | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV200 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV200_SETPOINT | STEAM FROM DRUM CONTROL | VALVE SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV200_POSITION | STEAM FROM DRUM CONTROL | VALVE POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV200 | STEAM FROM DRUM CONTROL | VALVE SETPOINT | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV201 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV201_OPEN | START-UP VALVE OPEN |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV201_CLOSE | START-UP VALVE CLOSE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV201 | START-UP VALVE OPEN |  | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV202 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV202_OPEN | STEAM PRESSURE REDUCTION | VALVE OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV202_CLOSE | STEAM PRESSURE REDUCTION | VALVE CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV202 | STEAM PRESSURE REDUCTION | VALVE OPEN | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV203 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV203_OPEN | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV203_CLOSE | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV203 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV402 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV402_SETPOINT | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | SETPOINT | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV402_POSITION | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | POSITION | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV402 | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV403 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV403_SETPOINT | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | SETPOINT | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1CV403_POSITION | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | POSITION | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV403 | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV405 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV405 | BOTTOM ASH VALVE | SOLENOID VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV405 | BOTTOM ASH VALVE |  | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV406 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV406 | BOTTOM ASH VALVE | SOLENOID VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV406 | BOTTOM ASH VALVE |  | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV412 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV412 | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV412 | BOTTOM ASH SIEVE BYPASS |  | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV413 | BIN_VLV_2DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV413 | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV413 | CONTROL VALVE OF |  | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1CV414 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1CV414 | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1CV414 | WORK AIR TO PNEUMATIC |  | CONTROL VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1DM300 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1DM300_SETPOINT | TERTIARY AIR DAMPER 1 | SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1DM300_POSITION | TERTIARY AIR DAMPER 1 | POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DM300 | TERTIARY AIR DAMPER 1 | SETPOINT | DAMPER | [10 empty] | #N/A | #N/A | #N/A
BB1DM301 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1DM301_SETPOINT | SECONDARY AIR DAMPER 4 | SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1DM301_POSITION | SECONDARY AIR DAMPER 4 | POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DM301 | SECONDARY AIR DAMPER 4 | SETPOINT | DAMPER | [10 empty] | #N/A | #N/A | #N/A
BB1DM302 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1DM302_SETPOINT | SECONDARY AIR DAMPER 3 | SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1DM302_POSITION | SECONDARY AIR DAMPER 3 | POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DM302 | SECONDARY AIR DAMPER 3 | SETPOINT | DAMPER | [10 empty] | #N/A | #N/A | #N/A
BB1DM303 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1DM303_SETPOINT | SECONDARY AIR DAMPER 2 | SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1DM303_POSITION | SECONDARY AIR DAMPER 2 | POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DM303 | SECONDARY AIR DAMPER 2 | SETPOINT | DAMPER | [10 empty] | #N/A | #N/A | #N/A
BB1DM304 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1DM304_SETPOINT | SECONDARY AIR DAMPER 1 | SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1DM304_POSITION | SECONDARY AIR DAMPER 1 | POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DM304 | SECONDARY AIR DAMPER 1 | SETPOINT | DAMPER | [10 empty] | #N/A | #N/A | #N/A
BB1DM400 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1DM400_SETPOINT | PRIMARY AIR DAMPER | SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1DM400_POSITION | PRIMARY AIR DAMPER | POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DM400 | PRIMARY AIR DAMPER | SETPOINT | DAMPER | [10 empty] | #N/A | #N/A | #N/A
BB1DM550 | CONT_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1DM550_SETPOINT | RECIRCULATION GAS DAMPER | SETPOINT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1DM550_POSITION | RECIRCULATION GAS DAMPER | POSITION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DM550 | RECIRCULATION GAS DAMPER | SETPOINT | DAMPER | [10 empty] | #N/A | #N/A | #N/A
BB1DR400 | MCCB_1ph | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DR400 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1DR401 | MCCB_1ph | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1DR401 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1EH600 | DOL_DIR_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EH600_ISOLATOR | ELECTRIC HEATER | HYDRAULIC UNIT ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM651_ISOLATOR | FUEL SILO DUST FILTER FAN | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EH600 | ELECTRIC HEATER | HYDRAULIC UNIT ISOLATOR | HEATER | [10 empty] | #N/A | #N/A | #N/A
BB1EH662 | MCCB_1ph | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EH662 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1EM001 | FRQ_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM001 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1EM002 | FRQ_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM002 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1EM008 | DOL_DIR_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM008_ISOLATOR | CONVEYOR COOLING PUMP | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM009_ISOLATOR | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN ISOLAT | OR | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM008 | CONVEYOR COOLING PUMP | ISOLATOR | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM009 | DOL_DIR_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM009_ISOLATOR | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN ISOLAT | OR | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM408_ISOLATOR | BOILER HOUSE HEATER 1 | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM009 | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN ISOLAT | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM400 | FRQ_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM400 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1EM401 | FRQ_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM401_ISOLATOR | EXHAUST FAN 1 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM402 | COMPRESSOR 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM401 | EXHAUST FAN 1 ISOLATOR |  | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM402 | COMPR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM402 | COMPRESSOR 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM402 | COMPRESSOR 1 |  | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM403 | COMPR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM403 | COMPRESSOR 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM403 | COMPRESSOR 2 |  | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM405 | BELIMO_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM405 | AIR INTAKE GRILL 1 | OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM405 | AIR INTAKE GRILL 1 |  | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM406 | BELIMO_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM406 | AIR INTAKE GRILL 2 | OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM406 | AIR INTAKE GRILL 2 |  | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM407 | BELIMO_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM407 | AIR INTAKE GRILL 3 | OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM407 | AIR INTAKE GRILL 3 |  | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM408 | DOL_DIR_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM408_ISOLATOR | BOILER HOUSE HEATER 1 | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM409_ISOLATOR | BOILER HOUSE HEATER 2 | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM408 | BOILER HOUSE HEATER 1 | ISOLATOR | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM409 | DOL_DIR_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM409_ISOLATOR | BOILER HOUSE HEATER 2 | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM703_RUNNING | CHEMICAL FILLING PUMP 1 | RUNNING |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM409 | BOILER HOUSE HEATER 2 | ISOLATOR | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM550 | FRQ_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM550 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1EM601 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM601_LOCAL_MODE | DUST EXTRACTION | ROTARY FEEDER LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM601_LOCAL_RUN_FWD | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_F | WD | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM601 | DUST EXTRACTION | ROTARY FEEDER LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM603 | FRQ_DIRH | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM603_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_MODE | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM603_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_RUN | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM603 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM604 | FRQ_DIRH | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM604_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_MODE | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM604_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_RUN | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM604 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM605 | FRQ_DIRH | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM605_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_MODE | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM605_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_RUN | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM605 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM606 | DOL_DIR_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM606_ISOLATOR | DUST EXTRACTION FAN | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EH600_ISOLATOR | ELECTRIC HEATER | HYDRAULIC UNIT ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM606 | DUST EXTRACTION FAN | ISOLATOR | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM650 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-500._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150000 | N | 150000 | F150000 |  | Q150000 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | RIO_ | 01 | 45 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM650_LOCAL_MODE | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 45 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM650_LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM650 | SLEWING MOTOR FOR SCREW | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM651 | DOL_DIR_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM651_ISOLATOR | FUEL SILO DUST FILTER FAN | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM008_ISOLATOR | CONVEYOR COOLING PUMP | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM651 | FUEL SILO DUST FILTER FAN | ISOLATOR | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM652 | DOL_DIRH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM652_LOCAL_MODE | ROTATING FUEL SPREADER | LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM652_LOCAL_RUN | ROTATING FUEL SPREADER | LOCAL_RUN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM652 | ROTATING FUEL SPREADER | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM653 | DOL_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM653_RUNNING | COOLING FAN FUEL | FEEDING SCREW 1 RUNNING |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM653_FAULT | COOLING FAN FUEL | FEEDING SCREW 1 FAULT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM653 | COOLING FAN FUEL | FEEDING SCREW 1 RUNNING | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM654 | DOL_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM654_RUNNING | LUBRICATION UNIT RUNNING |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM654_FAULT | LUBRICATION UNIT FAULT |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM654 | LUBRICATION UNIT RUNNING |  | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM655 | DOL_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM655_RUNNING | COOLING FAN FUEL | FEEDING SCREW 2 RUNNING |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM655_FAULT | COOLING FAN FUEL | FEEDING SCREW 2 FAULT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM655 | COOLING FAN FUEL | FEEDING SCREW 2 RUNNING | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM656 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM656_LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 2 LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM656_LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | FWD | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM656 | FUEL FEEDING | ROTARY VALVE 2 LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM657 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM657_LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 1 LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM657_LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | FWD | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM657 | FUEL FEEDING | ROTARY VALVE 1 LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM658 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-501._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150100 | N | 150100 | F150100 |  | Q150100 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | RIO_ | 01 | 40 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM658_LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 40 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM658_LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM658 | SCRAPER CONVEYOR 1 | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM659 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-502._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150200 | N | 150200 | F150200 |  | Q150200 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | RIO_ | 01 | 41 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM659_LOCAL_MODE | BELT CONVEYOR | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 41 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM659_LOCAL_RUN_FWD | BELT CONVEYOR | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM659 | BELT CONVEYOR | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM660 | DOL_DIR | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM660_RUNNING | COOLING FAN FOR | SLEWING MOTOR RUNNING |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM660_FAULT | COOLING FAN FOR | SLEWING MOTOR FAULT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM660 | COOLING FAN FOR | SLEWING MOTOR RUNNING | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM662 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-503._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150300 | N | 150300 | F150300 |  | Q150300 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 44 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM662_LOCAL_MODE | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 44 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM662_LOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM662 | FUEL SILO SCREW DISCHARGE | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM663 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-504._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150400 | N | 150400 | F150400 |  | Q150400 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | RIO_ | 01 | 46 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM663_LOCAL_MODE | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 46 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM663_LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM663 | FUEL SILO CROSS CONVEYOR | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM664 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-505._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150500 | N | 150500 | F150500 |  | Q150500 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | RIO_ | 01 | 47 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM664_LOCAL_MODE | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 47 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM664_LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM664 | FUEL FEEDING SCREW 1 | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM665 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-506._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150600 | N | 150600 | F150600 |  | Q150600 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | RIO_ | 01 | 48 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM665_LOCAL_MODE | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 48 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM665_LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM665 | FUEL FEEDING SCREW 2 | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM670 | DOL_DIRH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM670_LOCAL_MODE | BELT MAGNET LOCAL_MODE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM670_LOCAL_RUN | BELT MAGNET LOCAL_RUN |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM670 | BELT MAGNET LOCAL_MODE |  | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM672 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-507._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150700 | N | 150700 | F150700 |  | Q150700 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | RIO_ | 01 | 43 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM672_LOCAL_MODE | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 43 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM672_LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM672 | SCRAPER CONVEYOR 2 | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM673 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM673_LOCAL_MODE | LEVELLING ROLLER 1 | LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM673_LOCAL_RUN_FWD | LEVELLING ROLLER 1 | LOCAL_RUN_FWD |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM673 | LEVELLING ROLLER 1 | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM674 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM674_LOCAL_MODE | LEVELLING ROLLER 2 | LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM674_LOCAL_RUN_FWD | LEVELLING ROLLER 2 | LOCAL_RUN_FWD |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM674 | LEVELLING ROLLER 2 | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM675 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM675_LOCAL_MODE | DISC SCREEN DRIVE 1 | LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM675_LOCAL_RUN_FWD | DISC SCREEN DRIVE 1 | LOCAL_RUN_FWD |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM675 | DISC SCREEN DRIVE 1 | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM676 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-508._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150800 | N | 150800 | F150800 |  | Q150800 | GV2L22 | 3P CIRCUIT BREAKER, TESYS GV2L, 25A | SCHNEIDER GV2L22 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 22A | RIO_ | 01 | 42 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM676_LOCAL_MODE | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 42 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM676_LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM676 | DISC SCREEN DRIVE 2 | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM703 | DOL_DIRH | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM703_RUNNING | CHEMICAL FILLING PUMP 1 | RUNNING |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM703_FAULT | CHEMICAL FILLING PUMP 1 | FAULT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM703 | CHEMICAL FILLING PUMP 1 | RUNNING | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM704 | DOL_DIRH | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM704_RUNNING | CHEMICAL FILLING PUMP 2 | RUNNING |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM704_FAULT | CHEMICAL FILLING PUMP 2 | FAULT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM704 | CHEMICAL FILLING PUMP 2 | RUNNING | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM815 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM815_ISOLATOR | FLY ASH CONTAINER SCREW I | SOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM855_ISOLATOR | ASH CONTAINER SCREW ISOLA | TOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM815 | FLY ASH CONTAINER SCREW I | SOLATOR | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM850 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM850_LOCAL_MODE | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM850_LOCAL_RUN_FWD | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM850 | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM851 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM851_LOCAL_MODE | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM851_LOCAL_RUN_FWD | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM851 | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM852 | FRQ_REVH | FRQ_REVH | 38025-ELE | 01-509._L0 |  |  | KPA_FLOORX_IO | KPA NON ASSIGNED IO | [5 empty] | Q150900 | N | 150900 | F150900 |  | Q150900 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | RIO_ | 01 | 49 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM852_LOCAL_MODE | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | V+ | 0 | 24VDC | DI | RIO_ | 01 | 49 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM852_LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | V+ | 1 | 24VDC | DI | BB1EM852 | BOTTOM ASH CONVEYOR | LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM855 | DOL_REV_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM855_ISOLATOR | ASH CONTAINER SCREW ISOLA | TOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM401_ISOLATOR | EXHAUST FAN 1 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM855 | ASH CONTAINER SCREW ISOLA | TOR | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1EM856 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1EM856_LOCAL_MODE | PURIFIED SAND | SCREW CONVEYOR LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM856_LOCAL_RUN_FWD | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | FWD | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM856 | PURIFIED SAND | SCREW CONVEYOR LOCAL_MODE | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1FG300 | ESP_DI_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FG300_ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_ALARM | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1FG300_ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_WARNING | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FG300 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP | [10 empty] | #N/A | #N/A | #N/A
BB1FL650 | MCCB_1ph | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FL650 | #N/A | #N/A | <ExcelError> | [10 empty] | #N/A | #N/A | #N/A
BB1FM001 | OESA_3ph | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FM001_ESTOP | BOTTOM ASH SIEVE FEED | ESTOP |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1FM001_RUNNING | BOTTOM ASH SIEVE FEED | RUNNING |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FM001 | BOTTOM ASH SIEVE FEED | ESTOP | MOTOR | [10 empty] | #N/A | #N/A | #N/A
BB1FS003 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-301._L0 | [23 empty] | RIO_ | 01 | 36 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1FS003 | BOTTOM ASH COOLING | FLOW SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FS003 | BOTTOM ASH COOLING |  | FLOW SWITCH | [10 empty] | BB1FS003/01 | BB1FS003/02 | BB1FS003/03
BB1FT001 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FT001 | FEED WATER FLOW | AND CONTROL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FT001 | FEED WATER FLOW |  | FLOW TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1FT200 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FT200 | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FT200 | HEATING STEAM TO FEED |  | FLOW TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1FT201 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FT201 | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FT201 | STEAM FLOW TO SOOTBLOWING |  | FLOW TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1FT202 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FT202 | MAIN STEAM FLOW |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FT202 | MAIN STEAM FLOW |  | FLOW TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1FT203 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FT203 | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FT203 | STEAM TO EXISTING HEADER |  | FLOW TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1FT400 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FT400 | PRIMARY AIR FLOW |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FT400 | PRIMARY AIR FLOW |  | FLOW TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1FT401 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FT401 | SECONDARY AIR FLOW |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FT401 | SECONDARY AIR FLOW |  | FLOW TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1FT550 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1FT550 | RECIRCULATION GAS FLOW |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1FT550 | RECIRCULATION GAS FLOW |  | FLOW TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1GS001 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-302._L0 | [23 empty] | RIO_ | 01 | 02 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS001 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS001 | FEED WATER PUMP SUCTION |  | GATE SWITCH | [10 empty] | BB1GS001/01 | BB1GS001/02 | BB1GS001/03
BB1GS002 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-303._L0 | [23 empty] | RIO_ | 01 | 02 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS002 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS002 | FEED WATER PUMP SUCTION |  | GATE SWITCH | [10 empty] | BB1GS002/01 | BB1GS002/02 | BB1GS002/03
BB1GS003 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-304._L0 | [23 empty] | RIO_ | 01 | 01 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS003 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS003 | FEED WATER PUMP SUCTION |  | GATE SWITCH | [10 empty] | BB1GS003/01 | BB1GS003/02 | BB1GS003/03
BB1GS004 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-305._L0 | [23 empty] | RIO_ | 01 | 01 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS004 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS004 | FEED WATER PUMP SUCTION |  | GATE SWITCH | [10 empty] | BB1GS004/01 | BB1GS004/02 | BB1GS004/03
BB1GS005 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-306._L0 | [23 empty] | RIO_ | 01 | 02 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS005 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS005 | FW TANK OVERFLOW ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS005/01 | BB1GS005/02 | BB1GS005/03
BB1GS006 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-307._L0 | [23 empty] | RIO_ | 01 | 02 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS006 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS006 | FW TANK OVERFLOW ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS006/01 | BB1GS006/02 | BB1GS006/03
BB1GS007 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-308._L0 | [23 empty] | RIO_ | 01 | 03 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS007 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS007 | FEEDWATER PUMP 1 ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS007/01 | BB1GS007/02 | BB1GS007/03
BB1GS008 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-309._L0 | [23 empty] | RIO_ | 01 | 03 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS008 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS008 | FEEDWATER PUMP 1 ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS008/01 | BB1GS008/02 | BB1GS008/03
BB1GS009 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-310._L0 | [23 empty] | RIO_ | 01 | 03 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS009 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS009 | FEED WATER PUMP 2 ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS009/01 | BB1GS009/02 | BB1GS009/03
BB1GS010 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-311._L0 | [23 empty] | RIO_ | 01 | 03 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS010 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS010 | FEED WATER PUMP 2 ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS010/01 | BB1GS010/02 | BB1GS010/03
BB1GS011 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-312._L0 | [23 empty] | RIO_ | 01 | 04 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS011 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS011 | BOILER BOTTOM BLOW DOWN |  | GATE SWITCH | [10 empty] | BB1GS011/01 | BB1GS011/02 | BB1GS011/03
BB1GS012 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-313._L0 | [23 empty] | RIO_ | 01 | 04 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS012 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS012 | BOILER BOTTOM BLOW DOWN |  | GATE SWITCH | [10 empty] | BB1GS012/01 | BB1GS012/02 | BB1GS012/03
BB1GS020 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-314._L0 | [23 empty] | RIO_ | 01 | 39 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS020 | EMERGENCY SHOWER | USE SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS020 | EMERGENCY SHOWER |  | GATE SWITCH | [10 empty] | BB1GS020/01 | BB1GS020/02 | BB1GS020/03
BB1GS200 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-315._L0 | [23 empty] | RIO_ | 01 | 06 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS200 | SOOTBLOWER 1 IN | LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS200 | SOOTBLOWER 1 IN |  | GATE SWITCH | [10 empty] | BB1GS200/01 | BB1GS200/02 | BB1GS200/03
BB1GS201 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-316._L0 | [23 empty] | RIO_ | 01 | 06 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS201 | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS201 | SOOTBLOWER 1 OUT |  | GATE SWITCH | [10 empty] | BB1GS201/01 | BB1GS201/02 | BB1GS201/03
BB1GS203 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-317._L0 | [23 empty] | RIO_ | 01 | 06 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS203 | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS203 | SOOTBLOWER 2 OUT |  | GATE SWITCH | [10 empty] | BB1GS203/01 | BB1GS203/02 | BB1GS203/03
BB1GS204 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-318._L0 | [23 empty] | RIO_ | 01 | 06 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS204 | SOOTBLOWER 2 IN | LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS204 | SOOTBLOWER 2 IN |  | GATE SWITCH | [10 empty] | BB1GS204/01 | BB1GS204/02 | BB1GS204/03
BB1GS205 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-319._L0 | [23 empty] | RIO_ | 01 | 07 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS205 | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS205 | SOOTBLOWER 3 OUT |  | GATE SWITCH | [10 empty] | BB1GS205/01 | BB1GS205/02 | BB1GS205/03
BB1GS206 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-320._L0 | [23 empty] | RIO_ | 01 | 07 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS206 | SOOTBLOWER 3 IN | LIMIT SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS206 | SOOTBLOWER 3 IN |  | GATE SWITCH | [10 empty] | BB1GS206/01 | BB1GS206/02 | BB1GS206/03
BB1GS207 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-321._L0 | [23 empty] | RIO_ | 01 | 07 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS207 | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS207 | SOOTBLOWER 5 OUT |  | GATE SWITCH | [10 empty] | BB1GS207/01 | BB1GS207/02 | BB1GS207/03
BB1GS208 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-322._L0 | [23 empty] | RIO_ | 01 | 07 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS208 | SOOTBLOWER 5 IN | LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS208 | SOOTBLOWER 5 IN |  | GATE SWITCH | [10 empty] | BB1GS208/01 | BB1GS208/02 | BB1GS208/03
BB1GS209 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-323._L0 | [23 empty] | RIO_ | 01 | 08 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS209 | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS209 | SOOTBLOWER 6 OUT |  | GATE SWITCH | [10 empty] | BB1GS209/01 | BB1GS209/02 | BB1GS209/03
BB1GS210 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-324._L0 | [23 empty] | RIO_ | 01 | 08 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS210 | SOOTBLOWER 6 IN | LIMIT SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS210 | SOOTBLOWER 6 IN |  | GATE SWITCH | [10 empty] | BB1GS210/01 | BB1GS210/02 | BB1GS210/03
BB1GS211 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-325._L0 | [23 empty] | RIO_ | 01 | 08 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS211 | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS211 | SOOTBLOWER 7 OUT |  | GATE SWITCH | [10 empty] | BB1GS211/01 | BB1GS211/02 | BB1GS211/03
BB1GS212 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-326._L0 | [23 empty] | RIO_ | 01 | 08 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS212 | SOOTBLOWER 7 IN | LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS212 | SOOTBLOWER 7 IN |  | GATE SWITCH | [10 empty] | BB1GS212/01 | BB1GS212/02 | BB1GS212/03
BB1GS213 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-327._L0 | [23 empty] | RIO_ | 01 | 09 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS213 | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS213 | SOOTBLOWER 8 OUT |  | GATE SWITCH | [10 empty] | BB1GS213/01 | BB1GS213/02 | BB1GS213/03
BB1GS214 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-328._L0 | [23 empty] | RIO_ | 01 | 09 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS214 | SOOTBLOWER 8 IN | LIMIT SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS214 | SOOTBLOWER 8 IN |  | GATE SWITCH | [10 empty] | BB1GS214/01 | BB1GS214/02 | BB1GS214/03
BB1GS215 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-329._L0 | [23 empty] | RIO_ | 01 | 13 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS215 | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS215 | PRIMARY AIR PREHEATER |  | GATE SWITCH | [10 empty] | BB1GS215/01 | BB1GS215/02 | BB1GS215/03
BB1GS216 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-330._L0 | [23 empty] | RIO_ | 01 | 13 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS216 | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS216 | PRIMARY AIR PREHEATER |  | GATE SWITCH | [10 empty] | BB1GS216/01 | BB1GS216/02 | BB1GS216/03
BB1GS217 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-331._L0 | [23 empty] | RIO_ | 01 | 11 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS217 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS217 | MAIN STEAM LINE |  | GATE SWITCH | [10 empty] | BB1GS217/01 | BB1GS217/02 | BB1GS217/03
BB1GS218 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-332._L0 | [23 empty] | RIO_ | 01 | 11 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS218 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS218 | MAIN STEAM LINE |  | GATE SWITCH | [10 empty] | BB1GS218/01 | BB1GS218/02 | BB1GS218/03
BB1GS219 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-333._L0 | [23 empty] | RIO_ | 01 | 11 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS219 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS219 | STEAM ACCUMULATOR ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS219/01 | BB1GS219/02 | BB1GS219/03
BB1GS220 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-334._L0 | [23 empty] | RIO_ | 01 | 11 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS220 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS220 | STEAM ACCUMULATOR ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS220/01 | BB1GS220/02 | BB1GS220/03
BB1GS221 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-335._L0 | [23 empty] | RIO_ | 01 | 04 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS221 | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS221 | MAIN STEAM VALVE BY-PASS |  | GATE SWITCH | [10 empty] | BB1GS221/01 | BB1GS221/02 | BB1GS221/03
BB1GS222 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-336._L0 | [23 empty] | RIO_ | 01 | 04 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS222 | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS222 | MAIN STEAM VALVE BY-PASS |  | GATE SWITCH | [10 empty] | BB1GS222/01 | BB1GS222/02 | BB1GS222/03
BB1GS223 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-337._L0 | [23 empty] | RIO_ | 01 | 05 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS223 | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS223 | MAIN STEAM LINE VALVE |  | GATE SWITCH | [10 empty] | BB1GS223/01 | BB1GS223/02 | BB1GS223/03
BB1GS224 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-338._L0 | [23 empty] | RIO_ | 01 | 05 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS224 | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS224 | MAIN STEAM LINE VALVE |  | GATE SWITCH | [10 empty] | BB1GS224/01 | BB1GS224/02 | BB1GS224/03
BB1GS225 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-339._L0 | [23 empty] | RIO_ | 01 | 05 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS225 | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS225 | START-UP LINE ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS225/01 | BB1GS225/02 | BB1GS225/03
BB1GS226 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-340._L0 | [23 empty] | RIO_ | 01 | 05 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS226 | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS226 | START-UP LINE ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS226/01 | BB1GS226/02 | BB1GS226/03
BB1GS227 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-341._L0 | [23 empty] | RIO_ | 01 | 09 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS227 | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS227 | SOOTBLOWING LINE ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS227/01 | BB1GS227/02 | BB1GS227/03
BB1GS228 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-342._L0 | [23 empty] | RIO_ | 01 | 09 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS228 | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS228 | SOOTBLOWING LINE ON-OFF |  | GATE SWITCH | [10 empty] | BB1GS228/01 | BB1GS228/02 | BB1GS228/03
BB1GS230 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-343._L0 | [23 empty] | RIO_ | 01 | 10 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS230 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS230 | STEAM ACCUMULATOR |  | GATE SWITCH | [10 empty] | BB1GS230/01 | BB1GS230/02 | BB1GS230/03
BB1GS231 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-344._L0 | [23 empty] | RIO_ | 01 | 10 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS231 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS231 | STEAM ACCUMULATOR |  | GATE SWITCH | [10 empty] | BB1GS231/01 | BB1GS231/02 | BB1GS231/03
BB1GS232 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-345._L0 | [23 empty] | RIO_ | 01 | 10 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS232 | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS232 | STEAM PRESSURE REDUCTION |  | GATE SWITCH | [10 empty] | BB1GS232/01 | BB1GS232/02 | BB1GS232/03
BB1GS233 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-346._L0 | [23 empty] | RIO_ | 01 | 10 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS233 | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS233 | STEAM PRESSURE REDUCTION |  | GATE SWITCH | [10 empty] | BB1GS233/01 | BB1GS233/02 | BB1GS233/03
BB1GS401 | BELIMO_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1GS401 | AIR INTAKE GRILL 1 | OPENED LIMIT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS401 | AIR INTAKE GRILL 1 |  | GATE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1GS412 | BELIMO_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1GS412 | AIR INTAKE GRILL 2 | OPENED LIMIT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS412 | AIR INTAKE GRILL 2 |  | GATE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1GS413 | BELIMO_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1GS413 | AIR INTAKE GRILL 3 | OPENED LIMIT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS413 | AIR INTAKE GRILL 3 |  | GATE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1GS600 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-347._L0 | [23 empty] | RIO_ | 01 | 22 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS600 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS600 | UNLOADING STATION 1, |  | GATE SWITCH | [10 empty] | BB1GS600/01 | BB1GS600/02 | BB1GS600/03
BB1GS601 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-348._L0 | [23 empty] | RIO_ | 01 | 18 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS601 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS601 | UNLOADING STATION 1, |  | GATE SWITCH | [10 empty] | BB1GS601/01 | BB1GS601/02 | BB1GS601/03
BB1GS602 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-349._L0 | [23 empty] | RIO_ | 01 | 17 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS602 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS602 | UNLOADING STATION 1, |  | GATE SWITCH | [10 empty] | BB1GS602/01 | BB1GS602/02 | BB1GS602/03
BB1GS603 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-350._L0 | [23 empty] | RIO_ | 01 | 16 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS603 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS603 | UNLOADING STATION 1, |  | GATE SWITCH | [10 empty] | BB1GS603/01 | BB1GS603/02 | BB1GS603/03
BB1GS604 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-351._L0 | [23 empty] | RIO_ | 01 | 22 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS604 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS604 | UNLOADING STATION 1, |  | GATE SWITCH | [10 empty] | BB1GS604/01 | BB1GS604/02 | BB1GS604/03
BB1GS605 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-352._L0 | [23 empty] | RIO_ | 01 | 17 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS605 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS605 | UNLOADING STATION 1, |  | GATE SWITCH | [10 empty] | BB1GS605/01 | BB1GS605/02 | BB1GS605/03
BB1GS606 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-353._L0 | [23 empty] | RIO_ | 01 | 14 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS606 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS606 | UNLOADING STATION 1, |  | GATE SWITCH | [10 empty] | BB1GS606/01 | BB1GS606/02 | BB1GS606/03
BB1GS607 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-354._L0 | [23 empty] | RIO_ | 01 | 17 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS607 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS607 | UNLOADING STATION 1, |  | GATE SWITCH | [10 empty] | BB1GS607/01 | BB1GS607/02 | BB1GS607/03
BB1GS608 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-355._L0 | [23 empty] | RIO_ | 01 | 21 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS608 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS608 | UNLOADING STATION 2, |  | GATE SWITCH | [10 empty] | BB1GS608/01 | BB1GS608/02 | BB1GS608/03
BB1GS609 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-356._L0 | [23 empty] | RIO_ | 01 | 19 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS609 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS609 | UNLOADING STATION 2, |  | GATE SWITCH | [10 empty] | BB1GS609/01 | BB1GS609/02 | BB1GS609/03
BB1GS610 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-357._L0 | [23 empty] | RIO_ | 01 | 23 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS610 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS610 | UNLOADING STATION 2, |  | GATE SWITCH | [10 empty] | BB1GS610/01 | BB1GS610/02 | BB1GS610/03
BB1GS611 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-358._L0 | [23 empty] | RIO_ | 01 | 13 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS611 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS611 | UNLOADING STATION 2, |  | GATE SWITCH | [10 empty] | BB1GS611/01 | BB1GS611/02 | BB1GS611/03
BB1GS612 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-359._L0 | [23 empty] | RIO_ | 01 | 20 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS612 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS612 | UNLOADING STATION 2, |  | GATE SWITCH | [10 empty] | BB1GS612/01 | BB1GS612/02 | BB1GS612/03
BB1GS613 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-360._L0 | [23 empty] | RIO_ | 01 | 20 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS613 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS613 | UNLOADING STATION 2, |  | GATE SWITCH | [10 empty] | BB1GS613/01 | BB1GS613/02 | BB1GS613/03
BB1GS614 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-361._L0 | [23 empty] | RIO_ | 01 | 14 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS614 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS614 | UNLOADING STATION 2, |  | GATE SWITCH | [10 empty] | BB1GS614/01 | BB1GS614/02 | BB1GS614/03
BB1GS615 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-362._L0 | [23 empty] | RIO_ | 01 | 15 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS615 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS615 | UNLOADING STATION 2, |  | GATE SWITCH | [10 empty] | BB1GS615/01 | BB1GS615/02 | BB1GS615/03
BB1GS616 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-363._L0 | [23 empty] | RIO_ | 01 | 22 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS616 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS616 | UNLOADING STATION 3, |  | GATE SWITCH | [10 empty] | BB1GS616/01 | BB1GS616/02 | BB1GS616/03
BB1GS617 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-364._L0 | [23 empty] | RIO_ | 01 | 19 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS617 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS617 | UNLOADING STATION 3, |  | GATE SWITCH | [10 empty] | BB1GS617/01 | BB1GS617/02 | BB1GS617/03
BB1GS618 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-365._L0 | [23 empty] | RIO_ | 01 | 21 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS618 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS618 | UNLOADING STATION 3, |  | GATE SWITCH | [10 empty] | BB1GS618/01 | BB1GS618/02 | BB1GS618/03
BB1GS619 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-366._L0 | [23 empty] | RIO_ | 01 | 14 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS619 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS619 | UNLOADING STATION 3, |  | GATE SWITCH | [10 empty] | BB1GS619/01 | BB1GS619/02 | BB1GS619/03
BB1GS620 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-367._L0 | [23 empty] | RIO_ | 01 | 21 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS620 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS620 | UNLOADING STATION 3, |  | GATE SWITCH | [10 empty] | BB1GS620/01 | BB1GS620/02 | BB1GS620/03
BB1GS621 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-368._L0 | [23 empty] | RIO_ | 01 | 13 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS621 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS621 | UNLOADING STATION 3, |  | GATE SWITCH | [10 empty] | BB1GS621/01 | BB1GS621/02 | BB1GS621/03
BB1GS622 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-369._L0 | [23 empty] | RIO_ | 01 | 16 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS622 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS622 | UNLOADING STATION 3, |  | GATE SWITCH | [10 empty] | BB1GS622/01 | BB1GS622/02 | BB1GS622/03
BB1GS623 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-370._L0 | [23 empty] | RIO_ | 01 | 15 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS623 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS623 | UNLOADING STATION 3, |  | GATE SWITCH | [10 empty] | BB1GS623/01 | BB1GS623/02 | BB1GS623/03
BB1GS650 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-371._L0 | [23 empty] | RIO_ | 01 | 16 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS650 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS650 | DISC SCREEN BY-PASS |  | GATE SWITCH | [10 empty] | BB1GS650/01 | BB1GS650/02 | BB1GS650/03
BB1GS651 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-372._L0 | [23 empty] | RIO_ | 01 | 14 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS651 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS651 | DISC SCREEN BY-PASS |  | GATE SWITCH | [10 empty] | BB1GS651/01 | BB1GS651/02 | BB1GS651/03
BB1GS652 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-373._L0 | [23 empty] | RIO_ | 01 | 27 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS652 | EXPLOSION HATCH | LIMIT SWITCH 1 |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS652 | EXPLOSION HATCH |  | GATE SWITCH | [10 empty] | BB1GS652/01 | BB1GS652/02 | BB1GS652/03
BB1GS653 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-374._L0 | [23 empty] | RIO_ | 01 | 28 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS653 | EXPLOSION HATCH | LIMIT SWITCH 2 |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS653 | EXPLOSION HATCH |  | GATE SWITCH | [10 empty] | BB1GS653/01 | BB1GS653/02 | BB1GS653/03
BB1GS654 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-375._L0 | [23 empty] | RIO_ | 01 | 28 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS654 | EXPLOSION HATCH | LIMIT SWITCH 3 |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS654 | EXPLOSION HATCH |  | GATE SWITCH | [10 empty] | BB1GS654/01 | BB1GS654/02 | BB1GS654/03
BB1GS655 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-376._L0 | [23 empty] | RIO_ | 01 | 28 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS655 | EXPLOSION HATCH | LIMIT SWITCH 4 |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS655 | EXPLOSION HATCH |  | GATE SWITCH | [10 empty] | BB1GS655/01 | BB1GS655/02 | BB1GS655/03
BB1GS656 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-377._L0 | [23 empty] | RIO_ | 01 | 31 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS656 | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS656 | SLIDE GATE VALVE CLOSE |  | GATE SWITCH | [10 empty] | BB1GS656/01 | BB1GS656/02 | BB1GS656/03
BB1GS659 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-378._L0 | [23 empty] | RIO_ | 01 | 26 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS659 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS659 | BELT CONVEYOR |  | GATE SWITCH | [10 empty] | BB1GS659/01 | BB1GS659/02 | BB1GS659/03
BB1GS660 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-379._L0 | [23 empty] | RIO_ | 01 | 26 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS660 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS660 | BELT CONVEYOR |  | GATE SWITCH | [10 empty] | BB1GS660/01 | BB1GS660/02 | BB1GS660/03
BB1GS661 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-380._L0 | [23 empty] | RIO_ | 01 | 25 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS661 | BELT MAGNET | DEVIATION DETECTOR 1 |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS661 | BELT MAGNET |  | GATE SWITCH | [10 empty] | BB1GS661/01 | BB1GS661/02 | BB1GS661/03
BB1GS662 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-381._L0 | [23 empty] | RIO_ | 01 | 26 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS662 | BELT MAGNET | DEVIATION DETECTOR 2 |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS662 | BELT MAGNET |  | GATE SWITCH | [10 empty] | BB1GS662/01 | BB1GS662/02 | BB1GS662/03
BB1GS663 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-382._L0 | [23 empty] | RIO_ | 01 | 27 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS663 | BELT CONVEYOR | OVERSIZE DETECTOR |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS663 | BELT CONVEYOR |  | GATE SWITCH | [10 empty] | BB1GS663/01 | BB1GS663/02 | BB1GS663/03
BB1GS800 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-383._L0 | [23 empty] | RIO_ | 01 | 36 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS800 | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS800 | SAND FILLING VALVE |  | GATE SWITCH | [10 empty] | BB1GS800/01 | BB1GS800/02 | BB1GS800/03
BB1GS801 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-384._L0 | [23 empty] | RIO_ | 01 | 36 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS801 | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS801 | SAND FILLING VALVE |  | GATE SWITCH | [10 empty] | BB1GS801/01 | BB1GS801/02 | BB1GS801/03
BB1GS802 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-385._L0 | [23 empty] | RIO_ | 01 | 32 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS802 | BOTTOM ASH VALVE | LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS802 | BOTTOM ASH VALVE |  | GATE SWITCH | [10 empty] | BB1GS802/01 | BB1GS802/02 | BB1GS802/03
BB1GS803 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-386._L0 | [23 empty] | RIO_ | 01 | 32 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS803 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS803 | BOTTOM ASH DROPPING CHUTE |  | GATE SWITCH | [10 empty] | BB1GS803/01 | BB1GS803/02 | BB1GS803/03
BB1GS850 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-387._L0 | [23 empty] | RIO_ | 01 | 35 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS850 | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS850 | BOTTOM ASH SIEVE BYPASS |  | GATE SWITCH | [10 empty] | BB1GS850/01 | BB1GS850/02 | BB1GS850/03
BB1GS851 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-388._L0 | [23 empty] | RIO_ | 01 | 36 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS851 | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS851 | BOTTOM ASH SIEVE BYPASS |  | GATE SWITCH | [10 empty] | BB1GS851/01 | BB1GS851/02 | BB1GS851/03
BB1GS852 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-389._L0 | [23 empty] | RIO_ | 01 | 39 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS852 | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS852 | BOTTOM ASH CONVEYOR |  | GATE SWITCH | [10 empty] | BB1GS852/01 | BB1GS852/02 | BB1GS852/03
BB1GS853 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-390._L0 | [23 empty] | RIO_ | 01 | 37 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS853 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS853 | BOTTOM ASH DROPPING CHUTE |  | GATE SWITCH | [10 empty] | BB1GS853/01 | BB1GS853/02 | BB1GS853/03
BB1GS854 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-391._L0 | [23 empty] | RIO_ | 01 | 37 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS854 | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS854 | BOTTOM ASH DROPPING CHUTE |  | GATE SWITCH | [10 empty] | BB1GS854/01 | BB1GS854/02 | BB1GS854/03
BB1GS855 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-392._L0 | [23 empty] | RIO_ | 01 | 34 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS855 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS855 | BOTTOM ASH VALVE SOLENOID |  | GATE SWITCH | [10 empty] | BB1GS855/01 | BB1GS855/02 | BB1GS855/03
BB1GS856 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-393._L0 | [23 empty] | RIO_ | 01 | 35 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS856 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS856 | BOTTOM ASH VALVE SOLENOID |  | GATE SWITCH | [10 empty] | BB1GS856/01 | BB1GS856/02 | BB1GS856/03
BB1GS857 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-394._L0 | [23 empty] | RIO_ | 01 | 35 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS857 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS857 | BOTTOM ASH VALVE SOLENOID |  | GATE SWITCH | [10 empty] | BB1GS857/01 | BB1GS857/02 | BB1GS857/03
BB1GS858 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-395._L0 | [23 empty] | RIO_ | 01 | 35 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS858 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS858 | BOTTOM ASH VALVE SOLENOID |  | GATE SWITCH | [10 empty] | BB1GS858/01 | BB1GS858/02 | BB1GS858/03
BB1GS859 | MEAS_BIN | [26 empty] | RIO_ | 01 | 37 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS859 | BOTTOM ASH TO CONTAINER | IN PLACE |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1GS859 | BOTTOM ASH TO CONTAINER |  | GATE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1HS101 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS101 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS101 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS102 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS102 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS102 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS103 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS103 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS103 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS104 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS104 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS104 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS105 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS105 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS105 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS106 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS106 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS106 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS107 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS107 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS107 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS108 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS108 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS108 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS109 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS109 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS109 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS110 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS110 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS110 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS111 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS111 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS111 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS112 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS112 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS112 | BOILER EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS601 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS601 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS601 | FUEL SYSTEM EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS602 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS602 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS602 | FUEL SYSTEM EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS603 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS603 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS603 | FUEL SYSTEM EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1HS604 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1HS604 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1HS604 | FUEL SYSTEM EMERGENCY |  | EMERGENCY STOP | [10 empty] | #N/A | #N/A | #N/A
BB1IJ001 | ALM_HORN | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IJ001 | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IJ001 | SCRAPER CONVEYOR 2 |  | ALARM | [10 empty] | #N/A | #N/A | #N/A
BB1IJ002 | ALM_HORN | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IJ002 | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IJ002 | SCRAPER CONVEYOR 1 |  | ALARM | [10 empty] | #N/A | #N/A | #N/A
BB1IJ004 | ALM_HORN | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IJ004 | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IJ004 | BOTTOM ASH CONVEYOR |  | ALARM | [10 empty] | #N/A | #N/A | #N/A
BB1IL001 | ALM_HORN | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IL001 | ALARM HORN AND LIGHT | CO ALARM |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IL001 | ALARM HORN AND LIGHT |  | ALARM | [10 empty] | #N/A | #N/A | #N/A
BB1IV002 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV002_OPEN | FEEDWATER PUMP 1 ON-OFF | VALVE OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV002_CLOSE | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV002 | FEEDWATER PUMP 1 ON-OFF | VALVE OPEN | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV003 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV003_OPEN | FEED WATER PUMP 2 ON-OFF | VALVE OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV003_CLOSE | FEED WATER PUMP 2 ON-OFF | VALVE CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV003 | FEED WATER PUMP 2 ON-OFF | VALVE OPEN | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV004 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV004 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV004 | BOILER BOTTOM BLOW DOWN |  | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV200 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV200_OPEN | START-UP CHECK VALVE | OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV200_CLOSE | START-UP CHECK VALVE | CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV200 | START-UP CHECK VALVE | OPEN | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV201 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV201_OPEN | MAIN STEAM VALVE OPEN |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV201_CLOSE | MAIN STEAM VALVE CLOSE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV201 | MAIN STEAM VALVE OPEN |  | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV202 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV202_OPEN | MAIN STEAM VALVE BY-PASS | VALVE OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV202_CLOSE | MAIN STEAM VALVE BY-PASS | VALVE CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV202 | MAIN STEAM VALVE BY-PASS | VALVE OPEN | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV203 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV203_OPEN | SOOTBLOWING LINE ON-OFF | VALVE OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV203_CLOSE | SOOTBLOWING LINE ON-OFF | VALVE CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV203 | SOOTBLOWING LINE ON-OFF | VALVE OPEN | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV204 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV204_OPEN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV204_CLOSE | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV204 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV205 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV205_OPEN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV205_CLOSE | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV205 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV206 | MTR_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV206_OPEN | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV206_CLOSE | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV206 | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1IV650 | DOL_REVH_BUS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1IV650_LOCAL_MODE | SLIDE GATE VALVE | LOCAL_MODE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1IV650_LOCAL_RUN_FWD | SLIDE GATE VALVE | LOCAL_RUN_FWD |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1IV650 | SLIDE GATE VALVE | LOCAL_MODE | ISOLATING VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1LS103 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LS103 | STEAM DRUM LEVEL SWITCH 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS103 | STEAM DRUM LEVEL SWITCH 1 |  | LEVEL SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1LS104 | MEAS_BIN_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LS104 | STEAM DRUM LEVEL SWITCH 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS104 | STEAM DRUM LEVEL SWITCH 2 |  | LEVEL SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1LS600 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-396._L0 | [23 empty] | RIO_ | 01 | 19 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS600 | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS600 | HYDRAULICS UNIT 1, |  | LEVEL SWITCH | [10 empty] | BB1LS600/01 | BB1LS600/02 | BB1LS600/03
BB1LS608 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-397._L0 | [23 empty] | RIO_ | 01 | 18 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS608 | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS608 | HYDRAULICS UNIT 1, |  | LEVEL SWITCH | [10 empty] | BB1LS608/01 | BB1LS608/02 | BB1LS608/03
BB1LS650 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-398._L0 | [23 empty] | RIO_ | 01 | 19 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS650 | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS650 | SCRAPER CONVEYOR 1 |  | LEVEL SWITCH | [10 empty] | BB1LS650/01 | BB1LS650/02 | BB1LS650/03
BB1LS651 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-399._L0 | [23 empty] | RIO_ | 01 | 20 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS651 | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS651 | UNLOADING STATION 3, |  | LEVEL SWITCH | [10 empty] | BB1LS651/01 | BB1LS651/02 | BB1LS651/03
BB1LS652 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-400._L0 | [23 empty] | RIO_ | 01 | 18 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS652 | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS652 | UNLOADING STATION 2, |  | LEVEL SWITCH | [10 empty] | BB1LS652/01 | BB1LS652/02 | BB1LS652/03
BB1LS653 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-401._L0 | [23 empty] | RIO_ | 01 | 22 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1LS653 | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS653 | UNLOADING STATION 1, |  | LEVEL SWITCH | [10 empty] | BB1LS653/01 | BB1LS653/02 | BB1LS653/03
BB1LS654 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-402._L0 | [23 empty] | RIO_ | 01 | 20 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS654 | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS654 | SCRAPER CONVEYOR 1, |  | LEVEL SWITCH | [10 empty] | BB1LS654/01 | BB1LS654/02 | BB1LS654/03
BB1LS655 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-403._L0 | [23 empty] | RIO_ | 01 | 17 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1LS655 | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS655 | SCRAPER CONVEYOR 2, |  | LEVEL SWITCH | [10 empty] | BB1LS655/01 | BB1LS655/02 | BB1LS655/03
BB1LS656 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-404._L0 | [23 empty] | RIO_ | 01 | 18 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1LS656 | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS656 | SCRAPER CONVEYOR 2, |  | LEVEL SWITCH | [10 empty] | BB1LS656/01 | BB1LS656/02 | BB1LS656/03
BB1LS657 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-405._L0 | [23 empty] | RIO_ | 01 | 28 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1LS657 | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS657 | FUEL SILO DISCHARGE |  | LEVEL SWITCH | [10 empty] | BB1LS657/01 | BB1LS657/02 | BB1LS657/03
BB1LS658 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-406._L0 | [23 empty] | RIO_ | 01 | 29 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS658 | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS658 | FUEL SILO CROSS CONVEYOR |  | LEVEL SWITCH | [10 empty] | BB1LS658/01 | BB1LS658/02 | BB1LS658/03
BB1LS659 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-407._L0 | [23 empty] | RIO_ | 01 | 29 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1LS659 | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS659 | FUEL FEEDING SCREW 1 |  | LEVEL SWITCH | [10 empty] | BB1LS659/01 | BB1LS659/02 | BB1LS659/03
BB1LS660 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-408._L0 | [23 empty] | RIO_ | 01 | 29 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS660 | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS660 | FUEL FEEDING SCREW 2 |  | LEVEL SWITCH | [10 empty] | BB1LS660/01 | BB1LS660/02 | BB1LS660/03
BB1LS661 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-409._L0 | [23 empty] | RIO_ | 01 | 31 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1LS661 | LUBRICATION ALARM | SCREW DISCHARGER |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS661 | LUBRICATION ALARM |  | LEVEL SWITCH | [10 empty] | BB1LS661/01 | BB1LS661/02 | BB1LS661/03
BB1LS700 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-410._L0 | [23 empty] | RIO_ | 01 | 01 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS700 | CHEMICAL TANK 1 | LEVEL SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS700 | CHEMICAL TANK 1 |  | LEVEL SWITCH | [10 empty] | BB1LS700/01 | BB1LS700/02 | BB1LS700/03
BB1LS701 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-411._L0 | [23 empty] | RIO_ | 01 | 01 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1LS701 | CHEMICAL TANK 2 | LEVEL SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS701 | CHEMICAL TANK 2 |  | LEVEL SWITCH | [10 empty] | BB1LS701/01 | BB1LS701/02 | BB1LS701/03
BB1LS850 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-412._L0 | [23 empty] | RIO_ | 01 | 37 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1LS850 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS850 | BOTTOM ASH CONTAINER |  | LEVEL SWITCH | [10 empty] | BB1LS850/01 | BB1LS850/02 | BB1LS850/03
BB1LS851 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-413._L0 | [23 empty] | RIO_ | 01 | 38 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS851 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS851 | BOTTOM ASH CONTAINER |  | LEVEL SWITCH | [10 empty] | BB1LS851/01 | BB1LS851/02 | BB1LS851/03
BB1LS852 | MEAS_BIN | [26 empty] | RIO_ | 01 | 32 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS852 | FLY ASH CONTAINER | LEVEL SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LS852 | FLY ASH CONTAINER |  | LEVEL SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1LT001 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT001 | FEED WATER TANK LEVEL 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT001 | FEED WATER TANK LEVEL 1 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT002 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT002 | FEED WATER TANK LEVEL 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT002 | FEED WATER TANK LEVEL 2 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT003 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT003 | STEAM ACCUMULATOR LEVEL 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT003 | STEAM ACCUMULATOR LEVEL 1 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT004 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT004 | STEAM ACCUMULATOR LEVEL 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT004 | STEAM ACCUMULATOR LEVEL 2 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT101 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT101 | STEAM DRUM LEVEL 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT101 | STEAM DRUM LEVEL 1 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT102 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT102 | STEAM DRUM LEVEL 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT102 | STEAM DRUM LEVEL 2 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT103 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT103 | STEAM DRUM LEVEL 3 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT103 | STEAM DRUM LEVEL 3 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT611 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT611 | UNLOADING STATION 1 LEVEL |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT611 | UNLOADING STATION 1 LEVEL |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT612 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT612 | UNLOADING STATION 3 LEVEL |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT612 | UNLOADING STATION 3 LEVEL |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT613 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT613 | UNLOADING STATION 2 LEVEL |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT613 | UNLOADING STATION 2 LEVEL |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT650 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT650 | FUEL SILO LEVEL RADAR 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT650 | FUEL SILO LEVEL RADAR 1 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT651 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT651 | FUEL SILO LEVEL RADAR 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT651 | FUEL SILO LEVEL RADAR 2 |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT652 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT652 | FUEL POCKET LEVEL |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT652 | FUEL POCKET LEVEL |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT800 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT800 | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT800 | RECYCLED BED MATERIAL |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1LT802 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1LT802 | SAND SILO LEVEL | MEASUREMENT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1LT802 | SAND SILO LEVEL |  | LEVEL TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PS600 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-414._L0 | [23 empty] | RIO_ | 01 | 21 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1PS600 | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PS600 | HYDRAULICS UNIT 1, |  | PRESSURE SWITCH | [10 empty] | BB1PS600/01 | BB1PS600/02 | BB1PS600/03
BB1PS601 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-415._L0 | [23 empty] | RIO_ | 01 | 16 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1PS601 | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PS601 | HYDRAULICS UNIT 1, |  | PRESSURE SWITCH | [10 empty] | BB1PS601/01 | BB1PS601/02 | BB1PS601/03
BB1PS602 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-416._L0 | [23 empty] | RIO_ | 01 | 15 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1PS602 | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PS602 | HYDRAULICS UNIT 1, |  | PRESSURE SWITCH | [10 empty] | BB1PS602/01 | BB1PS602/02 | BB1PS602/03
BB1PS603 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-417._L0 | [23 empty] | RIO_ | 01 | 25 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1PS603 | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PS603 | HYDRAULIC OIL RETURN |  | PRESSURE SWITCH | [10 empty] | BB1PS603/01 | BB1PS603/02 | BB1PS603/03
BB1PS604 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-418._L0 | [23 empty] | RIO_ | 01 | 25 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1PS604 | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PS604 | HYDRAULIC OIL RETURN |  | PRESSURE SWITCH | [10 empty] | BB1PS604/01 | BB1PS604/02 | BB1PS604/03
BB1PS605 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-419._L0 | [23 empty] | RIO_ | 01 | 24 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1PS605 | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PS605 | HYDRAULIC OIL RETURN |  | PRESSURE SWITCH | [10 empty] | BB1PS605/01 | BB1PS605/02 | BB1PS605/03
BB1PT001 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT001 | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT001 | FEED WATER PUMP 1 |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT002 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT002 | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT002 | FEED WATER PUMP 2 |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT004 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT004 | FEED WATER PRESSURE | BEFORE VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT004 | FEED WATER PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT005 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT005 | FEED WATER PRESSURE | AFTER VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT005 | FEED WATER PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT006 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT006 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT006 | FW SUCTION LINE STRAINER |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT007 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT007 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT007 | FW SUCTION LINE STRAINER |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT009 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT009 | COOLING WATER PRESSURE | BEFORE PUMP |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT009 | COOLING WATER PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT200 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT200 | FEED WATER TANK PRESSURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT200 | FEED WATER TANK PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT201 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT201 | STEAM DRUM PRESSURE 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT201 | STEAM DRUM PRESSURE 1 |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT203 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT203 | STEAM DRUM PRESSURE 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT203 | STEAM DRUM PRESSURE 2 |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT204 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT204 | MAIN STEAM PRESSURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT204 | MAIN STEAM PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT205 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT205 | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT205 | STEAM OUTLET PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT207 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT207 | ACCUMULATOR PRESSURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT207 | ACCUMULATOR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT208 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT208 | ACCUMULATOR PRESSURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT208 | ACCUMULATOR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT400 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT400 | PRIMARY AIR PRESSURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT400 | PRIMARY AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT401 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT401 | SECONDARY AIR PRESSURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT401 | SECONDARY AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT402 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT402 | INSTRUMENT AIR PRESSURE | AFTER DRYER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT402 | INSTRUMENT AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT403 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT403 | SECONDARY AIR PRESSURE | INNER BACK WALL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT403 | SECONDARY AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT404 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT404 | BOILER UPPER PART | PRESSURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT404 | BOILER UPPER PART |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT405 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT405 | BOILER UPPER PART | PRESSURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT405 | BOILER UPPER PART |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT406 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT406 | BOILER UPPER PART | PRESSURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT406 | BOILER UPPER PART |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT407 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT407 | TERTIARY AIR PRESSURE | RIGHT WALL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT407 | TERTIARY AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT408 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT408 | TERTIARY AIR PRESSURE | LEFT WALL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT408 | TERTIARY AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT409 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT409 | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT409 | SECONDARY AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT410 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT410 | SECONDARY AIR PRESSURE | INNER FRONT WALL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT410 | SECONDARY AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT411 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT411 | SECONDARY AIR PRESSURE | OUTER BACK WALL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT411 | SECONDARY AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT478 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT478 | INSTRUMENT AIR PRESSURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT478 | INSTRUMENT AIR PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT550 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT550 | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT550 | FLUE GAS PRESSURE AT THE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT552 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT552 | ESP INLET PRESSURE | TRANSMITTER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT552 | ESP INLET PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT553 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PT553 | ESP OUTLET PRESSURE | TRANSMITTER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT553 | ESP OUTLET PRESSURE |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PT800 | MEAS_BIN | [26 empty] | RIO_ | 01 | 38 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1PT800 | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PT800 | RECYCLED BED MATERIAL |  | PRESSURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1PU800 | CHEMICAL_PUMP | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PU800 | CHEMICAL DOSING PUMP 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PU800 | CHEMICAL DOSING PUMP 1 |  | PUMP | [10 empty] | #N/A | #N/A | #N/A
BB1PU801 | CHEMICAL_PUMP | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1PU801 | CHEMICAL DOSING PUMP 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1PU801 | CHEMICAL DOSING PUMP 2 |  | PUMP | [10 empty] | #N/A | #N/A | #N/A
BB1QT001 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT001 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT001 | CONDUCTIVITY MEASUREMENT |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT002 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT002 | PH MEASUREMENT FROM FEED | WATER TANK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT002 | PH MEASUREMENT FROM FEED |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT003 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT003 | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT003 | CONDUCTIVITY MEASUREMENT |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT004 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT004 | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT004 | CONDUCTIVITY MEASUREMENT |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT005 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT005 | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT005 | CONDUCTIVITY MEASUREMENT |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT006 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT006 | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT006 | CONDUCTIVITY MEASUREMENT |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT007 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT007 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT007 | CONDUCTIVITY MEASUREMENT |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT550 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT550 | FLUEGAS OXYGEN | MEASUREMENT 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT550 | FLUEGAS OXYGEN |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT551 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT551 | FLUEGAS OXYGEN | MEASUREMENT 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT551 | FLUEGAS OXYGEN |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT552 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT552 | FLUEGAS CO MEASUREMENT |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT552 | FLUEGAS CO MEASUREMENT |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT553 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT553 | BOILER ROOM GAS DETECTOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT553 | BOILER ROOM GAS DETECTOR |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1QT554 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1QT554 | OPACITY AFTER ESP |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1QT554 | OPACITY AFTER ESP |  | GAS/pH/CONDUCTIVITY TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1SI400 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI400 | PRIMARY AIR FAN | SAFETY INTERLOCK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI400 | PRIMARY AIR FAN |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI401 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI401 | SECONDARY AIR FAN | SAFETY INTERLOCK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI401 | SECONDARY AIR FAN |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI550 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI550 | FLUE GAS FAN | SAFETY INTERLOCK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI550 | FLUE GAS FAN |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI603 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI603 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI603 | FUEL RECEPTION HYDRAULIC |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI604 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI604 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI604 | FUEL RECEPTION HYDRAULIC |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI605 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI605 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI605 | FUEL RECEPTION HYDRAULIC |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI658 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI658 | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI658 | SCRAPER CONVEYOR 1 |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI659 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI659 | BELT CONVEYOR | SAFETY INTERLOCK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI659 | BELT CONVEYOR |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI672 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI672 | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI672 | SCRAPER CONVEYOR 2 |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI675 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI675 | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI675 | DISC SCREEN DRIVE 1 |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1SI676 | FAN_SRS_DO | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SI676 | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SI676 | DISC SCREEN DRIVE 2 |  | SAFETY INTERLOCK | [10 empty] | #N/A | #N/A | #N/A
BB1ST649 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-420._L0 | [23 empty] | RIO_ | 01 | 29 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST649 | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST649 | FUEL SILO CROSS CONVEYOR |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST649/01 | BB1ST649/02 | BB1ST649/03
BB1ST650 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-421._L0 | [23 empty] | RIO_ | 01 | 23 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1ST650 | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST650 | SCRAPER CONVEYOR 1, |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST650/01 | BB1ST650/02 | BB1ST650/03
BB1ST651 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-422._L0 | [23 empty] | RIO_ | 01 | 15 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST651 | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST651 | SCRAPER CONVEYOR 2, |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST651/01 | BB1ST651/02 | BB1ST651/03
BB1ST652 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-423._L0 | [23 empty] | RIO_ | 01 | 26 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST652 | BELT CONVEYOR | ROTATION GUARD |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST652 | BELT CONVEYOR |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST652/01 | BB1ST652/02 | BB1ST652/03
BB1ST653 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-424._L0 | [23 empty] | RIO_ | 01 | 30 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST653 | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST653 | FUEL FEEDING SCREW 2 |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST653/01 | BB1ST653/02 | BB1ST653/03
BB1ST654 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-425._L0 | [23 empty] | RIO_ | 01 | 25 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST654 | BELT MAGNET | ROTATION GUARD |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST654 | BELT MAGNET |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST654/01 | BB1ST654/02 | BB1ST654/03
BB1ST655 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-426._L0 | [23 empty] | RIO_ | 01 | 30 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST655 | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST655 | FUEL FEEDING ROTARY |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST655/01 | BB1ST655/02 | BB1ST655/03
BB1ST656 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-427._L0 | [23 empty] | RIO_ | 01 | 27 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST656 | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST656 | DISC SCREEN DRIVE 1 |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST656/01 | BB1ST656/02 | BB1ST656/03
BB1ST657 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-428._L0 | [23 empty] | RIO_ | 01 | 27 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST657 | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST657 | DISC SCREEN DRIVE 2 |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST657/01 | BB1ST657/02 | BB1ST657/03
BB1ST659 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-429._L0 | [23 empty] | RIO_ | 01 | 31 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1ST659 | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST659 | FUEL FEEDING SCREW 1 |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST659/01 | BB1ST659/02 | BB1ST659/03
BB1ST673 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-430._L0 | [23 empty] | RIO_ | 01 | 24 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1ST673 | LEVELING ROLLER 1 | SPEED SWITCH |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST673 | LEVELING ROLLER 1 |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST673/01 | BB1ST673/02 | BB1ST673/03
BB1ST674 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-431._L0 | [23 empty] | RIO_ | 01 | 24 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST674 | LEVELING ROLLER 2 | SPEED SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST674 | LEVELING ROLLER 2 |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST674/01 | BB1ST674/02 | BB1ST674/03
BB1ST675 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-432._L0 | [23 empty] | RIO_ | 01 | 23 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST675 | LEVELING ROLLER 3 | SPEED SWITCH |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST675 | LEVELING ROLLER 3 |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST675/01 | BB1ST675/02 | BB1ST675/03
BB1ST804 | MEAS_BIN | [26 empty] | RIO_ | 01 | 33 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST804 | ESP ROTARY VALVE | ROTATION GUARD |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST804 | ESP ROTARY VALVE |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | #N/A | #N/A | #N/A
BB1ST805 | MEAS_BIN | [26 empty] | RIO_ | 01 | 32 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST805 | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST805 | HEATED ESP COLLECTION |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | #N/A | #N/A | #N/A
BB1ST808 | MEAS_BIN | [26 empty] | RIO_ | 01 | 33 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1ST808 | ESP HOPPER 2 SCREW | ROTATION GUARD |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST808 | ESP HOPPER 2 SCREW |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | #N/A | #N/A | #N/A
BB1ST809 | MEAS_BIN | [26 empty] | RIO_ | 01 | 33 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST809 | ESP HOPPER 1 SCREW | ROTATION GUARD |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST809 | ESP HOPPER 1 SCREW |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | #N/A | #N/A | #N/A
BB1ST850 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-433._L0 | [23 empty] | RIO_ | 01 | 38 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST850 | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST850 | BOTTOM ASH CONVEYOR |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST850/01 | BB1ST850/02 | BB1ST850/03
BB1ST852 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-434._L0 | [23 empty] | RIO_ | 01 | 39 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST852 | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST852 | 2ND PASS FLY ASH ROTARY |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST852/01 | BB1ST852/02 | BB1ST852/03
BB1ST853 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-435._L0 | [23 empty] | RIO_ | 01 | 39 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST853 | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST853 | 3RD PASS FLY ASH ROTARY |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST853/01 | BB1ST853/02 | BB1ST853/03
BB1ST856 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-436._L0 | [23 empty] | RIO_ | 01 | 38 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST856 | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1ST856 | PURIFIED SAND SCREW |  | SPEED SWITCH/ROTATION GUARD | [10 empty] | BB1ST856/01 | BB1ST856/02 | BB1ST856/03
BB1SV001 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV001 | BLOW DOWN TANK COOLING | ON/OFF VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV001 | BLOW DOWN TANK COOLING |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV400 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV400 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV400 | SEALING AIR TO ROTARY |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV401 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV401 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV401 | BOTTOM ASH PURGING AIR |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV402 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV402 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV402 | BOTTOM ASH PURGING AIR |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV405 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV405 | SAND FILLING VALVE | SOLENOID VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV405 | SAND FILLING VALVE |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV406 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV406 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV406 | SEALING AIR TO ROTARY |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV410 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV410 | FEED WATER TANK | OVERFLOW VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV410 | FEED WATER TANK |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV601 | PUSH_FEED | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV601_OUT | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1SV601_IN | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV601 | CONTROL VALVE PUSH | FEEDERS UNLOADING | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV602 | PUSH_FEED | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV602_OUT | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1SV602_IN | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV602 | CONTROL VALVE PUSH | FEEDERS UNLOADING | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV603 | PUSH_FEED | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV603_OUT | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1SV603_IN | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV603 | CONTROL VALVE PUSH | FEEDERS UNLOADING | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV950 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV950 | FUEL SILO FIRE WATER | CONTROL VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV950 | FUEL SILO FIRE WATER |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1SV951 | BIN_VLV | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1SV951 | FUEL POCKET FIRE WATER | CONTROL VALVE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1SV951 | FUEL POCKET FIRE WATER |  | SOLENOID VALVE | [10 empty] | #N/A | #N/A | #N/A
BB1TS501 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TS501 | ESP INSULATOR 1 | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TS501 | ESP INSULATOR 1 |  | TEMPERATURE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1TS508 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TS508 | ESP INSULATOR 2 | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TS508 | ESP INSULATOR 2 |  | TEMPERATURE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1TS600 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-437._L0 | [23 empty] | RIO_ | 01 | 24 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1TS600 | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TS600 | HYDRAULICS UNIT, |  | TEMPERATURE SWITCH | [10 empty] | BB1TS600/01 | BB1TS600/02 | BB1TS600/03
BB1TS608 | MEAS_BIN | POINTIO_1DI_LOOP24VDC | 38025-ELE | 01-438._L0 | [23 empty] | RIO_ | 01 | 23 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1TS608 | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TS608 | HIGH TEMPERATURE SWITCH |  | TEMPERATURE SWITCH | [10 empty] | BB1TS608/01 | BB1TS608/02 | BB1TS608/03
BB1TS804 | MEAS_BIN | [26 empty] | RIO_ | 01 | 34 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1TS804 | ESP ROTARY VALVE | HEATING THERMOSTAT |  | V+ | 2 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TS804 | ESP ROTARY VALVE |  | TEMPERATURE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1TS805 | MEAS_BIN | [26 empty] | RIO_ | 01 | 34 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1TS805 | ESP COLLECTION SCREW | HEATING THERMOSTAT |  | V+ | 1 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TS805 | ESP COLLECTION SCREW |  | TEMPERATURE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1TS808 | MEAS_BIN | [26 empty] | RIO_ | 01 | 33 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1TS808 | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  | V+ | 3 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TS808 | ESP ASH HOPPER 2 |  | TEMPERATURE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1TS809 | MEAS_BIN | [26 empty] | RIO_ | 01 | 34 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1TS809 | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  | V+ | 0 | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TS809 | ESP ASH HOPPER 1 |  | TEMPERATURE SWITCH | [10 empty] | #N/A | #N/A | #N/A
BB1TT001 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT001 | FEED WATER TEMPERATURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT001 | FEED WATER TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT002 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT002 | FEED WATER PUMP 2 | BEARING TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT002 | FEED WATER PUMP 2 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT003 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT003 | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT003 | FW PUMP 1 MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT004 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT004 | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT004 | FW PUMP 1 MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT005 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT005 | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT005 | FW PUMP 2 MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT006 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT006 | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT006 | BLOW DOWN TANK |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT007 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT007 | ACCUMULATOR TEMPERATURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT007 | ACCUMULATOR TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT008 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT008 | TEMPERATURE AFTER | ECONOMIZER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT008 | TEMPERATURE AFTER |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT009 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT009 | TEMPERATURE BEFORE | ECONOMIZER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT009 | TEMPERATURE BEFORE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT012 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT012 | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT012 | CONDENSATE TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT031 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT031 | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT031 | COOLING WATER TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT116 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT116 | STEAM TEMPERATURE TO | AIR PREHEATER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT116 | STEAM TEMPERATURE TO |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT200 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT200 | MAIN STEAM TEMPERATURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT200 | MAIN STEAM TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT201 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT201 | SOOTBLOWING | LINE TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT201 | SOOTBLOWING |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT202 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT202 | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT202 | STEAM OUTLET TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT203 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT203 | 18BAR(G) STEAM | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT203 | 18BAR(G) STEAM |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT308 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT308 | FURNACE TEMPERATURE | CONNECTION |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT308 | FURNACE TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT400 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT400 | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT400 | PRIMARY AIR TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT401 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT401 | BOILER ROOM UPPER PART | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT401 | BOILER ROOM UPPER PART |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT402 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT402 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT402 | PRIMARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT403 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT403 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT403 | PRIMARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT404 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT404 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT404 | PRIMARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT404 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT404 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT404 | PRIMARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT405 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT405 | PRIMARY AIR TEMPERATURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT405 | PRIMARY AIR TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT405 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT405 | PRIMARY AIR TEMPERATURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT405 | PRIMARY AIR TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT406 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT406 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT406 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT406 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT406 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT406 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT407 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT407 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT407 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT407 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT407 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT407 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT408 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT408 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT408 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT408 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT408 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT408 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT409 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT409 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT409 | PRIMARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT409 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT409 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT409 | PRIMARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT410 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT410 | BOILER 1ST DRAFT | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT410 | BOILER 1ST DRAFT |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT410 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT410 | BOILER 1ST DRAFT | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT410 | BOILER 1ST DRAFT |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT411 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT411 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT411 | BOILER TEMPERATURE AFTER |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT411 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT411 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT411 | BOILER TEMPERATURE AFTER |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT412 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT412 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT412 | BOILER TEMPERATURE AFTER |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT412 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT412 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT412 | BOILER TEMPERATURE AFTER |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT413 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT413 | BED TEMPERATURE 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT413 | BED TEMPERATURE 1 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT413 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT413 | BED TEMPERATURE 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT413 | BED TEMPERATURE 1 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT414 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT414 | BED TEMPERATURE 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT414 | BED TEMPERATURE 2 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT414 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT414 | BED TEMPERATURE 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT414 | BED TEMPERATURE 2 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT415 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT415 | BOILER BED TEMPERATURE | MIDDLE LEVEL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT415 | BOILER BED TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT415 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT415 | BOILER BED TEMPERATURE | MIDDLE LEVEL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT415 | BOILER BED TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT416 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT416 | BOILER BED TEMPERATURE | LOWER LEVEL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT416 | BOILER BED TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT416 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT416 | BOILER BED TEMPERATURE | LOWER LEVEL |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT416 | BOILER BED TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT417 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT417 | BED TEMPERATURE 3 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT417 | BED TEMPERATURE 3 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT417 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT417 | BED TEMPERATURE 3 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT417 | BED TEMPERATURE 3 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT418 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT418 | BED TEMPERATURE 4 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT418 | BED TEMPERATURE 4 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT418 | MEAS_ANA_SRS | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT418 | BED TEMPERATURE 4 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT418 | BED TEMPERATURE 4 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT421 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT421 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT421 | PRIMARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT421 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT421 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT421 | PRIMARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT422 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT422 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT422 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT422 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT422 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT422 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT423 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT423 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT423 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT423 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT423 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT423 | SECONDARY AIR FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT430 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT430 | INSTRUMENT AIR TANK | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT430 | INSTRUMENT AIR TANK |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT430 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT430 | INSTRUMENT AIR TANK | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT430 | INSTRUMENT AIR TANK |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT550 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT550 | FLUE GAS TEMPERATURE 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT550 | FLUE GAS TEMPERATURE 1 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT550 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT550 | FLUE GAS TEMPERATURE 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT550 | FLUE GAS TEMPERATURE 1 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT551 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT551 | FLUE GAS TEMPERATURE 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT551 | FLUE GAS TEMPERATURE 2 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT551 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT551 | FLUE GAS TEMPERATURE 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT551 | FLUE GAS TEMPERATURE 2 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT552 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT552 | FLUE GAS TEMPERATURE | BEFORE ESP |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT552 | FLUE GAS TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT552 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT552 | FLUE GAS TEMPERATURE | BEFORE ESP |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT552 | FLUE GAS TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT553 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT553 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT553 | FLUE GAS FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT553 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT553 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT553 | FLUE GAS FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT554 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT554 | FLUE GAS FAN BEARING | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT554 | FLUE GAS FAN BEARING |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT554 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT554 | FLUE GAS FAN BEARING | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT554 | FLUE GAS FAN BEARING |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT555 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT555 | FLUE GAS FAN BEARING | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT555 | FLUE GAS FAN BEARING |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT555 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT555 | FLUE GAS FAN BEARING | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT555 | FLUE GAS FAN BEARING |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT556 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT556 | FLUE GAS TEMPERATURE | BEFORE STACK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT556 | FLUE GAS TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT556 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT556 | FLUE GAS TEMPERATURE | BEFORE STACK |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT556 | FLUE GAS TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT557 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT557 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT557 | FLUE GAS FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT557 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT557 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT557 | FLUE GAS FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT558 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT558 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT558 | FLUE GAS FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT558 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT558 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT558 | FLUE GAS FAN MOTOR |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT650 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT650 | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT650 | SCRAPER CONVEYOR 1 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT650 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT650 | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT650 | SCRAPER CONVEYOR 1 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT652 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT652 | FUEL SILO TEMPERATURE | MEASUREMENT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT652 | FUEL SILO TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT652 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT652 | FUEL SILO TEMPERATURE | MEASUREMENT |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT652 | FUEL SILO TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT653 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT653 | FUEL POCKET TEMPERATURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT653 | FUEL POCKET TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT653 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT653 | FUEL POCKET TEMPERATURE |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT653 | FUEL POCKET TEMPERATURE |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT850 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT850 | ESP ASH HOPPER 1 | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT850 | ESP ASH HOPPER 1 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT850 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT850 | ESP ASH HOPPER 1 | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT850 | ESP ASH HOPPER 1 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT851 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT851 | ESP ASH HOPPER 2 | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT851 | ESP ASH HOPPER 2 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
BB1TT851 | MEAS_ANA | POINTIO_1AI_LOOP24VDC | [25 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | BB1TT851 | ESP ASH HOPPER 2 | TEMPERATURE |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [11 empty] | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1TT851 | ESP ASH HOPPER 2 |  | TEMPERATURE TRANSMITTER | [10 empty] | #N/A | #N/A | #N/A
Note on A1: Author: This is the primary output sheet. All fields are generated, no user input required unless overriding a generated value

## Z_DRAWING
Tag Info | Drawing Filename
_Tag | _Type | Prefix | SubProject | _Base | _Index | _Number | _Append | testIndex | Drawing | Notes
<004> | ELE | 38025-ELE | 1 | 300 | 0 | 300 |  | 130000 | 01-300._L0
BB1FS003 | ELE | 38025-ELE | 1 | 300 | 1 | 301 |  | 130100 | 01-301._L0
BB1GS001 | ELE | 38025-ELE | 1 | 300 | 2 | 302 |  | 130200 | 01-302._L0
BB1GS002 | ELE | 38025-ELE | 1 | 300 | 3 | 303 |  | 130300 | 01-303._L0
BB1GS003 | ELE | 38025-ELE | 1 | 300 | 4 | 304 |  | 130400 | 01-304._L0
BB1GS004 | ELE | 38025-ELE | 1 | 300 | 5 | 305 |  | 130500 | 01-305._L0
BB1GS005 | ELE | 38025-ELE | 1 | 300 | 6 | 306 |  | 130600 | 01-306._L0
BB1GS006 | ELE | 38025-ELE | 1 | 300 | 7 | 307 |  | 130700 | 01-307._L0
BB1GS007 | ELE | 38025-ELE | 1 | 300 | 8 | 308 |  | 130800 | 01-308._L0
BB1GS008 | ELE | 38025-ELE | 1 | 300 | 9 | 309 |  | 130900 | 01-309._L0
BB1GS009 | ELE | 38025-ELE | 1 | 300 | 10 | 310 |  | 131000 | 01-310._L0
BB1GS010 | ELE | 38025-ELE | 1 | 300 | 11 | 311 |  | 131100 | 01-311._L0
BB1GS011 | ELE | 38025-ELE | 1 | 300 | 12 | 312 |  | 131200 | 01-312._L0
BB1GS012 | ELE | 38025-ELE | 1 | 300 | 13 | 313 |  | 131300 | 01-313._L0
BB1GS020 | ELE | 38025-ELE | 1 | 300 | 14 | 314 |  | 131400 | 01-314._L0
BB1GS200 | ELE | 38025-ELE | 1 | 300 | 15 | 315 |  | 131500 | 01-315._L0
BB1GS201 | ELE | 38025-ELE | 1 | 300 | 16 | 316 |  | 131600 | 01-316._L0
BB1GS203 | ELE | 38025-ELE | 1 | 300 | 17 | 317 |  | 131700 | 01-317._L0
BB1GS204 | ELE | 38025-ELE | 1 | 300 | 18 | 318 |  | 131800 | 01-318._L0
BB1GS205 | ELE | 38025-ELE | 1 | 300 | 19 | 319 |  | 131900 | 01-319._L0
BB1GS206 | ELE | 38025-ELE | 1 | 300 | 20 | 320 |  | 132000 | 01-320._L0
BB1GS207 | ELE | 38025-ELE | 1 | 300 | 21 | 321 |  | 132100 | 01-321._L0
BB1GS208 | ELE | 38025-ELE | 1 | 300 | 22 | 322 |  | 132200 | 01-322._L0
BB1GS209 | ELE | 38025-ELE | 1 | 300 | 23 | 323 |  | 132300 | 01-323._L0
BB1GS210 | ELE | 38025-ELE | 1 | 300 | 24 | 324 |  | 132400 | 01-324._L0
BB1GS211 | ELE | 38025-ELE | 1 | 300 | 25 | 325 |  | 132500 | 01-325._L0
BB1GS212 | ELE | 38025-ELE | 1 | 300 | 26 | 326 |  | 132600 | 01-326._L0
BB1GS213 | ELE | 38025-ELE | 1 | 300 | 27 | 327 |  | 132700 | 01-327._L0
BB1GS214 | ELE | 38025-ELE | 1 | 300 | 28 | 328 |  | 132800 | 01-328._L0
BB1GS215 | ELE | 38025-ELE | 1 | 300 | 29 | 329 |  | 132900 | 01-329._L0
BB1GS216 | ELE | 38025-ELE | 1 | 300 | 30 | 330 |  | 133000 | 01-330._L0
BB1GS217 | ELE | 38025-ELE | 1 | 300 | 31 | 331 |  | 133100 | 01-331._L0
BB1GS218 | ELE | 38025-ELE | 1 | 300 | 32 | 332 |  | 133200 | 01-332._L0
BB1GS219 | ELE | 38025-ELE | 1 | 300 | 33 | 333 |  | 133300 | 01-333._L0
BB1GS220 | ELE | 38025-ELE | 1 | 300 | 34 | 334 |  | 133400 | 01-334._L0
BB1GS221 | ELE | 38025-ELE | 1 | 300 | 35 | 335 |  | 133500 | 01-335._L0
BB1GS222 | ELE | 38025-ELE | 1 | 300 | 36 | 336 |  | 133600 | 01-336._L0
BB1GS223 | ELE | 38025-ELE | 1 | 300 | 37 | 337 |  | 133700 | 01-337._L0
BB1GS224 | ELE | 38025-ELE | 1 | 300 | 38 | 338 |  | 133800 | 01-338._L0
BB1GS225 | ELE | 38025-ELE | 1 | 300 | 39 | 339 |  | 133900 | 01-339._L0
BB1GS226 | ELE | 38025-ELE | 1 | 300 | 40 | 340 |  | 134000 | 01-340._L0
BB1GS227 | ELE | 38025-ELE | 1 | 300 | 41 | 341 |  | 134100 | 01-341._L0
BB1GS228 | ELE | 38025-ELE | 1 | 300 | 42 | 342 |  | 134200 | 01-342._L0
BB1GS230 | ELE | 38025-ELE | 1 | 300 | 43 | 343 |  | 134300 | 01-343._L0
BB1GS231 | ELE | 38025-ELE | 1 | 300 | 44 | 344 |  | 134400 | 01-344._L0
BB1GS232 | ELE | 38025-ELE | 1 | 300 | 45 | 345 |  | 134500 | 01-345._L0
BB1GS233 | ELE | 38025-ELE | 1 | 300 | 46 | 346 |  | 134600 | 01-346._L0
BB1GS600 | ELE | 38025-ELE | 1 | 300 | 47 | 347 |  | 134700 | 01-347._L0
BB1GS601 | ELE | 38025-ELE | 1 | 300 | 48 | 348 |  | 134800 | 01-348._L0
BB1GS602 | ELE | 38025-ELE | 1 | 300 | 49 | 349 |  | 134900 | 01-349._L0
BB1GS603 | ELE | 38025-ELE | 1 | 300 | 50 | 350 |  | 135000 | 01-350._L0
BB1GS604 | ELE | 38025-ELE | 1 | 300 | 51 | 351 |  | 135100 | 01-351._L0
BB1GS605 | ELE | 38025-ELE | 1 | 300 | 52 | 352 |  | 135200 | 01-352._L0
BB1GS606 | ELE | 38025-ELE | 1 | 300 | 53 | 353 |  | 135300 | 01-353._L0
BB1GS607 | ELE | 38025-ELE | 1 | 300 | 54 | 354 |  | 135400 | 01-354._L0
BB1GS608 | ELE | 38025-ELE | 1 | 300 | 55 | 355 |  | 135500 | 01-355._L0
BB1GS609 | ELE | 38025-ELE | 1 | 300 | 56 | 356 |  | 135600 | 01-356._L0
BB1GS610 | ELE | 38025-ELE | 1 | 300 | 57 | 357 |  | 135700 | 01-357._L0
BB1GS611 | ELE | 38025-ELE | 1 | 300 | 58 | 358 |  | 135800 | 01-358._L0
BB1GS612 | ELE | 38025-ELE | 1 | 300 | 59 | 359 |  | 135900 | 01-359._L0
BB1GS613 | ELE | 38025-ELE | 1 | 300 | 60 | 360 |  | 136000 | 01-360._L0
BB1GS614 | ELE | 38025-ELE | 1 | 300 | 61 | 361 |  | 136100 | 01-361._L0
BB1GS615 | ELE | 38025-ELE | 1 | 300 | 62 | 362 |  | 136200 | 01-362._L0
BB1GS616 | ELE | 38025-ELE | 1 | 300 | 63 | 363 |  | 136300 | 01-363._L0
BB1GS617 | ELE | 38025-ELE | 1 | 300 | 64 | 364 |  | 136400 | 01-364._L0
BB1GS618 | ELE | 38025-ELE | 1 | 300 | 65 | 365 |  | 136500 | 01-365._L0
BB1GS619 | ELE | 38025-ELE | 1 | 300 | 66 | 366 |  | 136600 | 01-366._L0
BB1GS620 | ELE | 38025-ELE | 1 | 300 | 67 | 367 |  | 136700 | 01-367._L0
BB1GS621 | ELE | 38025-ELE | 1 | 300 | 68 | 368 |  | 136800 | 01-368._L0
BB1GS622 | ELE | 38025-ELE | 1 | 300 | 69 | 369 |  | 136900 | 01-369._L0
BB1GS623 | ELE | 38025-ELE | 1 | 300 | 70 | 370 |  | 137000 | 01-370._L0
BB1GS650 | ELE | 38025-ELE | 1 | 300 | 71 | 371 |  | 137100 | 01-371._L0
BB1GS651 | ELE | 38025-ELE | 1 | 300 | 72 | 372 |  | 137200 | 01-372._L0
BB1GS652 | ELE | 38025-ELE | 1 | 300 | 73 | 373 |  | 137300 | 01-373._L0
BB1GS653 | ELE | 38025-ELE | 1 | 300 | 74 | 374 |  | 137400 | 01-374._L0
BB1GS654 | ELE | 38025-ELE | 1 | 300 | 75 | 375 |  | 137500 | 01-375._L0
BB1GS655 | ELE | 38025-ELE | 1 | 300 | 76 | 376 |  | 137600 | 01-376._L0
BB1GS656 | ELE | 38025-ELE | 1 | 300 | 77 | 377 |  | 137700 | 01-377._L0
BB1GS659 | ELE | 38025-ELE | 1 | 300 | 78 | 378 |  | 137800 | 01-378._L0
BB1GS660 | ELE | 38025-ELE | 1 | 300 | 79 | 379 |  | 137900 | 01-379._L0
BB1GS661 | ELE | 38025-ELE | 1 | 300 | 80 | 380 |  | 138000 | 01-380._L0
BB1GS662 | ELE | 38025-ELE | 1 | 300 | 81 | 381 |  | 138100 | 01-381._L0
BB1GS663 | ELE | 38025-ELE | 1 | 300 | 82 | 382 |  | 138200 | 01-382._L0
BB1GS800 | ELE | 38025-ELE | 1 | 300 | 83 | 383 |  | 138300 | 01-383._L0
BB1GS801 | ELE | 38025-ELE | 1 | 300 | 84 | 384 |  | 138400 | 01-384._L0
BB1GS802 | ELE | 38025-ELE | 1 | 300 | 85 | 385 |  | 138500 | 01-385._L0
BB1GS803 | ELE | 38025-ELE | 1 | 300 | 86 | 386 |  | 138600 | 01-386._L0
BB1GS850 | ELE | 38025-ELE | 1 | 300 | 87 | 387 |  | 138700 | 01-387._L0
BB1GS851 | ELE | 38025-ELE | 1 | 300 | 88 | 388 |  | 138800 | 01-388._L0
BB1GS852 | ELE | 38025-ELE | 1 | 300 | 89 | 389 |  | 138900 | 01-389._L0
BB1GS853 | ELE | 38025-ELE | 1 | 300 | 90 | 390 |  | 139000 | 01-390._L0
BB1GS854 | ELE | 38025-ELE | 1 | 300 | 91 | 391 |  | 139100 | 01-391._L0
BB1GS855 | ELE | 38025-ELE | 1 | 300 | 92 | 392 |  | 139200 | 01-392._L0
BB1GS856 | ELE | 38025-ELE | 1 | 300 | 93 | 393 |  | 139300 | 01-393._L0
BB1GS857 | ELE | 38025-ELE | 1 | 300 | 94 | 394 |  | 139400 | 01-394._L0
BB1GS858 | ELE | 38025-ELE | 1 | 300 | 95 | 395 |  | 139500 | 01-395._L0
BB1LS600 | ELE | 38025-ELE | 1 | 300 | 96 | 396 |  | 139600 | 01-396._L0
BB1LS608 | ELE | 38025-ELE | 1 | 300 | 97 | 397 |  | 139700 | 01-397._L0
BB1LS650 | ELE | 38025-ELE | 1 | 300 | 98 | 398 |  | 139800 | 01-398._L0
BB1LS651 | ELE | 38025-ELE | 1 | 300 | 99 | 399 |  | 139900 | 01-399._L0
BB1LS652 | ELE | 38025-ELE | 1 | 300 | 100 | 400 |  | 140000 | 01-400._L0
BB1LS653 | ELE | 38025-ELE | 1 | 300 | 101 | 401 |  | 140100 | 01-401._L0
BB1LS654 | ELE | 38025-ELE | 1 | 300 | 102 | 402 |  | 140200 | 01-402._L0
BB1LS655 | ELE | 38025-ELE | 1 | 300 | 103 | 403 |  | 140300 | 01-403._L0
BB1LS656 | ELE | 38025-ELE | 1 | 300 | 104 | 404 |  | 140400 | 01-404._L0
BB1LS657 | ELE | 38025-ELE | 1 | 300 | 105 | 405 |  | 140500 | 01-405._L0
BB1LS658 | ELE | 38025-ELE | 1 | 300 | 106 | 406 |  | 140600 | 01-406._L0
BB1LS659 | ELE | 38025-ELE | 1 | 300 | 107 | 407 |  | 140700 | 01-407._L0
BB1LS660 | ELE | 38025-ELE | 1 | 300 | 108 | 408 |  | 140800 | 01-408._L0
BB1LS661 | ELE | 38025-ELE | 1 | 300 | 109 | 409 |  | 140900 | 01-409._L0
BB1LS700 | ELE | 38025-ELE | 1 | 300 | 110 | 410 |  | 141000 | 01-410._L0
BB1LS701 | ELE | 38025-ELE | 1 | 300 | 111 | 411 |  | 141100 | 01-411._L0
BB1LS850 | ELE | 38025-ELE | 1 | 300 | 112 | 412 |  | 141200 | 01-412._L0
BB1LS851 | ELE | 38025-ELE | 1 | 300 | 113 | 413 |  | 141300 | 01-413._L0
BB1PS600 | ELE | 38025-ELE | 1 | 300 | 114 | 414 |  | 141400 | 01-414._L0
BB1PS601 | ELE | 38025-ELE | 1 | 300 | 115 | 415 |  | 141500 | 01-415._L0
BB1PS602 | ELE | 38025-ELE | 1 | 300 | 116 | 416 |  | 141600 | 01-416._L0
BB1PS603 | ELE | 38025-ELE | 1 | 300 | 117 | 417 |  | 141700 | 01-417._L0
BB1PS604 | ELE | 38025-ELE | 1 | 300 | 118 | 418 |  | 141800 | 01-418._L0
BB1PS605 | ELE | 38025-ELE | 1 | 300 | 119 | 419 |  | 141900 | 01-419._L0
BB1ST649 | ELE | 38025-ELE | 1 | 300 | 120 | 420 |  | 142000 | 01-420._L0
BB1ST650 | ELE | 38025-ELE | 1 | 300 | 121 | 421 |  | 142100 | 01-421._L0
BB1ST651 | ELE | 38025-ELE | 1 | 300 | 122 | 422 |  | 142200 | 01-422._L0
BB1ST652 | ELE | 38025-ELE | 1 | 300 | 123 | 423 |  | 142300 | 01-423._L0
BB1ST653 | ELE | 38025-ELE | 1 | 300 | 124 | 424 |  | 142400 | 01-424._L0
BB1ST654 | ELE | 38025-ELE | 1 | 300 | 125 | 425 |  | 142500 | 01-425._L0
BB1ST655 | ELE | 38025-ELE | 1 | 300 | 126 | 426 |  | 142600 | 01-426._L0
BB1ST656 | ELE | 38025-ELE | 1 | 300 | 127 | 427 |  | 142700 | 01-427._L0
BB1ST657 | ELE | 38025-ELE | 1 | 300 | 128 | 428 |  | 142800 | 01-428._L0
BB1ST659 | ELE | 38025-ELE | 1 | 300 | 129 | 429 |  | 142900 | 01-429._L0
BB1ST673 | ELE | 38025-ELE | 1 | 300 | 130 | 430 |  | 143000 | 01-430._L0
BB1ST674 | ELE | 38025-ELE | 1 | 300 | 131 | 431 |  | 143100 | 01-431._L0
BB1ST675 | ELE | 38025-ELE | 1 | 300 | 132 | 432 |  | 143200 | 01-432._L0
BB1ST850 | ELE | 38025-ELE | 1 | 300 | 133 | 433 |  | 143300 | 01-433._L0
BB1ST852 | ELE | 38025-ELE | 1 | 300 | 134 | 434 |  | 143400 | 01-434._L0
BB1ST853 | ELE | 38025-ELE | 1 | 300 | 135 | 435 |  | 143500 | 01-435._L0
BB1ST856 | ELE | 38025-ELE | 1 | 300 | 136 | 436 |  | 143600 | 01-436._L0
BB1TS600 | ELE | 38025-ELE | 1 | 300 | 137 | 437 |  | 143700 | 01-437._L0
BB1TS608 | ELE | 38025-ELE | 1 | 300 | 138 | 438 |  | 143800 | 01-438._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 0 | 100 |  | 110000 | 01-100._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 1 | 101 |  | 110100 | 01-101._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 2 | 102 |  | 110200 | 01-102._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 3 | 103 |  | 110300 | 01-103._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 4 | 104 |  | 110400 | 01-104._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 5 | 105 |  | 110500 | 01-105._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 6 | 106 |  | 110600 | 01-106._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 7 | 107 |  | 110700 | 01-107._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 8 | 108 |  | 110800 | 01-108._L0
DETAIL | ELE | 38025-ELE | 1 | 100 | 9 | 109 |  | 110900 | 01-109._L0
BB1EM650 | ELE | 38025-ELE | 1 | 500 | 0 | 500 |  | 150000 | 01-500._L0
BB1EM658 | ELE | 38025-ELE | 1 | 500 | 1 | 501 |  | 150100 | 01-501._L0
BB1EM659 | ELE | 38025-ELE | 1 | 500 | 2 | 502 |  | 150200 | 01-502._L0
BB1EM662 | ELE | 38025-ELE | 1 | 500 | 3 | 503 |  | 150300 | 01-503._L0
BB1EM663 | ELE | 38025-ELE | 1 | 500 | 4 | 504 |  | 150400 | 01-504._L0
BB1EM664 | ELE | 38025-ELE | 1 | 500 | 5 | 505 |  | 150500 | 01-505._L0
BB1EM665 | ELE | 38025-ELE | 1 | 500 | 6 | 506 |  | 150600 | 01-506._L0
BB1EM672 | ELE | 38025-ELE | 1 | 500 | 7 | 507 |  | 150700 | 01-507._L0
BB1EM676 | ELE | 38025-ELE | 1 | 500 | 8 | 508 |  | 150800 | 01-508._L0
BB1EM852 | ELE | 38025-ELE | 1 | 500 | 9 | 509 |  | 150900 | 01-509._L0
| ELE | 38025-ELE | 1 | 500 | 10 | 510 |  | 151000 | 01-510._L0
| ELE | 38025-ELE | 1 | 500 | 11 | 511 |  | 151100 | 01-511._L0
| ELE | 38025-ELE | 1 | 500 | 12 | 512 |  | 151200 | 01-512._L0
| ELE | 38025-ELE | 1 | 500 | 13 | 513 |  | 151300 | 01-513._L0
| ELE | 38025-ELE | 1 | 500 | 14 | 514 |  | 151400 | 01-514._L0
| ELE | 38025-ELE | 1 | 500 | 15 | 515 |  | 151500 | 01-515._L0
| ELE | 38025-ELE | 1 | 500 | 16 | 516 |  | 151600 | 01-516._L0
| ELE | 38025-ELE | 1 | 500 | 17 | 517 |  | 151700 | 01-517._L0
| ELE | 38025-ELE | 1 | 500 | 18 | 518 |  | 151800 | 01-518._L0
| ELE | 38025-ELE | 1 | 500 | 19 | 519 |  | 151900 | 01-519._L0
| ELE | 38025-ELE | 1 |  | 20 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 21 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 22 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 23 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 24 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 25 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 26 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 27 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 28 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 29 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 30 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 31 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 32 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 33 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 34 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 35 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 36 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 37 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 38 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 39 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 40 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 41 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 42 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 43 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 44 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 45 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 46 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 47 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 48 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 49 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 50 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 51 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 52 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 53 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 54 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 55 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 56 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 57 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 58 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 59 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 60 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 61 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 62 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 63 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 64 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 65 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 66 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 67 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 68 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 69 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 70 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 71 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 72 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 73 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 74 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 75 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 76 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 77 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 78 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 79 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 80 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 81 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 82 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 83 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 84 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 85 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 86 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 87 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 88 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 89 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 90 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 91 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 92 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 93 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 94 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 95 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 96 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 97 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 98 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 99 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 100 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 101 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 102 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 103 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 104 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 105 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 106 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 107 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 108 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 109 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 110 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 111 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 112 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 113 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 114 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 115 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 116 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 117 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 118 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 119 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 120 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 121 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 122 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 123 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 124 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 125 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 126 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 127 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 128 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 129 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 130 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 131 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 132 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 133 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 134 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 135 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 136 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 137 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 138 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 139 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 140 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 141 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 142 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 143 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 144 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 145 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 146 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 147 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 148 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 149 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 150 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 151 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 152 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 153 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 154 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 155 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 156 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 157 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 158 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 159 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 160 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 161 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 162 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 163 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 164 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 165 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 166 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 167 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 168 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 169 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 170 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 171 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 172 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 173 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 174 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 175 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 176 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 177 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 178 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 179 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 180 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 181 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 182 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 183 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 184 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 185 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 186 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 187 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 188 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 189 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 190 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 191 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 192 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 193 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 194 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 195 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 196 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 197 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 198 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 199 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 200 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 201 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 202 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 203 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 204 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 205 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 206 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 207 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 208 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 209 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 210 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 211 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 212 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 213 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 214 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 215 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 216 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 217 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 218 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 219 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 220 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 221 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 222 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 223 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 224 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 225 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 226 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 227 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 228 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 229 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 230 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 231 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 232 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 233 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 234 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 235 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 236 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 237 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 238 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 239 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 240 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 241 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 242 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 243 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 244 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 245 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 246 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 247 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 248 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 249 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 250 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 251 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 252 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 253 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 254 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 255 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 256 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 257 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 258 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 259 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 260 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 261 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 262 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 263 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 264 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 265 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 266 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 267 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 268 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 269 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 270 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 271 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 272 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 273 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 274 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 275 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 276 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 277 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 278 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 279 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 280 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 281 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 282 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 283 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 284 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 285 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 286 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 287 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 288 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 289 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 290 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 291 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 292 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 293 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 294 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 295 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 296 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 297 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 298 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 299 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 300 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 301 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 302 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 303 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 304 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 305 |  |  | #VALUE! | 01-._L0
| ELE | 38025-ELE | 1 |  | 306 |  |  | #VALUE! | 01-._L0
Note on A1: Author: Generation of drawing number set is performed on this page

## X_PANEL
Tag | Description | _DeviceCount | 24VDC | 0VDC | Terminal | Fuse | 230VL1 | 230VN | DBTerminal | DBFuse | DBBreaker | Notes
KPA_FLOORX_IO | KPA NON ASSIGNED IO | 412
KPA_FLOOR0_IO | KPA LEVEL 0 REMOTE IO CABINET | 0
KPA_FLOOR1_IO | KPA LEVEL 1 REMOTE IO CABINET | 0
KPA_FLOOR2_IO | KPA LEVEL 2 REMOTE IO CABINET | 0
KPA_FLOOR3_IO | KPA LEVEL 3 REMOTE IO CABINET | 0
KPA_FLOOR4_IO | KPA LEVEL 4 REMOTE IO CABINET | 0
KPA_FUEL_STATION_IO | KPA FUEL STATION REMOTE IO CABINET | 0
KPA_MCC | KPA REMOTE IO INTERNAL TO MCC | 1
KPA_PLC | KPA PLC CABINET | 0
ESP_PLC | ESP PLC CABINET | 0
ESP_MCC | ESP REMOTE IO INTERNAL TO MCC | 0
0
Panel Assignment |  |  | Indices
_Drawing | _Tag | Assignment | 24VDC | 0VDC | Terminal | Fuse | 230V | 230VN | DBTerminal | DBFuse | DBBreaker | Notes | Q1CATN | Q1CATD | Q1NAME1 | Q1NAME2 | Q1TCATN | Q1TCATD | Q1TNAME | Q1TSETTO
01-100._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q100 |  | 110000 | F110000 | Q100 | INCOMER
01-101._L0 | DETAIL | KPA_MCC |  |  |  |  | Q101 |  | 110100 | F110100 | Q101 | PWR MONITOR
01-102._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q102 |  | 110200 | F110200 | Q102 | AHF
01-103._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q103 |  | 110300 | F110300 | Q103 | SURGE PROTECTION
01-104._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q104 |  | 110400 | F110400 | Q104 | FEEDERS
01-105._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q108 |  | 110500 | F110500 | Q108 | FEEDERS
01-106._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q111 |  | 110600 | F110600 | Q111 | FEEDERS
01-107._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q110700 |  | 110700 | F110700 | Q110700
01-108._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q110800 |  | 110800 | F110800 | Q110800
01-109._L0 | DETAIL | KPA_FLOORX_IO |  |  |  |  | Q110900 |  | 110900 | F110900 | Q110900
01-500._L0 | BB1EM650 | KPA_FLOORX_IO |  |  |  |  | Q150000 | N | 150000 | F150000 | Q150000 | GV2L10 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A
01-501._L0 | BB1EM658 | KPA_FLOORX_IO |  |  |  |  | Q150100 | N | 150100 | F150100 | Q150100 | NSX100H/MA50 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A
01-502._L0 | BB1EM659 | KPA_FLOORX_IO |  |  |  |  | Q150200 | N | 150200 | F150200 | Q150200 | GV2L14 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A
01-503._L0 | BB1EM662 | KPA_FLOORX_IO |  |  |  |  | Q150300 | N | 150300 | F150300 | Q150300 | NSX100H/MA100 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A
01-504._L0 | BB1EM663 | KPA_FLOORX_IO |  |  |  |  | Q150400 | N | 150400 | F150400 | Q150400 | GV2L14 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A
01-505._L0 | BB1EM664 | KPA_FLOORX_IO |  |  |  |  | Q150500 | N | 150500 | F150500 | Q150500 | GV2L16 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A
01-506._L0 | BB1EM665 | KPA_FLOORX_IO |  |  |  |  | Q150600 | N | 150600 | F150600 | Q150600 | GV2L16 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A
01-507._L0 | BB1EM672 | KPA_FLOORX_IO |  |  |  |  | Q150700 | N | 150700 | F150700 | Q150700 | NSX100H/MA50 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A
01-508._L0 | BB1EM676 | KPA_FLOORX_IO |  |  |  |  | Q150800 | N | 150800 | F150800 | Q150800 | GV2L22 | GV2L22 | 3P CIRCUIT BREAKER, TESYS GV2L, 25A | SCHNEIDER GV2L22 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 22A
01-509._L0 | BB1EM852 | KPA_FLOORX_IO |  |  |  |  | Q150900 | N | 150900 | F150900 | Q150900 | GV2L10 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A
01-510._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151000 |  | 151000 | F151000 | Q151000
01-511._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151100 |  | 151100 | F151100 | Q151100
01-512._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151200 |  | 151200 | F151200 | Q151200
01-513._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151300 |  | 151300 | F151300 | Q151300
01-514._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151400 |  | 151400 | F151400 | Q151400
01-515._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151500 |  | 151500 | F151500 | Q151500
01-516._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151600 |  | 151600 | F151600 | Q151600
01-517._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151700 |  | 151700 | F151700 | Q151700
01-518._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151800 |  | 151800 | F151800 | Q151800
01-519._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | Q151900 |  | 151900 | F151900 | Q151900
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
01-._L0 | 0 | KPA_FLOORX_IO |  |  |  |  | #VALUE! |  | #VALUE! | #VALUE! | #VALUE!
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | KPA_FLOORX_IO |  |  |  |  | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | [5 empty] | #N/A |  | #N/A | #N/A | #N/A
0 | 0 | [5 empty] | #N/A |  | #N/A | #N/A | #N/A

## W_WIRE
Tag | _Typical | W1 | W2 | WireNameLoopA | WireNameLoopB | WireNameIO | WireNameUserA | WireNameUserB | Notes
<004> | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1FS003 | MEAS_BIN | RIO_01:36.DI:V+ BB1FS003 | RIO_01:36.DI:01 BB1FS003 | RIO_01:36.DI:V+ BB1FS003 | BB1FS003 | RIO_01:36.DI:01 BB1FS003 | BB1FS003/K1
BB1GS001 | MEAS_BIN | RIO_01:02.DI:V+ BB1GS001 | RIO_01:02.DI:00 BB1GS001 | RIO_01:02.DI:V+ BB1GS001 | BB1GS001 | RIO_01:02.DI:00 BB1GS001 | BB1GS001/K1
BB1GS002 | MEAS_BIN | RIO_01:02.DI:V+ BB1GS002 | RIO_01:02.DI:01 BB1GS002 | RIO_01:02.DI:V+ BB1GS002 | BB1GS002 | RIO_01:02.DI:01 BB1GS002 | BB1GS002/K1
BB1GS003 | MEAS_BIN | RIO_01:01.DI:V+ BB1GS003 | RIO_01:01.DI:03 BB1GS003 | RIO_01:01.DI:V+ BB1GS003 | BB1GS003 | RIO_01:01.DI:03 BB1GS003 | BB1GS003/K1
BB1GS004 | MEAS_BIN | RIO_01:01.DI:V+ BB1GS004 | RIO_01:01.DI:02 BB1GS004 | RIO_01:01.DI:V+ BB1GS004 | BB1GS004 | RIO_01:01.DI:02 BB1GS004 | BB1GS004/K1
BB1GS005 | MEAS_BIN | RIO_01:02.DI:V+ BB1GS005 | RIO_01:02.DI:02 BB1GS005 | RIO_01:02.DI:V+ BB1GS005 | BB1GS005 | RIO_01:02.DI:02 BB1GS005 | BB1GS005/K1
BB1GS006 | MEAS_BIN | RIO_01:02.DI:V+ BB1GS006 | RIO_01:02.DI:03 BB1GS006 | RIO_01:02.DI:V+ BB1GS006 | BB1GS006 | RIO_01:02.DI:03 BB1GS006 | BB1GS006/K1
BB1GS007 | MEAS_BIN | RIO_01:03.DI:V+ BB1GS007 | RIO_01:03.DI:00 BB1GS007 | RIO_01:03.DI:V+ BB1GS007 | BB1GS007 | RIO_01:03.DI:00 BB1GS007 | BB1GS007/K1
BB1GS008 | MEAS_BIN | RIO_01:03.DI:V+ BB1GS008 | RIO_01:03.DI:01 BB1GS008 | RIO_01:03.DI:V+ BB1GS008 | BB1GS008 | RIO_01:03.DI:01 BB1GS008 | BB1GS008/K1
BB1GS009 | MEAS_BIN | RIO_01:03.DI:V+ BB1GS009 | RIO_01:03.DI:02 BB1GS009 | RIO_01:03.DI:V+ BB1GS009 | BB1GS009 | RIO_01:03.DI:02 BB1GS009 | BB1GS009/K1
BB1GS010 | MEAS_BIN | RIO_01:03.DI:V+ BB1GS010 | RIO_01:03.DI:03 BB1GS010 | RIO_01:03.DI:V+ BB1GS010 | BB1GS010 | RIO_01:03.DI:03 BB1GS010 | BB1GS010/K1
BB1GS011 | MEAS_BIN | RIO_01:04.DI:V+ BB1GS011 | RIO_01:04.DI:00 BB1GS011 | RIO_01:04.DI:V+ BB1GS011 | BB1GS011 | RIO_01:04.DI:00 BB1GS011 | BB1GS011/K1
BB1GS012 | MEAS_BIN | RIO_01:04.DI:V+ BB1GS012 | RIO_01:04.DI:01 BB1GS012 | RIO_01:04.DI:V+ BB1GS012 | BB1GS012 | RIO_01:04.DI:01 BB1GS012 | BB1GS012/K1
BB1GS020 | MEAS_BIN | RIO_01:39.DI:V+ BB1GS020 | RIO_01:39.DI:03 BB1GS020 | RIO_01:39.DI:V+ BB1GS020 | BB1GS020 | RIO_01:39.DI:03 BB1GS020 | BB1GS020/K1
BB1GS200 | MEAS_BIN | RIO_01:06.DI:V+ BB1GS200 | RIO_01:06.DI:00 BB1GS200 | RIO_01:06.DI:V+ BB1GS200 | BB1GS200 | RIO_01:06.DI:00 BB1GS200 | BB1GS200/K1
BB1GS201 | MEAS_BIN | RIO_01:06.DI:V+ BB1GS201 | RIO_01:06.DI:01 BB1GS201 | RIO_01:06.DI:V+ BB1GS201 | BB1GS201 | RIO_01:06.DI:01 BB1GS201 | BB1GS201/K1
BB1GS203 | MEAS_BIN | RIO_01:06.DI:V+ BB1GS203 | RIO_01:06.DI:02 BB1GS203 | RIO_01:06.DI:V+ BB1GS203 | BB1GS203 | RIO_01:06.DI:02 BB1GS203 | BB1GS203/K1
BB1GS204 | MEAS_BIN | RIO_01:06.DI:V+ BB1GS204 | RIO_01:06.DI:03 BB1GS204 | RIO_01:06.DI:V+ BB1GS204 | BB1GS204 | RIO_01:06.DI:03 BB1GS204 | BB1GS204/K1
BB1GS205 | MEAS_BIN | RIO_01:07.DI:V+ BB1GS205 | RIO_01:07.DI:00 BB1GS205 | RIO_01:07.DI:V+ BB1GS205 | BB1GS205 | RIO_01:07.DI:00 BB1GS205 | BB1GS205/K1
BB1GS206 | MEAS_BIN | RIO_01:07.DI:V+ BB1GS206 | RIO_01:07.DI:01 BB1GS206 | RIO_01:07.DI:V+ BB1GS206 | BB1GS206 | RIO_01:07.DI:01 BB1GS206 | BB1GS206/K1
BB1GS207 | MEAS_BIN | RIO_01:07.DI:V+ BB1GS207 | RIO_01:07.DI:02 BB1GS207 | RIO_01:07.DI:V+ BB1GS207 | BB1GS207 | RIO_01:07.DI:02 BB1GS207 | BB1GS207/K1
BB1GS208 | MEAS_BIN | RIO_01:07.DI:V+ BB1GS208 | RIO_01:07.DI:03 BB1GS208 | RIO_01:07.DI:V+ BB1GS208 | BB1GS208 | RIO_01:07.DI:03 BB1GS208 | BB1GS208/K1
BB1GS209 | MEAS_BIN | RIO_01:08.DI:V+ BB1GS209 | RIO_01:08.DI:00 BB1GS209 | RIO_01:08.DI:V+ BB1GS209 | BB1GS209 | RIO_01:08.DI:00 BB1GS209 | BB1GS209/K1
BB1GS210 | MEAS_BIN | RIO_01:08.DI:V+ BB1GS210 | RIO_01:08.DI:01 BB1GS210 | RIO_01:08.DI:V+ BB1GS210 | BB1GS210 | RIO_01:08.DI:01 BB1GS210 | BB1GS210/K1
BB1GS211 | MEAS_BIN | RIO_01:08.DI:V+ BB1GS211 | RIO_01:08.DI:02 BB1GS211 | RIO_01:08.DI:V+ BB1GS211 | BB1GS211 | RIO_01:08.DI:02 BB1GS211 | BB1GS211/K1
BB1GS212 | MEAS_BIN | RIO_01:08.DI:V+ BB1GS212 | RIO_01:08.DI:03 BB1GS212 | RIO_01:08.DI:V+ BB1GS212 | BB1GS212 | RIO_01:08.DI:03 BB1GS212 | BB1GS212/K1
BB1GS213 | MEAS_BIN | RIO_01:09.DI:V+ BB1GS213 | RIO_01:09.DI:00 BB1GS213 | RIO_01:09.DI:V+ BB1GS213 | BB1GS213 | RIO_01:09.DI:00 BB1GS213 | BB1GS213/K1
BB1GS214 | MEAS_BIN | RIO_01:09.DI:V+ BB1GS214 | RIO_01:09.DI:01 BB1GS214 | RIO_01:09.DI:V+ BB1GS214 | BB1GS214 | RIO_01:09.DI:01 BB1GS214 | BB1GS214/K1
BB1GS215 | MEAS_BIN | RIO_01:13.DI:V+ BB1GS215 | RIO_01:13.DI:00 BB1GS215 | RIO_01:13.DI:V+ BB1GS215 | BB1GS215 | RIO_01:13.DI:00 BB1GS215 | BB1GS215/K1
BB1GS216 | MEAS_BIN | RIO_01:13.DI:V+ BB1GS216 | RIO_01:13.DI:01 BB1GS216 | RIO_01:13.DI:V+ BB1GS216 | BB1GS216 | RIO_01:13.DI:01 BB1GS216 | BB1GS216/K1
BB1GS217 | MEAS_BIN | RIO_01:11.DI:V+ BB1GS217 | RIO_01:11.DI:00 BB1GS217 | RIO_01:11.DI:V+ BB1GS217 | BB1GS217 | RIO_01:11.DI:00 BB1GS217 | BB1GS217/K1
BB1GS218 | MEAS_BIN | RIO_01:11.DI:V+ BB1GS218 | RIO_01:11.DI:01 BB1GS218 | RIO_01:11.DI:V+ BB1GS218 | BB1GS218 | RIO_01:11.DI:01 BB1GS218 | BB1GS218/K1
BB1GS219 | MEAS_BIN | RIO_01:11.DI:V+ BB1GS219 | RIO_01:11.DI:02 BB1GS219 | RIO_01:11.DI:V+ BB1GS219 | BB1GS219 | RIO_01:11.DI:02 BB1GS219 | BB1GS219/K1
BB1GS220 | MEAS_BIN | RIO_01:11.DI:V+ BB1GS220 | RIO_01:11.DI:03 BB1GS220 | RIO_01:11.DI:V+ BB1GS220 | BB1GS220 | RIO_01:11.DI:03 BB1GS220 | BB1GS220/K1
BB1GS221 | MEAS_BIN | RIO_01:04.DI:V+ BB1GS221 | RIO_01:04.DI:02 BB1GS221 | RIO_01:04.DI:V+ BB1GS221 | BB1GS221 | RIO_01:04.DI:02 BB1GS221 | BB1GS221/K1
BB1GS222 | MEAS_BIN | RIO_01:04.DI:V+ BB1GS222 | RIO_01:04.DI:03 BB1GS222 | RIO_01:04.DI:V+ BB1GS222 | BB1GS222 | RIO_01:04.DI:03 BB1GS222 | BB1GS222/K1
BB1GS223 | MEAS_BIN | RIO_01:05.DI:V+ BB1GS223 | RIO_01:05.DI:00 BB1GS223 | RIO_01:05.DI:V+ BB1GS223 | BB1GS223 | RIO_01:05.DI:00 BB1GS223 | BB1GS223/K1
BB1GS224 | MEAS_BIN | RIO_01:05.DI:V+ BB1GS224 | RIO_01:05.DI:01 BB1GS224 | RIO_01:05.DI:V+ BB1GS224 | BB1GS224 | RIO_01:05.DI:01 BB1GS224 | BB1GS224/K1
BB1GS225 | MEAS_BIN | RIO_01:05.DI:V+ BB1GS225 | RIO_01:05.DI:02 BB1GS225 | RIO_01:05.DI:V+ BB1GS225 | BB1GS225 | RIO_01:05.DI:02 BB1GS225 | BB1GS225/K1
BB1GS226 | MEAS_BIN | RIO_01:05.DI:V+ BB1GS226 | RIO_01:05.DI:03 BB1GS226 | RIO_01:05.DI:V+ BB1GS226 | BB1GS226 | RIO_01:05.DI:03 BB1GS226 | BB1GS226/K1
BB1GS227 | MEAS_BIN | RIO_01:09.DI:V+ BB1GS227 | RIO_01:09.DI:02 BB1GS227 | RIO_01:09.DI:V+ BB1GS227 | BB1GS227 | RIO_01:09.DI:02 BB1GS227 | BB1GS227/K1
BB1GS228 | MEAS_BIN | RIO_01:09.DI:V+ BB1GS228 | RIO_01:09.DI:03 BB1GS228 | RIO_01:09.DI:V+ BB1GS228 | BB1GS228 | RIO_01:09.DI:03 BB1GS228 | BB1GS228/K1
BB1GS230 | MEAS_BIN | RIO_01:10.DI:V+ BB1GS230 | RIO_01:10.DI:01 BB1GS230 | RIO_01:10.DI:V+ BB1GS230 | BB1GS230 | RIO_01:10.DI:01 BB1GS230 | BB1GS230/K1
BB1GS231 | MEAS_BIN | RIO_01:10.DI:V+ BB1GS231 | RIO_01:10.DI:00 BB1GS231 | RIO_01:10.DI:V+ BB1GS231 | BB1GS231 | RIO_01:10.DI:00 BB1GS231 | BB1GS231/K1
BB1GS232 | MEAS_BIN | RIO_01:10.DI:V+ BB1GS232 | RIO_01:10.DI:03 BB1GS232 | RIO_01:10.DI:V+ BB1GS232 | BB1GS232 | RIO_01:10.DI:03 BB1GS232 | BB1GS232/K1
BB1GS233 | MEAS_BIN | RIO_01:10.DI:V+ BB1GS233 | RIO_01:10.DI:02 BB1GS233 | RIO_01:10.DI:V+ BB1GS233 | BB1GS233 | RIO_01:10.DI:02 BB1GS233 | BB1GS233/K1
BB1GS600 | MEAS_BIN | RIO_01:22.DI:V+ BB1GS600 | RIO_01:22.DI:03 BB1GS600 | RIO_01:22.DI:V+ BB1GS600 | BB1GS600 | RIO_01:22.DI:03 BB1GS600 | BB1GS600/K1
BB1GS601 | MEAS_BIN | RIO_01:18.DI:V+ BB1GS601 | RIO_01:18.DI:01 BB1GS601 | RIO_01:18.DI:V+ BB1GS601 | BB1GS601 | RIO_01:18.DI:01 BB1GS601 | BB1GS601/K1
BB1GS602 | MEAS_BIN | RIO_01:17.DI:V+ BB1GS602 | RIO_01:17.DI:00 BB1GS602 | RIO_01:17.DI:V+ BB1GS602 | BB1GS602 | RIO_01:17.DI:00 BB1GS602 | BB1GS602/K1
BB1GS603 | MEAS_BIN | RIO_01:16.DI:V+ BB1GS603 | RIO_01:16.DI:00 BB1GS603 | RIO_01:16.DI:V+ BB1GS603 | BB1GS603 | RIO_01:16.DI:00 BB1GS603 | BB1GS603/K1
BB1GS604 | MEAS_BIN | RIO_01:22.DI:V+ BB1GS604 | RIO_01:22.DI:00 BB1GS604 | RIO_01:22.DI:V+ BB1GS604 | BB1GS604 | RIO_01:22.DI:00 BB1GS604 | BB1GS604/K1
BB1GS605 | MEAS_BIN | RIO_01:17.DI:V+ BB1GS605 | RIO_01:17.DI:03 BB1GS605 | RIO_01:17.DI:V+ BB1GS605 | BB1GS605 | RIO_01:17.DI:03 BB1GS605 | BB1GS605/K1
BB1GS606 | MEAS_BIN | RIO_01:14.DI:V+ BB1GS606 | RIO_01:14.DI:00 BB1GS606 | RIO_01:14.DI:V+ BB1GS606 | BB1GS606 | RIO_01:14.DI:00 BB1GS606 | BB1GS606/K1
BB1GS607 | MEAS_BIN | RIO_01:17.DI:V+ BB1GS607 | RIO_01:17.DI:02 BB1GS607 | RIO_01:17.DI:V+ BB1GS607 | BB1GS607 | RIO_01:17.DI:02 BB1GS607 | BB1GS607/K1
BB1GS608 | MEAS_BIN | RIO_01:21.DI:V+ BB1GS608 | RIO_01:21.DI:03 BB1GS608 | RIO_01:21.DI:V+ BB1GS608 | BB1GS608 | RIO_01:21.DI:03 BB1GS608 | BB1GS608/K1
BB1GS609 | MEAS_BIN | RIO_01:19.DI:V+ BB1GS609 | RIO_01:19.DI:01 BB1GS609 | RIO_01:19.DI:V+ BB1GS609 | BB1GS609 | RIO_01:19.DI:01 BB1GS609 | BB1GS609/K1
BB1GS610 | MEAS_BIN | RIO_01:23.DI:V+ BB1GS610 | RIO_01:23.DI:01 BB1GS610 | RIO_01:23.DI:V+ BB1GS610 | BB1GS610 | RIO_01:23.DI:01 BB1GS610 | BB1GS610/K1
BB1GS611 | MEAS_BIN | RIO_01:13.DI:V+ BB1GS611 | RIO_01:13.DI:03 BB1GS611 | RIO_01:13.DI:V+ BB1GS611 | BB1GS611 | RIO_01:13.DI:03 BB1GS611 | BB1GS611/K1
BB1GS612 | MEAS_BIN | RIO_01:20.DI:V+ BB1GS612 | RIO_01:20.DI:01 BB1GS612 | RIO_01:20.DI:V+ BB1GS612 | BB1GS612 | RIO_01:20.DI:01 BB1GS612 | BB1GS612/K1
BB1GS613 | MEAS_BIN | RIO_01:20.DI:V+ BB1GS613 | RIO_01:20.DI:03 BB1GS613 | RIO_01:20.DI:V+ BB1GS613 | BB1GS613 | RIO_01:20.DI:03 BB1GS613 | BB1GS613/K1
BB1GS614 | MEAS_BIN | RIO_01:14.DI:V+ BB1GS614 | RIO_01:14.DI:01 BB1GS614 | RIO_01:14.DI:V+ BB1GS614 | BB1GS614 | RIO_01:14.DI:01 BB1GS614 | BB1GS614/K1
BB1GS615 | MEAS_BIN | RIO_01:15.DI:V+ BB1GS615 | RIO_01:15.DI:01 BB1GS615 | RIO_01:15.DI:V+ BB1GS615 | BB1GS615 | RIO_01:15.DI:01 BB1GS615 | BB1GS615/K1
BB1GS616 | MEAS_BIN | RIO_01:22.DI:V+ BB1GS616 | RIO_01:22.DI:02 BB1GS616 | RIO_01:22.DI:V+ BB1GS616 | BB1GS616 | RIO_01:22.DI:02 BB1GS616 | BB1GS616/K1
BB1GS617 | MEAS_BIN | RIO_01:19.DI:V+ BB1GS617 | RIO_01:19.DI:03 BB1GS617 | RIO_01:19.DI:V+ BB1GS617 | BB1GS617 | RIO_01:19.DI:03 BB1GS617 | BB1GS617/K1
BB1GS618 | MEAS_BIN | RIO_01:21.DI:V+ BB1GS618 | RIO_01:21.DI:01 BB1GS618 | RIO_01:21.DI:V+ BB1GS618 | BB1GS618 | RIO_01:21.DI:01 BB1GS618 | BB1GS618/K1
BB1GS619 | MEAS_BIN | RIO_01:14.DI:V+ BB1GS619 | RIO_01:14.DI:02 BB1GS619 | RIO_01:14.DI:V+ BB1GS619 | BB1GS619 | RIO_01:14.DI:02 BB1GS619 | BB1GS619/K1
BB1GS620 | MEAS_BIN | RIO_01:21.DI:V+ BB1GS620 | RIO_01:21.DI:00 BB1GS620 | RIO_01:21.DI:V+ BB1GS620 | BB1GS620 | RIO_01:21.DI:00 BB1GS620 | BB1GS620/K1
BB1GS621 | MEAS_BIN | RIO_01:13.DI:V+ BB1GS621 | RIO_01:13.DI:02 BB1GS621 | RIO_01:13.DI:V+ BB1GS621 | BB1GS621 | RIO_01:13.DI:02 BB1GS621 | BB1GS621/K1
BB1GS622 | MEAS_BIN | RIO_01:16.DI:V+ BB1GS622 | RIO_01:16.DI:03 BB1GS622 | RIO_01:16.DI:V+ BB1GS622 | BB1GS622 | RIO_01:16.DI:03 BB1GS622 | BB1GS622/K1
BB1GS623 | MEAS_BIN | RIO_01:15.DI:V+ BB1GS623 | RIO_01:15.DI:02 BB1GS623 | RIO_01:15.DI:V+ BB1GS623 | BB1GS623 | RIO_01:15.DI:02 BB1GS623 | BB1GS623/K1
BB1GS650 | MEAS_BIN | RIO_01:16.DI:V+ BB1GS650 | RIO_01:16.DI:02 BB1GS650 | RIO_01:16.DI:V+ BB1GS650 | BB1GS650 | RIO_01:16.DI:02 BB1GS650 | BB1GS650/K1
BB1GS651 | MEAS_BIN | RIO_01:14.DI:V+ BB1GS651 | RIO_01:14.DI:03 BB1GS651 | RIO_01:14.DI:V+ BB1GS651 | BB1GS651 | RIO_01:14.DI:03 BB1GS651 | BB1GS651/K1
BB1GS652 | MEAS_BIN | RIO_01:27.DI:V+ BB1GS652 | RIO_01:27.DI:03 BB1GS652 | RIO_01:27.DI:V+ BB1GS652 | BB1GS652 | RIO_01:27.DI:03 BB1GS652 | BB1GS652/K1
BB1GS653 | MEAS_BIN | RIO_01:28.DI:V+ BB1GS653 | RIO_01:28.DI:00 BB1GS653 | RIO_01:28.DI:V+ BB1GS653 | BB1GS653 | RIO_01:28.DI:00 BB1GS653 | BB1GS653/K1
BB1GS654 | MEAS_BIN | RIO_01:28.DI:V+ BB1GS654 | RIO_01:28.DI:01 BB1GS654 | RIO_01:28.DI:V+ BB1GS654 | BB1GS654 | RIO_01:28.DI:01 BB1GS654 | BB1GS654/K1
BB1GS655 | MEAS_BIN | RIO_01:28.DI:V+ BB1GS655 | RIO_01:28.DI:02 BB1GS655 | RIO_01:28.DI:V+ BB1GS655 | BB1GS655 | RIO_01:28.DI:02 BB1GS655 | BB1GS655/K1
BB1GS656 | MEAS_BIN | RIO_01:31.DI:V+ BB1GS656 | RIO_01:31.DI:02 BB1GS656 | RIO_01:31.DI:V+ BB1GS656 | BB1GS656 | RIO_01:31.DI:02 BB1GS656 | BB1GS656/K1
BB1GS659 | MEAS_BIN | RIO_01:26.DI:V+ BB1GS659 | RIO_01:26.DI:02 BB1GS659 | RIO_01:26.DI:V+ BB1GS659 | BB1GS659 | RIO_01:26.DI:02 BB1GS659 | BB1GS659/K1
BB1GS660 | MEAS_BIN | RIO_01:26.DI:V+ BB1GS660 | RIO_01:26.DI:03 BB1GS660 | RIO_01:26.DI:V+ BB1GS660 | BB1GS660 | RIO_01:26.DI:03 BB1GS660 | BB1GS660/K1
BB1GS661 | MEAS_BIN | RIO_01:25.DI:V+ BB1GS661 | RIO_01:25.DI:03 BB1GS661 | RIO_01:25.DI:V+ BB1GS661 | BB1GS661 | RIO_01:25.DI:03 BB1GS661 | BB1GS661/K1
BB1GS662 | MEAS_BIN | RIO_01:26.DI:V+ BB1GS662 | RIO_01:26.DI:00 BB1GS662 | RIO_01:26.DI:V+ BB1GS662 | BB1GS662 | RIO_01:26.DI:00 BB1GS662 | BB1GS662/K1
BB1GS663 | MEAS_BIN | RIO_01:27.DI:V+ BB1GS663 | RIO_01:27.DI:00 BB1GS663 | RIO_01:27.DI:V+ BB1GS663 | BB1GS663 | RIO_01:27.DI:00 BB1GS663 | BB1GS663/K1
BB1GS800 | MEAS_BIN | RIO_01:36.DI:V+ BB1GS800 | RIO_01:36.DI:03 BB1GS800 | RIO_01:36.DI:V+ BB1GS800 | BB1GS800 | RIO_01:36.DI:03 BB1GS800 | BB1GS800/K1
BB1GS801 | MEAS_BIN | RIO_01:36.DI:V+ BB1GS801 | RIO_01:36.DI:02 BB1GS801 | RIO_01:36.DI:V+ BB1GS801 | BB1GS801 | RIO_01:36.DI:02 BB1GS801 | BB1GS801/K1
BB1GS802 | MEAS_BIN | RIO_01:32.DI:V+ BB1GS802 | RIO_01:32.DI:00 BB1GS802 | RIO_01:32.DI:V+ BB1GS802 | BB1GS802 | RIO_01:32.DI:00 BB1GS802 | BB1GS802/K1
BB1GS803 | MEAS_BIN | RIO_01:32.DI:V+ BB1GS803 | RIO_01:32.DI:01 BB1GS803 | RIO_01:32.DI:V+ BB1GS803 | BB1GS803 | RIO_01:32.DI:01 BB1GS803 | BB1GS803/K1
BB1GS850 | MEAS_BIN | RIO_01:35.DI:V+ BB1GS850 | RIO_01:35.DI:03 BB1GS850 | RIO_01:35.DI:V+ BB1GS850 | BB1GS850 | RIO_01:35.DI:03 BB1GS850 | BB1GS850/K1
BB1GS851 | MEAS_BIN | RIO_01:36.DI:V+ BB1GS851 | RIO_01:36.DI:00 BB1GS851 | RIO_01:36.DI:V+ BB1GS851 | BB1GS851 | RIO_01:36.DI:00 BB1GS851 | BB1GS851/K1
BB1GS852 | MEAS_BIN | RIO_01:39.DI:V+ BB1GS852 | RIO_01:39.DI:00 BB1GS852 | RIO_01:39.DI:V+ BB1GS852 | BB1GS852 | RIO_01:39.DI:00 BB1GS852 | BB1GS852/K1
BB1GS853 | MEAS_BIN | RIO_01:37.DI:V+ BB1GS853 | RIO_01:37.DI:01 BB1GS853 | RIO_01:37.DI:V+ BB1GS853 | BB1GS853 | RIO_01:37.DI:01 BB1GS853 | BB1GS853/K1
BB1GS854 | MEAS_BIN | RIO_01:37.DI:V+ BB1GS854 | RIO_01:37.DI:00 BB1GS854 | RIO_01:37.DI:V+ BB1GS854 | BB1GS854 | RIO_01:37.DI:00 BB1GS854 | BB1GS854/K1
BB1GS855 | MEAS_BIN | RIO_01:34.DI:V+ BB1GS855 | RIO_01:34.DI:03 BB1GS855 | RIO_01:34.DI:V+ BB1GS855 | BB1GS855 | RIO_01:34.DI:03 BB1GS855 | BB1GS855/K1
BB1GS856 | MEAS_BIN | RIO_01:35.DI:V+ BB1GS856 | RIO_01:35.DI:00 BB1GS856 | RIO_01:35.DI:V+ BB1GS856 | BB1GS856 | RIO_01:35.DI:00 BB1GS856 | BB1GS856/K1
BB1GS857 | MEAS_BIN | RIO_01:35.DI:V+ BB1GS857 | RIO_01:35.DI:01 BB1GS857 | RIO_01:35.DI:V+ BB1GS857 | BB1GS857 | RIO_01:35.DI:01 BB1GS857 | BB1GS857/K1
BB1GS858 | MEAS_BIN | RIO_01:35.DI:V+ BB1GS858 | RIO_01:35.DI:02 BB1GS858 | RIO_01:35.DI:V+ BB1GS858 | BB1GS858 | RIO_01:35.DI:02 BB1GS858 | BB1GS858/K1
BB1LS600 | MEAS_BIN | RIO_01:19.DI:V+ BB1LS600 | RIO_01:19.DI:00 BB1LS600 | RIO_01:19.DI:V+ BB1LS600 | BB1LS600 | RIO_01:19.DI:00 BB1LS600 | BB1LS600/K1
BB1LS608 | MEAS_BIN | RIO_01:18.DI:V+ BB1LS608 | RIO_01:18.DI:02 BB1LS608 | RIO_01:18.DI:V+ BB1LS608 | BB1LS608 | RIO_01:18.DI:02 BB1LS608 | BB1LS608/K1
BB1LS650 | MEAS_BIN | RIO_01:19.DI:V+ BB1LS650 | RIO_01:19.DI:02 BB1LS650 | RIO_01:19.DI:V+ BB1LS650 | BB1LS650 | RIO_01:19.DI:02 BB1LS650 | BB1LS650/K1
BB1LS651 | MEAS_BIN | RIO_01:20.DI:V+ BB1LS651 | RIO_01:20.DI:00 BB1LS651 | RIO_01:20.DI:V+ BB1LS651 | BB1LS651 | RIO_01:20.DI:00 BB1LS651 | BB1LS651/K1
BB1LS652 | MEAS_BIN | RIO_01:18.DI:V+ BB1LS652 | RIO_01:18.DI:00 BB1LS652 | RIO_01:18.DI:V+ BB1LS652 | BB1LS652 | RIO_01:18.DI:00 BB1LS652 | BB1LS652/K1
BB1LS653 | MEAS_BIN | RIO_01:22.DI:V+ BB1LS653 | RIO_01:22.DI:01 BB1LS653 | RIO_01:22.DI:V+ BB1LS653 | BB1LS653 | RIO_01:22.DI:01 BB1LS653 | BB1LS653/K1
BB1LS654 | MEAS_BIN | RIO_01:20.DI:V+ BB1LS654 | RIO_01:20.DI:02 BB1LS654 | RIO_01:20.DI:V+ BB1LS654 | BB1LS654 | RIO_01:20.DI:02 BB1LS654 | BB1LS654/K1
BB1LS655 | MEAS_BIN | RIO_01:17.DI:V+ BB1LS655 | RIO_01:17.DI:01 BB1LS655 | RIO_01:17.DI:V+ BB1LS655 | BB1LS655 | RIO_01:17.DI:01 BB1LS655 | BB1LS655/K1
BB1LS656 | MEAS_BIN | RIO_01:18.DI:V+ BB1LS656 | RIO_01:18.DI:03 BB1LS656 | RIO_01:18.DI:V+ BB1LS656 | BB1LS656 | RIO_01:18.DI:03 BB1LS656 | BB1LS656/K1
BB1LS657 | MEAS_BIN | RIO_01:28.DI:V+ BB1LS657 | RIO_01:28.DI:03 BB1LS657 | RIO_01:28.DI:V+ BB1LS657 | BB1LS657 | RIO_01:28.DI:03 BB1LS657 | BB1LS657/K1
BB1LS658 | MEAS_BIN | RIO_01:29.DI:V+ BB1LS658 | RIO_01:29.DI:00 BB1LS658 | RIO_01:29.DI:V+ BB1LS658 | BB1LS658 | RIO_01:29.DI:00 BB1LS658 | BB1LS658/K1
BB1LS659 | MEAS_BIN | RIO_01:29.DI:V+ BB1LS659 | RIO_01:29.DI:01 BB1LS659 | RIO_01:29.DI:V+ BB1LS659 | BB1LS659 | RIO_01:29.DI:01 BB1LS659 | BB1LS659/K1
BB1LS660 | MEAS_BIN | RIO_01:29.DI:V+ BB1LS660 | RIO_01:29.DI:02 BB1LS660 | RIO_01:29.DI:V+ BB1LS660 | BB1LS660 | RIO_01:29.DI:02 BB1LS660 | BB1LS660/K1
BB1LS661 | MEAS_BIN | RIO_01:31.DI:V+ BB1LS661 | RIO_01:31.DI:03 BB1LS661 | RIO_01:31.DI:V+ BB1LS661 | BB1LS661 | RIO_01:31.DI:03 BB1LS661 | BB1LS661/K1
BB1LS700 | MEAS_BIN | RIO_01:01.DI:V+ BB1LS700 | RIO_01:01.DI:00 BB1LS700 | RIO_01:01.DI:V+ BB1LS700 | BB1LS700 | RIO_01:01.DI:00 BB1LS700 | BB1LS700/K1
BB1LS701 | MEAS_BIN | RIO_01:01.DI:V+ BB1LS701 | RIO_01:01.DI:01 BB1LS701 | RIO_01:01.DI:V+ BB1LS701 | BB1LS701 | RIO_01:01.DI:01 BB1LS701 | BB1LS701/K1
BB1LS850 | MEAS_BIN | RIO_01:37.DI:V+ BB1LS850 | RIO_01:37.DI:03 BB1LS850 | RIO_01:37.DI:V+ BB1LS850 | BB1LS850 | RIO_01:37.DI:03 BB1LS850 | BB1LS850/K1
BB1LS851 | MEAS_BIN | RIO_01:38.DI:V+ BB1LS851 | RIO_01:38.DI:00 BB1LS851 | RIO_01:38.DI:V+ BB1LS851 | BB1LS851 | RIO_01:38.DI:00 BB1LS851 | BB1LS851/K1
BB1PS600 | MEAS_BIN | RIO_01:21.DI:V+ BB1PS600 | RIO_01:21.DI:02 BB1PS600 | RIO_01:21.DI:V+ BB1PS600 | BB1PS600 | RIO_01:21.DI:02 BB1PS600 | BB1PS600/K1
BB1PS601 | MEAS_BIN | RIO_01:16.DI:V+ BB1PS601 | RIO_01:16.DI:01 BB1PS601 | RIO_01:16.DI:V+ BB1PS601 | BB1PS601 | RIO_01:16.DI:01 BB1PS601 | BB1PS601/K1
BB1PS602 | MEAS_BIN | RIO_01:15.DI:V+ BB1PS602 | RIO_01:15.DI:00 BB1PS602 | RIO_01:15.DI:V+ BB1PS602 | BB1PS602 | RIO_01:15.DI:00 BB1PS602 | BB1PS602/K1
BB1PS603 | MEAS_BIN | RIO_01:25.DI:V+ BB1PS603 | RIO_01:25.DI:00 BB1PS603 | RIO_01:25.DI:V+ BB1PS603 | BB1PS603 | RIO_01:25.DI:00 BB1PS603 | BB1PS603/K1
BB1PS604 | MEAS_BIN | RIO_01:25.DI:V+ BB1PS604 | RIO_01:25.DI:01 BB1PS604 | RIO_01:25.DI:V+ BB1PS604 | BB1PS604 | RIO_01:25.DI:01 BB1PS604 | BB1PS604/K1
BB1PS605 | MEAS_BIN | RIO_01:24.DI:V+ BB1PS605 | RIO_01:24.DI:03 BB1PS605 | RIO_01:24.DI:V+ BB1PS605 | BB1PS605 | RIO_01:24.DI:03 BB1PS605 | BB1PS605/K1
BB1ST649 | MEAS_BIN | RIO_01:29.DI:V+ BB1ST649 | RIO_01:29.DI:03 BB1ST649 | RIO_01:29.DI:V+ BB1ST649 | BB1ST649 | RIO_01:29.DI:03 BB1ST649 | BB1ST649/K1
BB1ST650 | MEAS_BIN | RIO_01:23.DI:V+ BB1ST650 | RIO_01:23.DI:00 BB1ST650 | RIO_01:23.DI:V+ BB1ST650 | BB1ST650 | RIO_01:23.DI:00 BB1ST650 | BB1ST650/K1
BB1ST651 | MEAS_BIN | RIO_01:15.DI:V+ BB1ST651 | RIO_01:15.DI:03 BB1ST651 | RIO_01:15.DI:V+ BB1ST651 | BB1ST651 | RIO_01:15.DI:03 BB1ST651 | BB1ST651/K1
BB1ST652 | MEAS_BIN | RIO_01:26.DI:V+ BB1ST652 | RIO_01:26.DI:01 BB1ST652 | RIO_01:26.DI:V+ BB1ST652 | BB1ST652 | RIO_01:26.DI:01 BB1ST652 | BB1ST652/K1
BB1ST653 | MEAS_BIN | RIO_01:30.DI:V+ BB1ST653 | RIO_01:30.DI:01 BB1ST653 | RIO_01:30.DI:V+ BB1ST653 | BB1ST653 | RIO_01:30.DI:01 BB1ST653 | BB1ST653/K1
BB1ST654 | MEAS_BIN | RIO_01:25.DI:V+ BB1ST654 | RIO_01:25.DI:02 BB1ST654 | RIO_01:25.DI:V+ BB1ST654 | BB1ST654 | RIO_01:25.DI:02 BB1ST654 | BB1ST654/K1
BB1ST655 | MEAS_BIN | RIO_01:30.DI:V+ BB1ST655 | RIO_01:30.DI:03 BB1ST655 | RIO_01:30.DI:V+ BB1ST655 | BB1ST655 | RIO_01:30.DI:03 BB1ST655 | BB1ST655/K1
BB1ST656 | MEAS_BIN | RIO_01:27.DI:V+ BB1ST656 | RIO_01:27.DI:01 BB1ST656 | RIO_01:27.DI:V+ BB1ST656 | BB1ST656 | RIO_01:27.DI:01 BB1ST656 | BB1ST656/K1
BB1ST657 | MEAS_BIN | RIO_01:27.DI:V+ BB1ST657 | RIO_01:27.DI:02 BB1ST657 | RIO_01:27.DI:V+ BB1ST657 | BB1ST657 | RIO_01:27.DI:02 BB1ST657 | BB1ST657/K1
BB1ST659 | MEAS_BIN | RIO_01:31.DI:V+ BB1ST659 | RIO_01:31.DI:00 BB1ST659 | RIO_01:31.DI:V+ BB1ST659 | BB1ST659 | RIO_01:31.DI:00 BB1ST659 | BB1ST659/K1
BB1ST673 | MEAS_BIN | RIO_01:24.DI:V+ BB1ST673 | RIO_01:24.DI:00 BB1ST673 | RIO_01:24.DI:V+ BB1ST673 | BB1ST673 | RIO_01:24.DI:00 BB1ST673 | BB1ST673/K1
BB1ST674 | MEAS_BIN | RIO_01:24.DI:V+ BB1ST674 | RIO_01:24.DI:02 BB1ST674 | RIO_01:24.DI:V+ BB1ST674 | BB1ST674 | RIO_01:24.DI:02 BB1ST674 | BB1ST674/K1
BB1ST675 | MEAS_BIN | RIO_01:23.DI:V+ BB1ST675 | RIO_01:23.DI:02 BB1ST675 | RIO_01:23.DI:V+ BB1ST675 | BB1ST675 | RIO_01:23.DI:02 BB1ST675 | BB1ST675/K1
BB1ST850 | MEAS_BIN | RIO_01:38.DI:V+ BB1ST850 | RIO_01:38.DI:03 BB1ST850 | RIO_01:38.DI:V+ BB1ST850 | BB1ST850 | RIO_01:38.DI:03 BB1ST850 | BB1ST850/K1
BB1ST852 | MEAS_BIN | RIO_01:39.DI:V+ BB1ST852 | RIO_01:39.DI:01 BB1ST852 | RIO_01:39.DI:V+ BB1ST852 | BB1ST852 | RIO_01:39.DI:01 BB1ST852 | BB1ST852/K1
BB1ST853 | MEAS_BIN | RIO_01:39.DI:V+ BB1ST853 | RIO_01:39.DI:02 BB1ST853 | RIO_01:39.DI:V+ BB1ST853 | BB1ST853 | RIO_01:39.DI:02 BB1ST853 | BB1ST853/K1
BB1ST856 | MEAS_BIN | RIO_01:38.DI:V+ BB1ST856 | RIO_01:38.DI:02 BB1ST856 | RIO_01:38.DI:V+ BB1ST856 | BB1ST856 | RIO_01:38.DI:02 BB1ST856 | BB1ST856/K1
BB1TS600 | MEAS_BIN | RIO_01:24.DI:V+ BB1TS600 | RIO_01:24.DI:01 BB1TS600 | RIO_01:24.DI:V+ BB1TS600 | BB1TS600 | RIO_01:24.DI:01 BB1TS600 | BB1TS600/K1
BB1TS608 | MEAS_BIN | RIO_01:23.DI:V+ BB1TS608 | RIO_01:23.DI:03 BB1TS608 | RIO_01:23.DI:V+ BB1TS608 | BB1TS608 | RIO_01:23.DI:03 BB1TS608 | BB1TS608/K1
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM650 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM658 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM659 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM662 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM663 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM664 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM665 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM672 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM676 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM852 | FRQ_REVH | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## P_IO
IO Mapping |  |  |  | Description |  | Panel | Addressing | [10 empty] | Terminals | [5 empty] | Terminal Type/Names |  |  |  |  | Catalog
PLCTag | CardType | IOType | _Typical | Description2 | Description3 | Description4 | Panel | _PLC | _RackRaw | _SlotRaw | _ChannelRaw | _IsMax | Rack | Slot | Channel | LoopAddressA | LoopAddressB | AddressIO | TerminalIO | LoopTerminalA | LoopTerminalB | GndTerminal | T1 | T2 | T1Type | T2Type | LoopNameA | LoopNameB | GndName | CatalogNo | CatalogDesc2 | CatalogDesc | Notes
BB1LS700 | DI | DI | MEAS_BIN | CHEMICAL TANK 1 | LEVEL SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 0 | 0 | 01 | 01 | 00 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1LS701 | DI | DI | MEAS_BIN | CHEMICAL TANK 2 | LEVEL SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 1 | 0 | 01 | 01 | 01 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS004 | DI | DI | MEAS_BIN | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 1 | 2 | 0 | 01 | 01 | 02 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS003 | DI | DI | MEAS_BIN | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 1 | 3 | TRUE | 01 | 01 | 03 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS001 | DI | DI | MEAS_BIN | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 2 | 0 | 0 | 01 | 02 | 00 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS002 | DI | DI | MEAS_BIN | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 2 | 1 | 0 | 01 | 02 | 01 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS005 | DI | DI | MEAS_BIN | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 2 | 0 | 01 | 02 | 02 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS006 | DI | DI | MEAS_BIN | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 3 | TRUE | 01 | 02 | 03 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS007 | DI | DI | MEAS_BIN | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 0 | 0 | 01 | 03 | 00 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS008 | DI | DI | MEAS_BIN | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 1 | 0 | 01 | 03 | 01 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS009 | DI | DI | MEAS_BIN | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 2 | 0 | 01 | 03 | 02 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS010 | DI | DI | MEAS_BIN | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 3 | TRUE | 01 | 03 | 03 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS011 | DI | DI | MEAS_BIN | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | KPA_FLOORX_IO | RIO_ | 1 | 4 | 0 | 0 | 01 | 04 | 00 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS012 | DI | DI | MEAS_BIN | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | KPA_FLOORX_IO | RIO_ | 1 | 4 | 1 | 0 | 01 | 04 | 01 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS221 | DI | DI | MEAS_BIN | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 2 | 0 | 01 | 04 | 02 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS222 | DI | DI | MEAS_BIN | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 3 | TRUE | 01 | 04 | 03 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS223 | DI | DI | MEAS_BIN | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 0 | 0 | 01 | 05 | 00 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS224 | DI | DI | MEAS_BIN | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 1 | 0 | 01 | 05 | 01 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS225 | DI | DI | MEAS_BIN | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 2 | 0 | 01 | 05 | 02 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS226 | DI | DI | MEAS_BIN | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 3 | TRUE | 01 | 05 | 03 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS200 | DI | DI | MEAS_BIN | SOOTBLOWER 1 IN | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 0 | 0 | 01 | 06 | 00 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS201 | DI | DI | MEAS_BIN | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 1 | 0 | 01 | 06 | 01 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS203 | DI | DI | MEAS_BIN | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 2 | 0 | 01 | 06 | 02 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS204 | DI | DI | MEAS_BIN | SOOTBLOWER 2 IN | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 3 | TRUE | 01 | 06 | 03 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS205 | DI | DI | MEAS_BIN | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 0 | 0 | 01 | 07 | 00 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS206 | DI | DI | MEAS_BIN | SOOTBLOWER 3 IN | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 1 | 0 | 01 | 07 | 01 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS207 | DI | DI | MEAS_BIN | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 2 | 0 | 01 | 07 | 02 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS208 | DI | DI | MEAS_BIN | SOOTBLOWER 5 IN | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 3 | TRUE | 01 | 07 | 03 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS209 | DI | DI | MEAS_BIN | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 0 | 0 | 01 | 08 | 00 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS210 | DI | DI | MEAS_BIN | SOOTBLOWER 6 IN | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 1 | 0 | 01 | 08 | 01 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS211 | DI | DI | MEAS_BIN | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 2 | 0 | 01 | 08 | 02 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS212 | DI | DI | MEAS_BIN | SOOTBLOWER 7 IN | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 3 | TRUE | 01 | 08 | 03 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS213 | DI | DI | MEAS_BIN | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 0 | 0 | 01 | 09 | 00 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS214 | DI | DI | MEAS_BIN | SOOTBLOWER 8 IN | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 1 | 0 | 01 | 09 | 01 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS227 | DI | DI | MEAS_BIN | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 2 | 0 | 01 | 09 | 02 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS228 | DI | DI | MEAS_BIN | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 3 | TRUE | 01 | 09 | 03 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS231 | DI | DI | MEAS_BIN | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 10 | 0 | 0 | 01 | 10 | 00 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS230 | DI | DI | MEAS_BIN | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 10 | 1 | 0 | 01 | 10 | 01 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS233 | DI | DI | MEAS_BIN | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 2 | 0 | 01 | 10 | 02 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS232 | DI | DI | MEAS_BIN | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 3 | TRUE | 01 | 10 | 03 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS217 | DI | DI | MEAS_BIN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 11 | 0 | 0 | 01 | 11 | 00 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS218 | DI | DI | MEAS_BIN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 11 | 1 | 0 | 01 | 11 | 01 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS219 | DI | DI | MEAS_BIN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 11 | 2 | 0 | 01 | 11 | 02 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS220 | DI | DI | MEAS_BIN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 11 | 3 | TRUE | 01 | 11 | 03 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS217 | DI | DI | MEAS_BIN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 12 | 0 | 0 | 01 | 12 | 00 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS218 | DI | DI | MEAS_BIN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 12 | 1 | 0 | 01 | 12 | 01 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS220 | DI | DI | MEAS_BIN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 12 | 2 | 0 | 01 | 12 | 02 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS219 | DI | DI | MEAS_BIN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 12 | 3 | TRUE | 01 | 12 | 03 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS215 | DI | DI | MEAS_BIN | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 13 | 0 | 0 | 01 | 13 | 00 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS216 | DI | DI | MEAS_BIN | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 13 | 1 | 0 | 01 | 13 | 01 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS621 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 2 | 0 | 01 | 13 | 02 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS611 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 3 | TRUE | 01 | 13 | 03 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS606 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 0 | 0 | 01 | 14 | 00 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS614 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 1 | 0 | 01 | 14 | 01 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS619 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 2 | 0 | 01 | 14 | 02 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS651 | DI | DI | MEAS_BIN | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | KPA_FLOORX_IO | RIO_ | 1 | 14 | 3 | TRUE | 01 | 14 | 03 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1PS602 | DI | DI | MEAS_BIN | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 0 | 0 | 01 | 15 | 00 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS615 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 1 | 0 | 01 | 15 | 01 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS623 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 2 | 0 | 01 | 15 | 02 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1ST651 | DI | DI | MEAS_BIN | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 3 | TRUE | 01 | 15 | 03 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS603 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 0 | 0 | 01 | 16 | 00 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1PS601 | DI | DI | MEAS_BIN | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 1 | 0 | 01 | 16 | 01 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS650 | DI | DI | MEAS_BIN | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | KPA_FLOORX_IO | RIO_ | 1 | 16 | 2 | 0 | 01 | 16 | 02 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS622 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 3 | TRUE | 01 | 16 | 03 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS602 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 0 | 0 | 01 | 17 | 00 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1LS655 | DI | DI | MEAS_BIN | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | KPA_FLOORX_IO | RIO_ | 1 | 17 | 1 | 0 | 01 | 17 | 01 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS607 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 2 | 0 | 01 | 17 | 02 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS605 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 3 | TRUE | 01 | 17 | 03 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1LS652 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 0 | 0 | 01 | 18 | 00 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS601 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 1 | 0 | 01 | 18 | 01 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1LS608 | DI | DI | MEAS_BIN | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 2 | 0 | 01 | 18 | 02 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1LS656 | DI | DI | MEAS_BIN | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | KPA_FLOORX_IO | RIO_ | 1 | 18 | 3 | TRUE | 01 | 18 | 03 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1LS600 | DI | DI | MEAS_BIN | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 19 | 0 | 0 | 01 | 19 | 00 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS609 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 1 | 0 | 01 | 19 | 01 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1LS650 | DI | DI | MEAS_BIN | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 2 | 0 | 01 | 19 | 02 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS617 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 3 | TRUE | 01 | 19 | 03 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1LS651 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 0 | 0 | 01 | 20 | 00 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS612 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 1 | 0 | 01 | 20 | 01 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1LS654 | DI | DI | MEAS_BIN | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 2 | 0 | 01 | 20 | 02 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS613 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 3 | TRUE | 01 | 20 | 03 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS620 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 0 | 0 | 01 | 21 | 00 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS618 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 1 | 0 | 01 | 21 | 01 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1PS600 | DI | DI | MEAS_BIN | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 2 | 0 | 01 | 21 | 02 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS608 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 3 | TRUE | 01 | 21 | 03 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS604 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 0 | 0 | 01 | 22 | 00 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1LS653 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 1 | 0 | 01 | 22 | 01 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS616 | DI | DI | MEAS_BIN | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 2 | 0 | 01 | 22 | 02 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS600 | DI | DI | MEAS_BIN | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 3 | TRUE | 01 | 22 | 03 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1ST650 | DI | DI | MEAS_BIN | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 0 | 0 | 01 | 23 | 00 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS610 | DI | DI | MEAS_BIN | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 1 | 0 | 01 | 23 | 01 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1ST675 | DI | DI | MEAS_BIN | LEVELING ROLLER 3 | SPEED SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 2 | 0 | 01 | 23 | 02 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1TS608 | DI | DI | MEAS_BIN | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 3 | TRUE | 01 | 23 | 03 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1ST673 | DI | DI | MEAS_BIN | LEVELING ROLLER 1 | SPEED SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 0 | 0 | 01 | 24 | 00 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1TS600 | DI | DI | MEAS_BIN | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 1 | 0 | 01 | 24 | 01 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1ST674 | DI | DI | MEAS_BIN | LEVELING ROLLER 2 | SPEED SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 2 | 0 | 01 | 24 | 02 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1PS605 | DI | DI | MEAS_BIN | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 24 | 3 | TRUE | 01 | 24 | 03 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1PS603 | DI | DI | MEAS_BIN | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 25 | 0 | 0 | 01 | 25 | 00 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1PS604 | DI | DI | MEAS_BIN | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 25 | 1 | 0 | 01 | 25 | 01 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1ST654 | DI | DI | MEAS_BIN | BELT MAGNET | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 2 | 0 | 01 | 25 | 02 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS661 | DI | DI | MEAS_BIN | BELT MAGNET | DEVIATION DETECTOR 1 |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 3 | TRUE | 01 | 25 | 03 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS662 | DI | DI | MEAS_BIN | BELT MAGNET | DEVIATION DETECTOR 2 |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 0 | 0 | 01 | 26 | 00 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1ST652 | DI | DI | MEAS_BIN | BELT CONVEYOR | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 1 | 0 | 01 | 26 | 01 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS659 | DI | DI | MEAS_BIN | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 2 | 0 | 01 | 26 | 02 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS660 | DI | DI | MEAS_BIN | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 3 | TRUE | 01 | 26 | 03 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS663 | DI | DI | MEAS_BIN | BELT CONVEYOR | OVERSIZE DETECTOR |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 0 | 0 | 01 | 27 | 00 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1ST656 | DI | DI | MEAS_BIN | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 1 | 0 | 01 | 27 | 01 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1ST657 | DI | DI | MEAS_BIN | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 2 | 0 | 01 | 27 | 02 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS652 | DI | DI | MEAS_BIN | EXPLOSION HATCH | LIMIT SWITCH 1 |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 3 | TRUE | 01 | 27 | 03 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS653 | DI | DI | MEAS_BIN | EXPLOSION HATCH | LIMIT SWITCH 2 |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 0 | 0 | 01 | 28 | 00 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS654 | DI | DI | MEAS_BIN | EXPLOSION HATCH | LIMIT SWITCH 3 |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 1 | 0 | 01 | 28 | 01 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS655 | DI | DI | MEAS_BIN | EXPLOSION HATCH | LIMIT SWITCH 4 |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 2 | 0 | 01 | 28 | 02 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1LS657 | DI | DI | MEAS_BIN | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 3 | TRUE | 01 | 28 | 03 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1LS658 | DI | DI | MEAS_BIN | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 0 | 0 | 01 | 29 | 00 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1LS659 | DI | DI | MEAS_BIN | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 1 | 0 | 01 | 29 | 01 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1LS660 | DI | DI | MEAS_BIN | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 2 | 0 | 01 | 29 | 02 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1ST649 | DI | DI | MEAS_BIN | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 3 | TRUE | 01 | 29 | 03 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1ST652 | DI | DI | MEAS_BIN | BELT CONVEYOR | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 0 | 0 | 01 | 30 | 00 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1ST653 | DI | DI | MEAS_BIN | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 1 | 0 | 01 | 30 | 01 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1ST654 | DI | DI | MEAS_BIN | BELT MAGNET | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 2 | 0 | 01 | 30 | 02 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1ST655 | DI | DI | MEAS_BIN | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 3 | TRUE | 01 | 30 | 03 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1ST659 | DI | DI | MEAS_BIN | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 0 | 0 | 01 | 31 | 00 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS655 | DI | DI | MEAS_BIN | EXPLOSION HATCH | LIMIT SWITCH 4 |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 1 | 0 | 01 | 31 | 01 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS656 | DI | DI | MEAS_BIN | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 2 | 0 | 01 | 31 | 02 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1LS661 | DI | DI | MEAS_BIN | LUBRICATION ALARM | SCREW DISCHARGER |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 3 | TRUE | 01 | 31 | 03 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS802 | DI | DI | MEAS_BIN | BOTTOM ASH VALVE | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 0 | 0 | 01 | 32 | 00 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS803 | DI | DI | MEAS_BIN | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 32 | 1 | 0 | 01 | 32 | 01 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1LS852 | DI | DI | MEAS_BIN | FLY ASH CONTAINER | LEVEL SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 2 | 0 | 01 | 32 | 02 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1ST805 | DI | DI | MEAS_BIN | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 3 | TRUE | 01 | 32 | 03 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1ST808 | DI | DI | MEAS_BIN | ESP HOPPER 2 SCREW | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 0 | 0 | 01 | 33 | 00 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1ST809 | DI | DI | MEAS_BIN | ESP HOPPER 1 SCREW | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 1 | 0 | 01 | 33 | 01 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1ST804 | DI | DI | MEAS_BIN | ESP ROTARY VALVE | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 2 | 0 | 01 | 33 | 02 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1TS808 | DI | DI | MEAS_BIN | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 3 | TRUE | 01 | 33 | 03 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1TS809 | DI | DI | MEAS_BIN | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 0 | 0 | 01 | 34 | 00 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1TS805 | DI | DI | MEAS_BIN | ESP COLLECTION SCREW | HEATING THERMOSTAT |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 1 | 0 | 01 | 34 | 01 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1TS804 | DI | DI | MEAS_BIN | ESP ROTARY VALVE | HEATING THERMOSTAT |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 2 | 0 | 01 | 34 | 02 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS855 | DI | DI | MEAS_BIN | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 3 | TRUE | 01 | 34 | 03 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS856 | DI | DI | MEAS_BIN | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 0 | 0 | 01 | 35 | 00 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS857 | DI | DI | MEAS_BIN | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 1 | 0 | 01 | 35 | 01 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS858 | DI | DI | MEAS_BIN | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 2 | 0 | 01 | 35 | 02 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS850 | DI | DI | MEAS_BIN | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 3 | TRUE | 01 | 35 | 03 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS851 | DI | DI | MEAS_BIN | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 0 | 0 | 01 | 36 | 00 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1FS003 | DI | DI | MEAS_BIN | BOTTOM ASH COOLING | FLOW SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 1 | 0 | 01 | 36 | 01 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS801 | DI | DI | MEAS_BIN | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 36 | 2 | 0 | 01 | 36 | 02 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS800 | DI | DI | MEAS_BIN | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 36 | 3 | TRUE | 01 | 36 | 03 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS854 | DI | DI | MEAS_BIN | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 0 | 0 | 01 | 37 | 00 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1GS853 | DI | DI | MEAS_BIN | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | KPA_FLOORX_IO | RIO_ | 1 | 37 | 1 | 0 | 01 | 37 | 01 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1GS859 | DI | DI | MEAS_BIN | BOTTOM ASH TO CONTAINER | IN PLACE |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 2 | 0 | 01 | 37 | 02 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1LS850 | DI | DI | MEAS_BIN | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 3 | TRUE | 01 | 37 | 03 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1LS851 | DI | DI | MEAS_BIN | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 0 | 0 | 01 | 38 | 00 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1PT800 | DI | DI | MEAS_BIN | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 1 | 0 | 01 | 38 | 01 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1ST856 | DI | DI | MEAS_BIN | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 2 | 0 | 01 | 38 | 02 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1ST850 | DI | DI | MEAS_BIN | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 3 | TRUE | 01 | 38 | 03 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1GS852 | DI | DI | MEAS_BIN | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 0 | 0 | 01 | 39 | 00 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1ST852 | DI | DI | MEAS_BIN | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 1 | 0 | 01 | 39 | 01 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1ST853 | DI | DI | MEAS_BIN | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 2 | 0 | 01 | 39 | 02 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1GS020 | DI | DI | MEAS_BIN | EMERGENCY SHOWER | USE SWITCH |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 3 | TRUE | 01 | 39 | 03 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM658_LOCAL_MODE | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 0 | 0 | 01 | 40 | 00 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM658_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 1 | 0 | 01 | 40 | 01 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM658_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 2 | 0 | 01 | 40 | 02 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM658_ISOLATOR | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 3 | TRUE | 01 | 40 | 03 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM659_LOCAL_MODE | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 0 | 0 | 01 | 41 | 00 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM659_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 1 | 0 | 01 | 41 | 01 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM659_LOCAL_RUN_REV | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 2 | 0 | 01 | 41 | 02 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM659_ISOLATOR | DI | DI | FRQ_REVH | BELT CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 3 | TRUE | 01 | 41 | 03 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM676_LOCAL_MODE | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 0 | 0 | 01 | 42 | 00 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM676_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 1 | 0 | 01 | 42 | 01 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM676_LOCAL_RUN_REV | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 2 | 0 | 01 | 42 | 02 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM676_ISOLATOR | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 3 | TRUE | 01 | 42 | 03 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM672_LOCAL_MODE | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 0 | 0 | 01 | 43 | 00 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM672_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 1 | 0 | 01 | 43 | 01 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM672_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 2 | 0 | 01 | 43 | 02 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM672_ISOLATOR | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 3 | TRUE | 01 | 43 | 03 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM662_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 0 | 0 | 01 | 44 | 00 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM662_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 1 | 0 | 01 | 44 | 01 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM662_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 2 | 0 | 01 | 44 | 02 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM662_ISOLATOR | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 3 | TRUE | 01 | 44 | 03 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM650_LOCAL_MODE | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 0 | 0 | 01 | 45 | 00 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM650_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 1 | 0 | 01 | 45 | 01 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM650_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 2 | 0 | 01 | 45 | 02 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM650_ISOLATOR | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 3 | TRUE | 01 | 45 | 03 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM663_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 0 | 0 | 01 | 46 | 00 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM663_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 1 | 0 | 01 | 46 | 01 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM663_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 2 | 0 | 01 | 46 | 02 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM663_ISOLATOR | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 3 | TRUE | 01 | 46 | 03 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM664_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 0 | 0 | 01 | 47 | 00 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM664_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 1 | 0 | 01 | 47 | 01 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM664_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 2 | 0 | 01 | 47 | 02 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM664_ISOLATOR | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 3 | TRUE | 01 | 47 | 03 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM665_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 0 | 0 | 01 | 48 | 00 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM665_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 1 | 0 | 01 | 48 | 01 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM665_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 2 | 0 | 01 | 48 | 02 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM665_ISOLATOR | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 3 | TRUE | 01 | 48 | 03 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM852_LOCAL_MODE | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 0 | 0 | 01 | 49 | 00 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:00 | 0 | 1 |  |  | V+ | 0 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM852_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 1 | 0 | 01 | 49 | 01 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:01 | 1 | 3 |  |  | V+ | 1 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM852_LOCAL_RUN_REV | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 2 | 0 | 01 | 49 | 02 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:02 | 2 | 5 |  |  | V+ | 2 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM852_ISOLATOR | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 3 | TRUE | 01 | 49 | 03 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:03 | 3 | 7 |  |  | V+ | 3 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
|  |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 50 | 0 | #N/A | 01 | 50 | 00 | #N/A | #N/A | RIO_01:50.:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## D_DEVICES
Tags |  |  |  | Description |  |  |  |  | Types
DeviceTag | _Suffix | PLCTag | PLCAddress | _InitialDescription | Desc1 | Desc2 | Desc3 | LongDescription | DeviceCode | DeviceType | IOType | Typical | Notes
BB1IL001 |  | BB1IL001 | <IO NOT ASSIGNED> | Alarm horn and light CO alarm | ALARM HORN AND LIGHT | CO ALARM |  | ALARM HORN AND LIGHT CO ALARM | IL | ALARM | DO | ALM_HORN
BB1IJ002 |  | BB1IJ002 | <IO NOT ASSIGNED> | Scraper Conveyor 1 Alarm horn and lamp | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  | SCRAPER CONVEYOR 1 ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN
BB1IJ001 |  | BB1IJ001 | <IO NOT ASSIGNED> | Scraper Conveyor 2 Alarm horn and lamp | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  | SCRAPER CONVEYOR 2 ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN
BB1IJ004 |  | BB1IJ004 | <IO NOT ASSIGNED> | Bottom ash conveyor Alarm horn and lamp | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  | BOTTOM ASH CONVEYOR ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN
BB1EM405 |  | BB1EM405 | <IO NOT ASSIGNED> | Air intake grill 1 OPEN | AIR INTAKE GRILL 1 | OPEN |  | AIR INTAKE GRILL 1 OPEN | EM | MOTOR | DO | BELIMO_VLV
BB1GS401 |  | BB1GS401 | <IO NOT ASSIGNED> | Air intake grill 1 OPENED LIMIT | AIR INTAKE GRILL 1 | OPENED LIMIT |  | AIR INTAKE GRILL 1 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV
BB1EM406 |  | BB1EM406 | <IO NOT ASSIGNED> | Air intake grill 2 OPEN | AIR INTAKE GRILL 2 | OPEN |  | AIR INTAKE GRILL 2 OPEN | EM | MOTOR | DO | BELIMO_VLV
BB1GS412 |  | BB1GS412 | <IO NOT ASSIGNED> | Air intake grill 2 OPENED LIMIT | AIR INTAKE GRILL 2 | OPENED LIMIT |  | AIR INTAKE GRILL 2 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV
BB1EM407 |  | BB1EM407 | <IO NOT ASSIGNED> | Air intake grill 3 OPEN | AIR INTAKE GRILL 3 | OPEN |  | AIR INTAKE GRILL 3 OPEN | EM | MOTOR | DO | BELIMO_VLV
BB1GS413 |  | BB1GS413 | <IO NOT ASSIGNED> | Air intake grill 3 OPENED LIMIT | AIR INTAKE GRILL 3 | OPENED LIMIT |  | AIR INTAKE GRILL 3 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV
BB1SV410 |  | BB1SV410 | <IO NOT ASSIGNED> | Feed water tank overflow valve | FEED WATER TANK | OVERFLOW VALVE |  | FEED WATER TANK OVERFLOW VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1IV004 |  | BB1IV004 | <IO NOT ASSIGNED> | Boiler bottom blow down on-off valve | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  | BOILER BOTTOM BLOW DOWN ON-OFF VALVE | IV | ISOLATING VALVE | DO | BIN_VLV
BB1SV001 |  | BB1SV001 | <IO NOT ASSIGNED> | Blow down tank cooling on/off valve | BLOW DOWN TANK COOLING | ON/OFF VALVE |  | BLOW DOWN TANK COOLING ON/OFF VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1SV400 |  | BB1SV400 | <IO NOT ASSIGNED> | Sealing air to rotary feeder solenoid valve | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1SV406 |  | BB1SV406 | <IO NOT ASSIGNED> | Sealing air to rotary feeder solenoid valve | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1SV950 |  | BB1SV950 | <IO NOT ASSIGNED> | Fuel silo fire water control valve | FUEL SILO FIRE WATER | CONTROL VALVE |  | FUEL SILO FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1SV951 |  | BB1SV951 | <IO NOT ASSIGNED> | Fuel pocket fire water control valve | FUEL POCKET FIRE WATER | CONTROL VALVE |  | FUEL POCKET FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1CV405 |  | BB1CV405 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve | BOTTOM ASH VALVE | SOLENOID VALVE |  | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV
BB1CV406 |  | BB1CV406 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve | BOTTOM ASH VALVE | SOLENOID VALVE |  | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV
BB1CV412 |  | BB1CV412 | <IO NOT ASSIGNED> | Bottom ash sieve bypass solenoid valve | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  | BOTTOM ASH SIEVE BYPASS SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV
BB1CV414 |  | BB1CV414 | <IO NOT ASSIGNED> | Work air to pneumatic transmitter pneumatic valve | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE | WORK AIR TO PNEUMATIC TRANSMITTER PNEUMATIC VAL VE | CV | CONTROL VALVE | DO | BIN_VLV
BB1SV405 |  | BB1SV405 | <IO NOT ASSIGNED> | Sand filling valve solenoid valve | SAND FILLING VALVE | SOLENOID VALVE |  | SAND FILLING VALVE SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1SV401 |  | BB1SV401 | <IO NOT ASSIGNED> | Bottom ash purging air solenoid valve | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1SV402 |  | BB1SV402 | <IO NOT ASSIGNED> | Bottom ash purging air solenoid valve | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV
BB1CV413 |  | BB1CV413 | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER | CV | CONTROL VALVE | DO | BIN_VLV_2DO
BB1CV413 | _OPEN | BB1CV413_OPEN | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper OPEN | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER OPEN | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER OPEN | CV | CONTROL VALVE | DO | BIN_VLV_2DO
BB1CV413 | _CLOSE | BB1CV413_CLOSE | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper CLOSE | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER CLOSE | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER CLOSE | CV | CONTROL VALVE | DO | BIN_VLV_2DO
BB1BU500 | _DO_IF1 | BB1BU500_DO_IF1 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 1 | BURNER DIGITAL OUTPUT | INTERFACE 1 |  | BURNER DIGITAL OUTPUT INTERFACE 1 | BU | BURNER | DO | BURNER
BB1BU500 | _DO_IF2 | BB1BU500_DO_IF2 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 2 | BURNER DIGITAL OUTPUT | INTERFACE 2 |  | BURNER DIGITAL OUTPUT INTERFACE 2 | BU | BURNER | DO | BURNER
BB1BU500 | _DO_IF3 | BB1BU500_DO_IF3 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 3 | BURNER DIGITAL OUTPUT | INTERFACE 3 |  | BURNER DIGITAL OUTPUT INTERFACE 3 | BU | BURNER | DO | BURNER
BB1BU500 | _DO_IF4 | BB1BU500_DO_IF4 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 4 | BURNER DIGITAL OUTPUT | INTERFACE 4 |  | BURNER DIGITAL OUTPUT INTERFACE 4 | BU | BURNER | DO | BURNER
BB1BU500 | _DO_IF5 | BB1BU500_DO_IF5 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 5 | BURNER DIGITAL OUTPUT | INTERFACE 5 |  | BURNER DIGITAL OUTPUT INTERFACE 5 | BU | BURNER | DO | BURNER
BB1BU500 | _DI_IF1 | BB1BU500_DI_IF1 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 1 | BURNER DIGITAL INPUT | INTERFACE 1 |  | BURNER DIGITAL INPUT INTERFACE 1 | BU | BURNER | DI | BURNER
BB1BU500 | _DI_IF2 | BB1BU500_DI_IF2 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 2 | BURNER DIGITAL INPUT | INTERFACE 2 |  | BURNER DIGITAL INPUT INTERFACE 2 | BU | BURNER | DI | BURNER
BB1BU500 | _DI_IF3 | BB1BU500_DI_IF3 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 3 | BURNER DIGITAL INPUT | INTERFACE 3 |  | BURNER DIGITAL INPUT INTERFACE 3 | BU | BURNER | DI | BURNER
BB1BU500 | _DI_IF4 | BB1BU500_DI_IF4 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 4 | BURNER DIGITAL INPUT | INTERFACE 4 |  | BURNER DIGITAL INPUT INTERFACE 4 | BU | BURNER | DI | BURNER
BB1BU500 | _DI_IF5 | BB1BU500_DI_IF5 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 5 | BURNER DIGITAL INPUT | INTERFACE 5 |  | BURNER DIGITAL INPUT INTERFACE 5 | BU | BURNER | DI | BURNER
BB1BU500 | _AO_IF1 | BB1BU500_AO_IF1 | <IO NOT ASSIGNED> | BURNER ANALOGUE OUTPUT INTERFACE 1 | BURNER ANALOGUE OUTPUT | INTERFACE 1 |  | BURNER ANALOGUE OUTPUT INTERFACE 1 | BU | BURNER | AO | BURNER
BB1BU500 | _AO_IF2 | BB1BU500_AO_IF2 | <IO NOT ASSIGNED> | BURNER ANALOGUE OUTPUT INTERFACE 2 | BURNER ANALOGUE OUTPUT | INTERFACE 2 |  | BURNER ANALOGUE OUTPUT INTERFACE 2 | BU | BURNER | AO | BURNER
BB1BU500 | _AI_IF1 | BB1BU500_AI_IF1 | <IO NOT ASSIGNED> | BURNER ANALOGUE INPUT INTERFACE 1 | BURNER ANALOGUE INPUT | INTERFACE 1 |  | BURNER ANALOGUE INPUT INTERFACE 1 | BU | BURNER | AI | BURNER
BB1BU500 | _AI_IF2 | BB1BU500_AI_IF2 | <IO NOT ASSIGNED> | BURNER ANALOGUE INPUT INTERFACE 2 | BURNER ANALOGUE INPUT | INTERFACE 2 |  | BURNER ANALOGUE INPUT INTERFACE 2 | BU | BURNER | AI | BURNER
BB1PU800 |  | BB1PU800 | <IO NOT ASSIGNED> | Chemical dosing pump 1 | CHEMICAL DOSING PUMP 1 |  |  | CHEMICAL DOSING PUMP 1 | PU | PUMP | DO | CHEMICAL_PUMP
BB1PU801 |  | BB1PU801 | <IO NOT ASSIGNED> | Chemical dosing pump 2 | CHEMICAL DOSING PUMP 2 |  |  | CHEMICAL DOSING PUMP 2 | PU | PUMP | DO | CHEMICAL_PUMP
BB1EM402 |  | BB1EM402 | <IO NOT ASSIGNED> | Compressor 1 | COMPRESSOR 1 |  |  | COMPRESSOR 1 | EM | MOTOR | DO | COMPR
BB1EM402 | _FAULT_DI | BB1EM402_FAULT_DI | <IO NOT ASSIGNED> | Compressor 1 Fault | COMPRESSOR 1 | FAULT |  | COMPRESSOR 1 FAULT | EM | MOTOR | DO | COMPR
BB1EM402 | _RUNNING_DI | BB1EM402_RUNNING_DI | <IO NOT ASSIGNED> | Compressor 1 Running | COMPRESSOR 1 | RUNNING |  | COMPRESSOR 1 RUNNING | EM | MOTOR | DO | COMPR
BB1EM402 | _RESERVE_DI | BB1EM402_RESERVE_DI | <IO NOT ASSIGNED> | Compressor 1 reserve | COMPRESSOR 1 | RESERVE |  | COMPRESSOR 1 RESERVE | EM | MOTOR | DO | COMPR
BB1EM402 | _RUN_DO | BB1EM402_RUN_DO | <IO NOT ASSIGNED> | Compressor 1 remote run | COMPRESSOR 1 | REMOTE RUN |  | COMPRESSOR 1 REMOTE RUN | EM | MOTOR | DO | COMPR
BB1EM402 | _FAULT_ACK_DO | BB1EM402_FAULT_ACK_DO | <IO NOT ASSIGNED> | Compressor 1 Fault Acknowledge | COMPRESSOR 1 | FAULT ACKNOWLEDGE |  | COMPRESSOR 1 FAULT ACKNOWLEDGE | EM | MOTOR | DO | COMPR
BB1EM403 |  | BB1EM403 | <IO NOT ASSIGNED> | Compressor 2 | COMPRESSOR 2 |  |  | COMPRESSOR 2 | EM | MOTOR | DO | COMPR
BB1EM403 | _FAULT_DI | BB1EM403_FAULT_DI | <IO NOT ASSIGNED> | Compressor 2 Fault | COMPRESSOR 2 | FAULT |  | COMPRESSOR 2 FAULT | EM | MOTOR | DO | COMPR
BB1EM403 | _RUNNING_DI | BB1EM403_RUNNING_DI | <IO NOT ASSIGNED> | Compressor 2 Running | COMPRESSOR 2 | RUNNING |  | COMPRESSOR 2 RUNNING | EM | MOTOR | DO | COMPR
BB1EM403 | _RESERVE_DI | BB1EM403_RESERVE_DI | <IO NOT ASSIGNED> | Compressor 2 reserve | COMPRESSOR 2 | RESERVE |  | COMPRESSOR 2 RESERVE | EM | MOTOR | DO | COMPR
BB1EM403 | _RUN_DO | BB1EM403_RUN_DO | <IO NOT ASSIGNED> | Compressor 2 remote run | COMPRESSOR 2 | REMOTE RUN |  | COMPRESSOR 2 REMOTE RUN | EM | MOTOR | DO | COMPR
BB1EM403 | _FAULT_ACK_DO | BB1EM403_FAULT_ACK_DO | <IO NOT ASSIGNED> | Compressor 2 Fault Acknowledge | COMPRESSOR 2 | FAULT ACKNOWLEDGE |  | COMPRESSOR 2 FAULT ACKNOWLEDGE | EM | MOTOR | DO | COMPR
BB1CV200 | _SETPOINT | BB1CV200_SETPOINT | <IO NOT ASSIGNED> | Steam from drum control valve SETPOINT | STEAM FROM DRUM CONTROL | VALVE SETPOINT |  | STEAM FROM DRUM CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV
BB1CV200 | _POSITION | BB1CV200_POSITION | <IO NOT ASSIGNED> | Steam from drum control valve POSITION | STEAM FROM DRUM CONTROL | VALVE POSITION |  | STEAM FROM DRUM CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV
BB1CV001 | _SETPOINT | BB1CV001_SETPOINT | <IO NOT ASSIGNED> | Make-up water control valve SETPOINT | MAKE-UP WATER CONTROL | VALVE SETPOINT |  | MAKE-UP WATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV
BB1CV001 | _POSITION | BB1CV001_POSITION | <IO NOT ASSIGNED> | Make-up water control valve POSITION | MAKE-UP WATER CONTROL | VALVE POSITION |  | MAKE-UP WATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV
BB1CV002 | _SETPOINT | BB1CV002_SETPOINT | <IO NOT ASSIGNED> | Feed water control valve SETPOINT | FEED WATER CONTROL VALVE | SETPOINT |  | FEED WATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV
BB1CV002 | _POSITION | BB1CV002_POSITION | <IO NOT ASSIGNED> | Feed water control valve POSITION | FEED WATER CONTROL VALVE | POSITION |  | FEED WATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV
BB1DM300 | _SETPOINT | BB1DM300_SETPOINT | <IO NOT ASSIGNED> | Tertiary air damper 1 SETPOINT | TERTIARY AIR DAMPER 1 | SETPOINT |  | TERTIARY AIR DAMPER 1 SETPOINT | DM | DAMPER | AO | CONT_VLV
BB1DM300 | _POSITION | BB1DM300_POSITION | <IO NOT ASSIGNED> | Tertiary air damper 1 POSITION | TERTIARY AIR DAMPER 1 | POSITION |  | TERTIARY AIR DAMPER 1 POSITION | DM | DAMPER | AI | CONT_VLV
BB1DM400 | _SETPOINT | BB1DM400_SETPOINT | <IO NOT ASSIGNED> | Primary air damper SETPOINT | PRIMARY AIR DAMPER | SETPOINT |  | PRIMARY AIR DAMPER SETPOINT | DM | DAMPER | AO | CONT_VLV
BB1DM400 | _POSITION | BB1DM400_POSITION | <IO NOT ASSIGNED> | Primary air damper POSITION | PRIMARY AIR DAMPER | POSITION |  | PRIMARY AIR DAMPER POSITION | DM | DAMPER | AI | CONT_VLV
BB1DM550 | _SETPOINT | BB1DM550_SETPOINT | <IO NOT ASSIGNED> | Recirculation gas damper SETPOINT | RECIRCULATION GAS DAMPER | SETPOINT |  | RECIRCULATION GAS DAMPER SETPOINT | DM | DAMPER | AO | CONT_VLV
BB1DM550 | _POSITION | BB1DM550_POSITION | <IO NOT ASSIGNED> | Recirculation gas damper POSITION | RECIRCULATION GAS DAMPER | POSITION |  | RECIRCULATION GAS DAMPER POSITION | DM | DAMPER | AI | CONT_VLV
BB1DM301 | _SETPOINT | BB1DM301_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 4 SETPOINT | SECONDARY AIR DAMPER 4 | SETPOINT |  | SECONDARY AIR DAMPER 4 SETPOINT | DM | DAMPER | AO | CONT_VLV
BB1DM301 | _POSITION | BB1DM301_POSITION | <IO NOT ASSIGNED> | Secondary air damper 4 POSITION | SECONDARY AIR DAMPER 4 | POSITION |  | SECONDARY AIR DAMPER 4 POSITION | DM | DAMPER | AI | CONT_VLV
BB1DM302 | _SETPOINT | BB1DM302_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 3 SETPOINT | SECONDARY AIR DAMPER 3 | SETPOINT |  | SECONDARY AIR DAMPER 3 SETPOINT | DM | DAMPER | AO | CONT_VLV
BB1DM302 | _POSITION | BB1DM302_POSITION | <IO NOT ASSIGNED> | Secondary air damper 3 POSITION | SECONDARY AIR DAMPER 3 | POSITION |  | SECONDARY AIR DAMPER 3 POSITION | DM | DAMPER | AI | CONT_VLV
BB1DM304 | _SETPOINT | BB1DM304_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 1 SETPOINT | SECONDARY AIR DAMPER 1 | SETPOINT |  | SECONDARY AIR DAMPER 1 SETPOINT | DM | DAMPER | AO | CONT_VLV
BB1DM304 | _POSITION | BB1DM304_POSITION | <IO NOT ASSIGNED> | Secondary air damper 1 POSITION | SECONDARY AIR DAMPER 1 | POSITION |  | SECONDARY AIR DAMPER 1 POSITION | DM | DAMPER | AI | CONT_VLV
BB1DM303 | _SETPOINT | BB1DM303_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 2 SETPOINT | SECONDARY AIR DAMPER 2 | SETPOINT |  | SECONDARY AIR DAMPER 2 SETPOINT | DM | DAMPER | AO | CONT_VLV
BB1DM303 | _POSITION | BB1DM303_POSITION | <IO NOT ASSIGNED> | Secondary air damper 2 POSITION | SECONDARY AIR DAMPER 2 | POSITION |  | SECONDARY AIR DAMPER 2 POSITION | DM | DAMPER | AI | CONT_VLV
BB1CV004 | _SETPOINT | BB1CV004_SETPOINT | <IO NOT ASSIGNED> | Primary air preheater control valve SETPOINT | PRIMARY AIR PREHEATER | CONTROL VALVE SETPOINT |  | PRIMARY AIR PREHEATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV
BB1CV004 | _POSITION | BB1CV004_POSITION | <IO NOT ASSIGNED> | Primary air preheater control valve POSITION | PRIMARY AIR PREHEATER | CONTROL VALVE POSITION |  | PRIMARY AIR PREHEATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV
BB1CV402 | _SETPOINT | BB1CV402_SETPOINT | <IO NOT ASSIGNED> | Fuel chute B carrying air control valve 2 SETPOINT | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | SETPOINT | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV
BB1CV402 | _POSITION | BB1CV402_POSITION | <IO NOT ASSIGNED> | Fuel chute B carrying air control valve 2 POSITION | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | POSITION | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 POSITION | CV | CONTROL VALVE | AI | CONT_VLV
BB1CV403 | _SETPOINT | BB1CV403_SETPOINT | <IO NOT ASSIGNED> | Fuel chute A carrying air control valve 1 SETPOINT | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | SETPOINT | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV
BB1CV403 | _POSITION | BB1CV403_POSITION | <IO NOT ASSIGNED> | Fuel chute A carrying air control valve 1 POSITION | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | POSITION | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 POSITION | CV | CONTROL VALVE | AI | CONT_VLV
BB1PT200 |  | BB1PT200 | <IO NOT ASSIGNED> | Feed water tank pressure | FEED WATER TANK PRESSURE |  |  | FEED WATER TANK PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1LT001 |  | BB1LT001 | <IO NOT ASSIGNED> | Feed water tank level 1 | FEED WATER TANK LEVEL 1 |  |  | FEED WATER TANK LEVEL 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1LT002 |  | BB1LT002 | <IO NOT ASSIGNED> | Feed water tank level 2 | FEED WATER TANK LEVEL 2 |  |  | FEED WATER TANK LEVEL 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1PT005 |  | BB1PT005 | <IO NOT ASSIGNED> | Feed water pressure after valve | FEED WATER PRESSURE | AFTER VALVE |  | FEED WATER PRESSURE AFTER VALVE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1FT001 |  | BB1FT001 | <IO NOT ASSIGNED> | Feed water flow and control | FEED WATER FLOW | AND CONTROL |  | FEED WATER FLOW AND CONTROL | FT | FLOW TRANSMITTER | AI | MEAS_ANA
BB1TT001 |  | BB1TT001 | <IO NOT ASSIGNED> | Feed water temperature | FEED WATER TEMPERATURE |  |  | FEED WATER TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT002 |  | BB1TT002 | <IO NOT ASSIGNED> | Feed water pump 2 bearing temperature | FEED WATER PUMP 2 | BEARING TEMPERATURE |  | FEED WATER PUMP 2 BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1PT004 |  | BB1PT004 | <IO NOT ASSIGNED> | Feed water pressure before valve | FEED WATER PRESSURE | BEFORE VALVE |  | FEED WATER PRESSURE BEFORE VALVE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT002 |  | BB1PT002 | <IO NOT ASSIGNED> | Feed water pump 2 pressure side pressure | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  | FEED WATER PUMP 2 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT006 |  | BB1PT006 | <IO NOT ASSIGNED> | FW suction line strainer pressure diff. | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT007 |  | BB1PT007 | <IO NOT ASSIGNED> | FW suction line strainer pressure diff. | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1TT005 |  | BB1TT005 | <IO NOT ASSIGNED> | FW pump 2 motor winding temperature | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  | FW PUMP 2 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1PT001 |  | BB1PT001 | <IO NOT ASSIGNED> | Feed water pump 1 pressure side pressure | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  | FEED WATER PUMP 1 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1TT004 |  | BB1TT004 | <IO NOT ASSIGNED> | FW pump 1 motor winding temperature | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  | FW PUMP 1 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT003 |  | BB1TT003 | <IO NOT ASSIGNED> | FW pump 1 motor bearing temperature | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  | FW PUMP 1 MOTOR BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT008 |  | BB1TT008 | <IO NOT ASSIGNED> | Temperature after economizer | TEMPERATURE AFTER | ECONOMIZER |  | TEMPERATURE AFTER ECONOMIZER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1FT200 |  | BB1FT200 | <IO NOT ASSIGNED> | Heating steam to feed water tank flow measurement | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT | HEATING STEAM TO FEED WATER TANK FLOW MEASUREMENT | FT | FLOW TRANSMITTER | AI | MEAS_ANA
BB1TT009 |  | BB1TT009 | <IO NOT ASSIGNED> | Temperature before economizer | TEMPERATURE BEFORE | ECONOMIZER |  | TEMPERATURE BEFORE ECONOMIZER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT200 |  | BB1TT200 | <IO NOT ASSIGNED> | Main steam temperature | MAIN STEAM TEMPERATURE |  |  | MAIN STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1FT202 |  | BB1FT202 | <IO NOT ASSIGNED> | Main steam flow | MAIN STEAM FLOW |  |  | MAIN STEAM FLOW | FT | FLOW TRANSMITTER | AI | MEAS_ANA
BB1FT201 |  | BB1FT201 | <IO NOT ASSIGNED> | Steam flow to sootblowing and air preheater | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  | STEAM FLOW TO SOOTBLOWING AND AIR PREHEATER | FT | FLOW TRANSMITTER | AI | MEAS_ANA
BB1TT201 |  | BB1TT201 | <IO NOT ASSIGNED> | Sootblowing line temperature | SOOTBLOWING | LINE TEMPERATURE |  | SOOTBLOWING LINE TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
<001> |  | <001> | <IO NOT ASSIGNED> | Electrical room temperature | ELECTRICAL ROOM | TEMPERATURE |  | ELECTRICAL ROOM TEMPERATURE | 1> | #N/A | AI | #N/A
<002> |  | <002> | <IO NOT ASSIGNED> | PLC-cabinet temperature | PLC-CABINET | TEMPERATURE |  | PLC-CABINET TEMPERATURE | 2> | #N/A | AI | #N/A
BB1TT006 |  | BB1TT006 | <IO NOT ASSIGNED> | Blow down tank temperature and control | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  | BLOW DOWN TANK TEMPERATURE AND CONTROL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT202 |  | BB1TT202 | <IO NOT ASSIGNED> | Steam outlet temperature from accumulator | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  | STEAM OUTLET TEMPERATURE FROM ACCUMULATOR | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1PT207 |  | BB1PT207 | <IO NOT ASSIGNED> | Accumulator pressure | ACCUMULATOR PRESSURE |  |  | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1TT007 |  | BB1TT007 | <IO NOT ASSIGNED> | Accumulator temperature | ACCUMULATOR TEMPERATURE |  |  | ACCUMULATOR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT203 |  | BB1TT203 | <IO NOT ASSIGNED> | 18bar(g) steam temperature | 18BAR(G) STEAM | TEMPERATURE |  | 18BAR(G) STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1PT204 |  | BB1PT204 | <IO NOT ASSIGNED> | Main steam pressure | MAIN STEAM PRESSURE |  |  | MAIN STEAM PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1LT004 |  | BB1LT004 | <IO NOT ASSIGNED> | Steam accumulator level 2 | STEAM ACCUMULATOR LEVEL 2 |  |  | STEAM ACCUMULATOR LEVEL 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1PT208 |  | BB1PT208 | <IO NOT ASSIGNED> | Accumulator pressure | ACCUMULATOR PRESSURE |  |  | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1FT203 |  | BB1FT203 | <IO NOT ASSIGNED> | Steam to existing header flow measurement | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  | STEAM TO EXISTING HEADER FLOW MEASUREMENT | FT | FLOW TRANSMITTER | AI | MEAS_ANA
<003> |  | <003> | <IO NOT ASSIGNED> | Steam to existing header energy calculator | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  | STEAM TO EXISTING HEADER ENERGY CALCULATOR | 3> | #N/A | AI | #N/A
BB1LT003 |  | BB1LT003 | <IO NOT ASSIGNED> | Steam accumulator level 1 | STEAM ACCUMULATOR LEVEL 1 |  |  | STEAM ACCUMULATOR LEVEL 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1QT002 |  | BB1QT002 | <IO NOT ASSIGNED> | pH measurement from feed water tank | PH MEASUREMENT FROM FEED | WATER TANK |  | PH MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1QT006 |  | BB1QT006 | <IO NOT ASSIGNED> | Conductivity measurement from main steam | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  | CONDUCTIVITY MEASUREMENT FROM MAIN STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1QT005 |  | BB1QT005 | <IO NOT ASSIGNED> | Conductivity measurement from saturated steam | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  | CONDUCTIVITY MEASUREMENT FROM SATURATED STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1QT003 |  | BB1QT003 | <IO NOT ASSIGNED> | Conductivity measurement from condensate | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  | CONDUCTIVITY MEASUREMENT FROM CONDENSATE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1QT007 |  | BB1QT007 | <IO NOT ASSIGNED> | Conductivity measurement from feed water line | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  | CONDUCTIVITY MEASUREMENT FROM FEED WATER LINE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1QT001 |  | BB1QT001 | <IO NOT ASSIGNED> | Conductivity measurement from feed water tank | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  | CONDUCTIVITY MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1QT004 |  | BB1QT004 | <IO NOT ASSIGNED> | Conductivity measurement from boiler water | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  | CONDUCTIVITY MEASUREMENT FROM BOILER WATER | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1PT410 |  | BB1PT410 | <IO NOT ASSIGNED> | Secondary air pressure inner front wall | SECONDARY AIR PRESSURE | INNER FRONT WALL |  | SECONDARY AIR PRESSURE INNER FRONT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1TT551 |  | BB1TT551 | <IO NOT ASSIGNED> | Flue gas temperature 2 | FLUE GAS TEMPERATURE 2 |  |  | FLUE GAS TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT400 |  | BB1TT400 | <IO NOT ASSIGNED> | Primary air temperature before preheater | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  | PRIMARY AIR TEMPERATURE BEFORE PREHEATER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1PT403 |  | BB1PT403 | <IO NOT ASSIGNED> | Secondary air pressure inner back wall | SECONDARY AIR PRESSURE | INNER BACK WALL |  | SECONDARY AIR PRESSURE INNER BACK WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT550 |  | BB1PT550 | <IO NOT ASSIGNED> | Flue gas pressure at the outlet of the boiler | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  | FLUE GAS PRESSURE AT THE OUTLET OF THE BOILER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1TT012 |  | BB1TT012 | <IO NOT ASSIGNED> | Condensate temperature from primary air preheater | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R | CONDENSATE TEMPERATURE FROM PRIMARY AIR PREHEATE R | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT550 |  | BB1TT550 | <IO NOT ASSIGNED> | Flue gas temperature 1 | FLUE GAS TEMPERATURE 1 |  |  | FLUE GAS TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT412 |  | BB1TT412 | <IO NOT ASSIGNED> | Boiler temperature after empty draft 2 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  | BOILER TEMPERATURE AFTER EMPTY DRAFT 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT411 |  | BB1TT411 | <IO NOT ASSIGNED> | Boiler temperature after empty draft 1 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  | BOILER TEMPERATURE AFTER EMPTY DRAFT 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1QT552 |  | BB1QT552 | <IO NOT ASSIGNED> | Fluegas CO measurement | FLUEGAS CO MEASUREMENT |  |  | FLUEGAS CO MEASUREMENT | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1TT405 |  | BB1TT405 | <IO NOT ASSIGNED> | Primary air temperature | PRIMARY AIR TEMPERATURE |  |  | PRIMARY AIR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT415 |  | BB1TT415 | <IO NOT ASSIGNED> | Boiler bed temperature middle level | BOILER BED TEMPERATURE | MIDDLE LEVEL |  | BOILER BED TEMPERATURE MIDDLE LEVEL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT416 |  | BB1TT416 | <IO NOT ASSIGNED> | Boiler bed temperature lower level | BOILER BED TEMPERATURE | LOWER LEVEL |  | BOILER BED TEMPERATURE LOWER LEVEL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT410 |  | BB1TT410 | <IO NOT ASSIGNED> | Boiler 1st draft temperature | BOILER 1ST DRAFT | TEMPERATURE |  | BOILER 1ST DRAFT TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT116 |  | BB1TT116 | <IO NOT ASSIGNED> | Steam temperature to air preheater | STEAM TEMPERATURE TO | AIR PREHEATER |  | STEAM TEMPERATURE TO AIR PREHEATER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT308 |  | BB1TT308 | <IO NOT ASSIGNED> | Furnace temperature connection | FURNACE TEMPERATURE | CONNECTION |  | FURNACE TEMPERATURE CONNECTION | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1QT553 |  | BB1QT553 | <IO NOT ASSIGNED> | Boiler room gas detector | BOILER ROOM GAS DETECTOR |  |  | BOILER ROOM GAS DETECTOR | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1TT408 |  | BB1TT408 | <IO NOT ASSIGNED> | Secondary air fan motor bearing temperature 1 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT423 |  | BB1TT423 | <IO NOT ASSIGNED> | Secondary air fan motor bearing temperature 2 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT406 |  | BB1TT406 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 1 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT404 |  | BB1TT404 | <IO NOT ASSIGNED> | Primary air fan motor bearing temperature 1 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT409 |  | BB1TT409 | <IO NOT ASSIGNED> | Primary air fan motor bearing temperature 2 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT402 |  | BB1TT402 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 1 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT403 |  | BB1TT403 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 2 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT421 |  | BB1TT421 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 3 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT407 |  | BB1TT407 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 2 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT422 |  | BB1TT422 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 3 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1PT409 |  | BB1PT409 | <IO NOT ASSIGNED> | Secondary air pressure outer front wall | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  | SECONDARY AIR PRESSURE OUTER FRONT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT411 |  | BB1PT411 | <IO NOT ASSIGNED> | Secondary air pressure outer back wall | SECONDARY AIR PRESSURE | OUTER BACK WALL |  | SECONDARY AIR PRESSURE OUTER BACK WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT407 |  | BB1PT407 | <IO NOT ASSIGNED> | Tertiary air pressure right wall | TERTIARY AIR PRESSURE | RIGHT WALL |  | TERTIARY AIR PRESSURE RIGHT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT408 |  | BB1PT408 | <IO NOT ASSIGNED> | Tertiary air pressure left wall | TERTIARY AIR PRESSURE | LEFT WALL |  | TERTIARY AIR PRESSURE LEFT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1TT650 |  | BB1TT650 | <IO NOT ASSIGNED> | Scraper conveyor 1 temperature measurement | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  | SCRAPER CONVEYOR 1 TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1LT611 |  | BB1LT611 | <IO NOT ASSIGNED> | Unloading station 1 level | UNLOADING STATION 1 LEVEL |  |  | UNLOADING STATION 1 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1LT612 |  | BB1LT612 | <IO NOT ASSIGNED> | Unloading station 3 level | UNLOADING STATION 3 LEVEL |  |  | UNLOADING STATION 3 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1LT613 |  | BB1LT613 | <IO NOT ASSIGNED> | Unloading station 2 level | UNLOADING STATION 2 LEVEL |  |  | UNLOADING STATION 2 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1LT650 |  | BB1LT650 | <IO NOT ASSIGNED> | Fuel silo level radar 1 | FUEL SILO LEVEL RADAR 1 |  |  | FUEL SILO LEVEL RADAR 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1LT651 |  | BB1LT651 | <IO NOT ASSIGNED> | Fuel silo level radar 2 | FUEL SILO LEVEL RADAR 2 |  |  | FUEL SILO LEVEL RADAR 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1LT652 |  | BB1LT652 | <IO NOT ASSIGNED> | Fuel pocket level | FUEL POCKET LEVEL |  |  | FUEL POCKET LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1TT652 |  | BB1TT652 | <IO NOT ASSIGNED> | Fuel silo temperature measurement | FUEL SILO TEMPERATURE | MEASUREMENT |  | FUEL SILO TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT653 |  | BB1TT653 | <IO NOT ASSIGNED> | Fuel pocket temperature | FUEL POCKET TEMPERATURE |  |  | FUEL POCKET TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1PT552 |  | BB1PT552 | <IO NOT ASSIGNED> | ESP inlet pressure transmitter | ESP INLET PRESSURE | TRANSMITTER |  | ESP INLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT553 |  | BB1PT553 | <IO NOT ASSIGNED> | ESP outlet pressure transmitter | ESP OUTLET PRESSURE | TRANSMITTER |  | ESP OUTLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1QT554 |  | BB1QT554 | <IO NOT ASSIGNED> | Opacity after ESP | OPACITY AFTER ESP |  |  | OPACITY AFTER ESP | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA
BB1TT553 |  | BB1TT553 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 1 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT557 |  | BB1TT557 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 2 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT558 |  | BB1TT558 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 3 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT554 |  | BB1TT554 | <IO NOT ASSIGNED> | Flue gas fan bearing temperature | FLUE GAS FAN BEARING | TEMPERATURE |  | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT555 |  | BB1TT555 | <IO NOT ASSIGNED> | Flue gas fan bearing temperature | FLUE GAS FAN BEARING | TEMPERATURE |  | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT556 |  | BB1TT556 | <IO NOT ASSIGNED> | Flue gas temperature before stack | FLUE GAS TEMPERATURE | BEFORE STACK |  | FLUE GAS TEMPERATURE BEFORE STACK | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT850 |  | BB1TT850 | <IO NOT ASSIGNED> | ESP Ash hopper 1 temperature | ESP ASH HOPPER 1 | TEMPERATURE |  | ESP ASH HOPPER 1 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT851 |  | BB1TT851 | <IO NOT ASSIGNED> | ESP Ash hopper 2 temperature | ESP ASH HOPPER 2 | TEMPERATURE |  | ESP ASH HOPPER 2 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TS501 |  | BB1TS501 | <IO NOT ASSIGNED> | ESP Insulator 1 temperature | ESP INSULATOR 1 | TEMPERATURE |  | ESP INSULATOR 1 TEMPERATURE | TS | TEMPERATURE SWITCH | AI | MEAS_ANA
BB1TS508 |  | BB1TS508 | <IO NOT ASSIGNED> | ESP Insulator 2 temperature | ESP INSULATOR 2 | TEMPERATURE |  | ESP INSULATOR 2 TEMPERATURE | TS | TEMPERATURE SWITCH | AI | MEAS_ANA
BB1TT552 |  | BB1TT552 | <IO NOT ASSIGNED> | Flue gas temperature before ESP | FLUE GAS TEMPERATURE | BEFORE ESP |  | FLUE GAS TEMPERATURE BEFORE ESP | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1LT800 |  | BB1LT800 | <IO NOT ASSIGNED> | Recycled bed material hopper level switch | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  | RECYCLED BED MATERIAL HOPPER LEVEL SWITCH | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1LT802 |  | BB1LT802 | <IO NOT ASSIGNED> | Sand silo level measurement | SAND SILO LEVEL | MEASUREMENT |  | SAND SILO LEVEL MEASUREMENT | LT | LEVEL TRANSMITTER | AI | MEAS_ANA
BB1PT009 |  | BB1PT009 | <IO NOT ASSIGNED> | Cooling water pressure before pump | COOLING WATER PRESSURE | BEFORE PUMP |  | COOLING WATER PRESSURE BEFORE PUMP | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1TT031 |  | BB1TT031 | <IO NOT ASSIGNED> | Cooling water temperatureafter bottom ash conveyor | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  | COOLING WATER TEMPERATURE AFTER BOTTOM ASH CONVEYOR | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1PT478 |  | BB1PT478 | <IO NOT ASSIGNED> | Instrument air pressure | INSTRUMENT AIR PRESSURE |  |  | INSTRUMENT AIR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1PT402 |  | BB1PT402 | <IO NOT ASSIGNED> | Instrument air pressure after dryer | INSTRUMENT AIR PRESSURE | AFTER DRYER |  | INSTRUMENT AIR PRESSURE AFTER DRYER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA
BB1TT430 |  | BB1TT430 | <IO NOT ASSIGNED> | Instrument air tank temperature | INSTRUMENT AIR TANK | TEMPERATURE |  | INSTRUMENT AIR TANK TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1TT401 |  | BB1TT401 | <IO NOT ASSIGNED> | Boiler room upper part temperature | BOILER ROOM UPPER PART | TEMPERATURE |  | BOILER ROOM UPPER PART TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA
BB1LT101 |  | BB1LT101 | <IO NOT ASSIGNED> | Steam drum level 1 | STEAM DRUM LEVEL 1 |  |  | STEAM DRUM LEVEL 1 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS
BB1PT203 |  | BB1PT203 | <IO NOT ASSIGNED> | Steam drum pressure 2 | STEAM DRUM PRESSURE 2 |  |  | STEAM DRUM PRESSURE 2 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS
BB1LT102 |  | BB1LT102 | <IO NOT ASSIGNED> | Steam drum level 2 | STEAM DRUM LEVEL 2 |  |  | STEAM DRUM LEVEL 2 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS
BB1PT201 |  | BB1PT201 | <IO NOT ASSIGNED> | Steam drum pressure 1 | STEAM DRUM PRESSURE 1 |  |  | STEAM DRUM PRESSURE 1 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS
BB1LT103 |  | BB1LT103 | <IO NOT ASSIGNED> | Steam drum level 3 | STEAM DRUM LEVEL 3 |  |  | STEAM DRUM LEVEL 3 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS
BB1PT205 |  | BB1PT205 | <IO NOT ASSIGNED> | Steam outlet pressure from accumulator | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  | STEAM OUTLET PRESSURE FROM ACCUMULATOR | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS
BB1PT400 |  | BB1PT400 | <IO NOT ASSIGNED> | Primary air pressure | PRIMARY AIR PRESSURE |  |  | PRIMARY AIR PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS
BB1TT418 |  | BB1TT418 | <IO NOT ASSIGNED> | Bed temperature 4 | BED TEMPERATURE 4 |  |  | BED TEMPERATURE 4 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS
BB1PT404 |  | BB1PT404 | <IO NOT ASSIGNED> | Boiler upper part pressure 1 | BOILER UPPER PART | PRESSURE 1 |  | BOILER UPPER PART PRESSURE 1 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS
BB1FT400 |  | BB1FT400 | <IO NOT ASSIGNED> | Primary air flow | PRIMARY AIR FLOW |  |  | PRIMARY AIR FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS
BB1PT401 |  | BB1PT401 | <IO NOT ASSIGNED> | Secondary air pressure | SECONDARY AIR PRESSURE |  |  | SECONDARY AIR PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS
BB1FT401 |  | BB1FT401 | <IO NOT ASSIGNED> | Secondary air flow | SECONDARY AIR FLOW |  |  | SECONDARY AIR FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS
BB1TT417 |  | BB1TT417 | <IO NOT ASSIGNED> | Bed temperature 3 | BED TEMPERATURE 3 |  |  | BED TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS
BB1TT413 |  | BB1TT413 | <IO NOT ASSIGNED> | Bed temperature 1 | BED TEMPERATURE 1 |  |  | BED TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS
BB1TT414 |  | BB1TT414 | <IO NOT ASSIGNED> | Bed temperature 2 | BED TEMPERATURE 2 |  |  | BED TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS
BB1PT405 |  | BB1PT405 | <IO NOT ASSIGNED> | Boiler upper part pressure 2 | BOILER UPPER PART | PRESSURE 2 |  | BOILER UPPER PART PRESSURE 2 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS
BB1QT550 |  | BB1QT550 | <IO NOT ASSIGNED> | Fluegas oxygen measurement 1 | FLUEGAS OXYGEN | MEASUREMENT 1 |  | FLUEGAS OXYGEN MEASUREMENT 1 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | MEAS_ANA_SRS
BB1FT550 |  | BB1FT550 | <IO NOT ASSIGNED> | Recirculation gas flow | RECIRCULATION GAS FLOW |  |  | RECIRCULATION GAS FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS
BB1QT551 |  | BB1QT551 | <IO NOT ASSIGNED> | Fluegas oxygen measurement 2 | FLUEGAS OXYGEN | MEASUREMENT 2 |  | FLUEGAS OXYGEN MEASUREMENT 2 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | MEAS_ANA_SRS
BB1PT406 |  | BB1PT406 | <IO NOT ASSIGNED> | Boiler upper part pressure | BOILER UPPER PART | PRESSURE |  | BOILER UPPER PART PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS
BB1LS700 |  | BB1LS700 | RIO_01:01.DI:00 | Chemical tank 1 level switch | CHEMICAL TANK 1 | LEVEL SWITCH |  | CHEMICAL TANK 1 LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1LS701 |  | BB1LS701 | RIO_01:01.DI:01 | Chemical tank 2 level switch | CHEMICAL TANK 2 | LEVEL SWITCH |  | CHEMICAL TANK 2 LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS004 |  | BB1GS004 | RIO_01:01.DI:02 | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS003 |  | BB1GS003 | RIO_01:01.DI:03 | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS001 |  | BB1GS001 | RIO_01:02.DI:00 | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS002 |  | BB1GS002 | RIO_01:02.DI:01 | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS005 |  | BB1GS005 | RIO_01:02.DI:02 | FW tank overflow On-Off valve position | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS006 |  | BB1GS006 | RIO_01:02.DI:03 | FW tank overflow On-Off valve position | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS007 |  | BB1GS007 | RIO_01:03.DI:00 | Feedwater pump 1 on-off valve limit switch open | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS008 |  | BB1GS008 | RIO_01:03.DI:01 | Feedwater pump 1 on-off valve limit switch close | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS009 |  | BB1GS009 | RIO_01:03.DI:02 | Feed water pump 2 on-off valve limit switch open | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS010 |  | BB1GS010 | RIO_01:03.DI:03 | Feed water pump 2 on-off valve limit switch close | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS011 |  | BB1GS011 | RIO_01:04.DI:00 | Boiler bottom blow down on-off valve limit switch open | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS012 |  | BB1GS012 | RIO_01:04.DI:01 | Boiler bottom blow down on-off valve limit switch close | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS221 |  | BB1GS221 | RIO_01:04.DI:02 | Main steam valve by-pass open limit switch | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | MAIN STEAM VALVE BY-PASS OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS222 |  | BB1GS222 | RIO_01:04.DI:03 | Main steam valve by-pass close limit switch | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | MAIN STEAM VALVE BY-PASS CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS223 |  | BB1GS223 | RIO_01:05.DI:00 | Main steam line valve open limit switch | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | MAIN STEAM LINE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS224 |  | BB1GS224 | RIO_01:05.DI:01 | Main steam line valve close limit switch | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | MAIN STEAM LINE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS225 |  | BB1GS225 | RIO_01:05.DI:02 | Start-up line ON-OFF valve open limit switch | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | START-UP LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS226 |  | BB1GS226 | RIO_01:05.DI:03 | Start-up line ON-OFF valve close limit switch | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | START-UP LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS200 |  | BB1GS200 | RIO_01:06.DI:00 | Sootblower 1 IN limit switch | SOOTBLOWER 1 IN | LIMIT SWITCH |  | SOOTBLOWER 1 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS201 |  | BB1GS201 | RIO_01:06.DI:01 | Sootblower 1 OUT limit switch | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | SOOTBLOWER 1 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS203 |  | BB1GS203 | RIO_01:06.DI:02 | Sootblower 2 OUT limit switch | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | SOOTBLOWER 2 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS204 |  | BB1GS204 | RIO_01:06.DI:03 | Sootblower 2 IN limit switch | SOOTBLOWER 2 IN | LIMIT SWITCH |  | SOOTBLOWER 2 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS205 |  | BB1GS205 | RIO_01:07.DI:00 | Sootblower 3 OUT limit switch | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | SOOTBLOWER 3 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS206 |  | BB1GS206 | RIO_01:07.DI:01 | Sootblower 3 IN limit switch | SOOTBLOWER 3 IN | LIMIT SWITCH |  | SOOTBLOWER 3 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS207 |  | BB1GS207 | RIO_01:07.DI:02 | Sootblower 5 OUT limit switch | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | SOOTBLOWER 5 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS208 |  | BB1GS208 | RIO_01:07.DI:03 | Sootblower 5 IN limit switch | SOOTBLOWER 5 IN | LIMIT SWITCH |  | SOOTBLOWER 5 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS209 |  | BB1GS209 | RIO_01:08.DI:00 | Sootblower 6 OUT limit switch | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | SOOTBLOWER 6 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS210 |  | BB1GS210 | RIO_01:08.DI:01 | Sootblower 6 IN limit switch | SOOTBLOWER 6 IN | LIMIT SWITCH |  | SOOTBLOWER 6 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS211 |  | BB1GS211 | RIO_01:08.DI:02 | Sootblower 7 OUT limit switch | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | SOOTBLOWER 7 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS212 |  | BB1GS212 | RIO_01:08.DI:03 | Sootblower 7 IN limit switch | SOOTBLOWER 7 IN | LIMIT SWITCH |  | SOOTBLOWER 7 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS213 |  | BB1GS213 | RIO_01:09.DI:00 | Sootblower 8 OUT limit switch | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | SOOTBLOWER 8 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS214 |  | BB1GS214 | RIO_01:09.DI:01 | Sootblower 8 IN limit switch | SOOTBLOWER 8 IN | LIMIT SWITCH |  | SOOTBLOWER 8 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS227 |  | BB1GS227 | RIO_01:09.DI:02 | Sootblowing line on-off valve open limit switch | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | SOOTBLOWING LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS228 |  | BB1GS228 | RIO_01:09.DI:03 | Sootblowing line on-off valve close limit switch | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | SOOTBLOWING LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS231 |  | BB1GS231 | RIO_01:10.DI:00 | Steam accumulator pressure control valve open limit switch | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS230 |  | BB1GS230 | RIO_01:10.DI:01 | Steam accumulator pressure control valve close limit switch | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS233 |  | BB1GS233 | RIO_01:10.DI:02 | Steam pressure reduction valve open limit switch | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | STEAM PRESSURE REDUCTION VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS232 |  | BB1GS232 | RIO_01:10.DI:03 | Steam pressure reduction valve close limit switch | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | STEAM PRESSURE REDUCTION VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS217 |  | BB1GS217 | RIO_01:11.DI:00 | Main steam line accumulator bypass on-offvalve open limit switch | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS218 |  | BB1GS218 | RIO_01:11.DI:01 | Main steam line accumulator bypass on-offvalve close limit switch | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS219 |  | BB1GS219 | RIO_01:11.DI:02 | Steam accumulator ON-OFF isolating valve open limit switch | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS220 |  | BB1GS220 | RIO_01:11.DI:03 | Steam accumulator ON-OFF isolating valve close limit switch | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS217 |  | BB1GS217 | RIO_01:11.DI:00 | Steam accumulator by-passvalve open limit switch | STEAM ACCUMULATOR BY-PASS | VALVE OPEN LIMIT SWITCH |  | STEAM ACCUMULATOR BY-PASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS218 |  | BB1GS218 | RIO_01:11.DI:01 | Steam accumulator by-passvalve close limit switch | STEAM ACCUMULATOR BY-PASS | VALVE CLOSE LIMIT SWITCH |  | STEAM ACCUMULATOR BY-PASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS220 |  | BB1GS220 | RIO_01:11.DI:03 | Steam accumulator ON-OFF valve close limit switch | STEAM ACCUMULATOR ON-OFF | VALVE CLOSE LIMIT SWITCH |  | STEAM ACCUMULATOR ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS219 |  | BB1GS219 | RIO_01:11.DI:02 | Steam accumulator ON-OFF valve open limit switch | STEAM ACCUMULATOR ON-OFF | VALVE OPEN LIMIT SWITCH |  | STEAM ACCUMULATOR ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS215 |  | BB1GS215 | RIO_01:13.DI:00 | Primary air preheater on-off valve open limit switch | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS216 |  | BB1GS216 | RIO_01:13.DI:01 | Primary air preheater on-off valve close limit switch | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS621 |  | BB1GS621 | RIO_01:13.DI:02 | Unloading station 3, block 3, feeder 3, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS611 |  | BB1GS611 | RIO_01:13.DI:03 | Unloading station 2, block 2, feeder 2, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS606 |  | BB1GS606 | RIO_01:14.DI:00 | Unloading station 1, block 1, feeder 4, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS614 |  | BB1GS614 | RIO_01:14.DI:01 | Unloading station 2, block 2, feeder 4, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS619 |  | BB1GS619 | RIO_01:14.DI:02 | Unloading station 3, block 3, feeder 2, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS651 |  | BB1GS651 | RIO_01:14.DI:03 | Disc screen by-pass damper limit switch to screen | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH TO SCREEN | GS | GATE SWITCH | DI | MEAS_BIN
BB1PS602 |  | BB1PS602 | RIO_01:15.DI:00 | Hydraulics unit 1, block 3, pressure switch | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 3, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN
BB1GS615 |  | BB1GS615 | RIO_01:15.DI:01 | Unloading station 2, block 2, feeder 4, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS623 |  | BB1GS623 | RIO_01:15.DI:02 | Unloading station 3, block 3, feeder 4, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1ST651 |  | BB1ST651 | RIO_01:15.DI:03 | Scraper conveyor 2, rotation guard | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | SCRAPER CONVEYOR 2, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1GS603 |  | BB1GS603 | RIO_01:16.DI:00 | Unloading station 1, block 1, feeder 2, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1PS601 |  | BB1PS601 | RIO_01:16.DI:01 | Hydraulics unit 1, block 2, pressure switch | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 2, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN
BB1GS650 |  | BB1GS650 | RIO_01:16.DI:02 | Disc screen by-pass damper limit switch by-pass pos. | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH BY-PASS POS. | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS622 |  | BB1GS622 | RIO_01:16.DI:03 | Unloading station 3, block 3, feeder 4, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS602 |  | BB1GS602 | RIO_01:17.DI:00 | Unloading station 1, block 1, feeder 2, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS655 |  | BB1LS655 | RIO_01:17.DI:01 | Scraper conveyor 2, turning point blockage guard | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | SCRAPER CONVEYOR 2, TURNING POINT BLOCKAGE GU ARD | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS607 |  | BB1GS607 | RIO_01:17.DI:02 | Unloading station 1, block 1, feeder 4, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS605 |  | BB1GS605 | RIO_01:17.DI:03 | Unloading station 1, block 1, feeder 3, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS652 |  | BB1LS652 | RIO_01:18.DI:00 | Unloading station 2, block 2, blockage guard | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | UNLOADING STATION 2, BLOCK 2, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS601 |  | BB1GS601 | RIO_01:18.DI:01 | Unloading station 1, block 1, feeder 1, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS608 |  | BB1LS608 | RIO_01:18.DI:02 | Hydraulics unit 1, low oil level alarm | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | HYDRAULICS UNIT 1, LOW OIL LEVEL ALARM | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1LS656 |  | BB1LS656 | RIO_01:18.DI:03 | Scraper conveyor 2, fuel silo side blockage guard | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | SCRAPER CONVEYOR 2, FUEL SILO SIDE BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1LS600 |  | BB1LS600 | RIO_01:19.DI:00 | Hydraulics unit 1, leaking pool limit switch | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | HYDRAULICS UNIT 1, LEAKING POOL LIMIT SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS609 |  | BB1GS609 | RIO_01:19.DI:01 | Unloading station 2, block 2, feeder 1, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS650 |  | BB1LS650 | RIO_01:19.DI:02 | Scraper conveyor 1 bed height level switch | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | SCRAPER CONVEYOR 1 BED HEIGHT LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS617 |  | BB1GS617 | RIO_01:19.DI:03 | Unloading station 3, block 3, feeder 1, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS651 |  | BB1LS651 | RIO_01:20.DI:00 | Unloading station 3, block 3, blockage guard | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | UNLOADING STATION 3, BLOCK 3, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS612 |  | BB1GS612 | RIO_01:20.DI:01 | Unloading station 2, block 2, feeder 3, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS654 |  | BB1LS654 | RIO_01:20.DI:02 | Scraper conveyor 1, blockage guard | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | SCRAPER CONVEYOR 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS613 |  | BB1GS613 | RIO_01:20.DI:03 | Unloading station 2, block 2, feeder 3, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS620 |  | BB1GS620 | RIO_01:21.DI:00 | Unloading station 3, block 3, feeder 3, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS618 |  | BB1GS618 | RIO_01:21.DI:01 | Unloading station 3, block 3, feeder 2, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1PS600 |  | BB1PS600 | RIO_01:21.DI:02 | Hydraulics unit 1, block 1, pressure switch | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 1, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN
BB1GS608 |  | BB1GS608 | RIO_01:21.DI:03 | Unloading station 2, block 2, feeder 1, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS604 |  | BB1GS604 | RIO_01:22.DI:00 | Unloading station 1, block 1, feeder 3, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS653 |  | BB1LS653 | RIO_01:22.DI:01 | Unloading station 1, block 1, blockage guard | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | UNLOADING STATION 1, BLOCK 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS616 |  | BB1GS616 | RIO_01:22.DI:02 | Unloading station 3, block 3, feeder 1, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS600 |  | BB1GS600 | RIO_01:22.DI:03 | Unloading station 1, block 1, feeder 1, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1ST650 |  | BB1ST650 | RIO_01:23.DI:00 | Scraper conveyor 1, rotation guard | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | SCRAPER CONVEYOR 1, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1GS610 |  | BB1GS610 | RIO_01:23.DI:01 | Unloading station 2, block 2, feeder 2, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN
BB1ST675 |  | BB1ST675 | RIO_01:23.DI:02 | Leveling roller 3 speed switch | LEVELING ROLLER 3 | SPEED SWITCH |  | LEVELING ROLLER 3 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1TS608 |  | BB1TS608 | RIO_01:23.DI:03 | High temperature switch hydraulic oil | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | HIGH TEMPERATURE SWITCH HYDRAULIC OIL | TS | TEMPERATURE SWITCH | DI | MEAS_BIN
BB1ST673 |  | BB1ST673 | RIO_01:24.DI:00 | Leveling roller 1 speed switch | LEVELING ROLLER 1 | SPEED SWITCH |  | LEVELING ROLLER 1 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1TS600 |  | BB1TS600 | RIO_01:24.DI:01 | Hydraulics unit, thermostat for heater | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | HYDRAULICS UNIT, THERMOSTAT FOR HEATER | TS | TEMPERATURE SWITCH | DI | MEAS_BIN
BB1ST674 |  | BB1ST674 | RIO_01:24.DI:02 | Leveling roller 2 speed switch | LEVELING ROLLER 2 | SPEED SWITCH |  | LEVELING ROLLER 2 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1PS605 |  | BB1PS605 | RIO_01:24.DI:03 | Hydraulic oil return block 3 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 3 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN
BB1PS603 |  | BB1PS603 | RIO_01:25.DI:00 | Hydraulic oil return block 1 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 1 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN
BB1PS604 |  | BB1PS604 | RIO_01:25.DI:01 | Hydraulic oil return block 2 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 2 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN
BB1ST654 |  | BB1ST654 | RIO_01:25.DI:02 | Belt magnet rotation guard | BELT MAGNET | ROTATION GUARD |  | BELT MAGNET ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1GS661 |  | BB1GS661 | RIO_01:25.DI:03 | Belt magnet deviation detector 1 | BELT MAGNET | DEVIATION DETECTOR 1 |  | BELT MAGNET DEVIATION DETECTOR 1 | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS662 |  | BB1GS662 | RIO_01:26.DI:00 | Belt magnet deviation detector 2 | BELT MAGNET | DEVIATION DETECTOR 2 |  | BELT MAGNET DEVIATION DETECTOR 2 | GS | GATE SWITCH | DI | MEAS_BIN
BB1ST652 |  | BB1ST652 | RIO_01:26.DI:01 | Belt conveyor rotation guard | BELT CONVEYOR | ROTATION GUARD |  | BELT CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1GS659 |  | BB1GS659 | RIO_01:26.DI:02 | Belt conveyor deviation detector 1 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | BELT CONVEYOR DEVIATION DETECTOR 1 | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS660 |  | BB1GS660 | RIO_01:26.DI:03 | Belt conveyor deviation detector 2 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | BELT CONVEYOR DEVIATION DETECTOR 2 | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS663 |  | BB1GS663 | RIO_01:27.DI:00 | Belt conveyor oversize detector | BELT CONVEYOR | OVERSIZE DETECTOR |  | BELT CONVEYOR OVERSIZE DETECTOR | GS | GATE SWITCH | DI | MEAS_BIN
BB1ST656 |  | BB1ST656 | RIO_01:27.DI:01 | Disc screen drive 1 rotation guard | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | DISC SCREEN DRIVE 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST657 |  | BB1ST657 | RIO_01:27.DI:02 | Disc screen drive 2 rotation guard | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | DISC SCREEN DRIVE 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1GS652 |  | BB1GS652 | RIO_01:27.DI:03 | Explosion hatch limit switch 1 | EXPLOSION HATCH | LIMIT SWITCH 1 |  | EXPLOSION HATCH LIMIT SWITCH 1 | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS653 |  | BB1GS653 | RIO_01:28.DI:00 | Explosion hatch limit switch 2 | EXPLOSION HATCH | LIMIT SWITCH 2 |  | EXPLOSION HATCH LIMIT SWITCH 2 | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS654 |  | BB1GS654 | RIO_01:28.DI:01 | Explosion hatch limit switch 3 | EXPLOSION HATCH | LIMIT SWITCH 3 |  | EXPLOSION HATCH LIMIT SWITCH 3 | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS655 |  | BB1GS655 | RIO_01:28.DI:02 | Explosion hatch limit switch 4 | EXPLOSION HATCH | LIMIT SWITCH 4 |  | EXPLOSION HATCH LIMIT SWITCH 4 | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS657 |  | BB1LS657 | RIO_01:28.DI:03 | Fuel silo discharge screw blockage switch | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | FUEL SILO DISCHARGE SCREW BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1LS658 |  | BB1LS658 | RIO_01:29.DI:00 | Fuel silo cross conveyor blockage switch | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | FUEL SILO CROSS CONVEYOR BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
<004> |  | <004> | <IO NOT ASSIGNED> | Fuel silo cross conveyor explosion hatch limit switch | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | FUEL SILO CROSS CONVEYOR EXPLOSION HATCH LIMIT SWITCH | 4> | #N/A | DI | #N/A
BB1LS659 |  | BB1LS659 | RIO_01:29.DI:01 | Fuel feeding screw 1 blockage switch | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | FUEL FEEDING SCREW 1 BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1LS660 |  | BB1LS660 | RIO_01:29.DI:02 | Fuel feeding screw 2 blockage switch | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | FUEL FEEDING SCREW 2 BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1ST649 |  | BB1ST649 | RIO_01:29.DI:03 | Fuel silo cross conveyor rotation guard | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | FUEL SILO CROSS CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST652 |  | BB1ST652 | RIO_01:26.DI:01 | Rotating fuel spreader rotation guard | ROTATING FUEL SPREADER | ROTATION GUARD |  | ROTATING FUEL SPREADER ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST653 |  | BB1ST653 | RIO_01:30.DI:01 | Fuel feeding screw 2 rotation guard | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | FUEL FEEDING SCREW 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST654 |  | BB1ST654 | RIO_01:25.DI:02 | Fuel feeding rotary feeder 1 rotation guard | FUEL FEEDING ROTARY | FEEDER 1 ROTATION GUARD |  | FUEL FEEDING ROTARY FEEDER 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST655 |  | BB1ST655 | RIO_01:30.DI:03 | Fuel feeding rotary feeder 2 rotation guard | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | FUEL FEEDING ROTARY FEEDER 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST659 |  | BB1ST659 | RIO_01:31.DI:00 | Fuel feeding screw 1 rotation guard | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | FUEL FEEDING SCREW 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1GS655 |  | BB1GS655 | RIO_01:28.DI:02 | Slide gate valve open limit switch | SLIDE GATE VALVE OPEN | LIMIT SWITCH |  | SLIDE GATE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS656 |  | BB1GS656 | RIO_01:31.DI:02 | Slide gate valve close limit switch | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | SLIDE GATE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS661 |  | BB1LS661 | RIO_01:31.DI:03 | Lubrication alarm screw discharger | LUBRICATION ALARM | SCREW DISCHARGER |  | LUBRICATION ALARM SCREW DISCHARGER | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1GS802 |  | BB1GS802 | RIO_01:32.DI:00 | Bottom ash valve limit switch | BOTTOM ASH VALVE | LIMIT SWITCH |  | BOTTOM ASH VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS803 |  | BB1GS803 | RIO_01:32.DI:01 | Bottom ash dropping chuteclosing device limit switch | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS852 |  | BB1LS852 | RIO_01:32.DI:02 | Fly ash container level switch | FLY ASH CONTAINER | LEVEL SWITCH |  | FLY ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1ST805 |  | BB1ST805 | RIO_01:32.DI:03 | Heated ESP collection screw rotation guard | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  | HEATED ESP COLLECTION SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST808 |  | BB1ST808 | RIO_01:33.DI:00 | ESP hopper 2 screw rotation guard | ESP HOPPER 2 SCREW | ROTATION GUARD |  | ESP HOPPER 2 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST809 |  | BB1ST809 | RIO_01:33.DI:01 | ESP hopper 1 screw rotation guard | ESP HOPPER 1 SCREW | ROTATION GUARD |  | ESP HOPPER 1 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST804 |  | BB1ST804 | RIO_01:33.DI:02 | ESP Rotary valve rotation guard | ESP ROTARY VALVE | ROTATION GUARD |  | ESP ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1TS808 |  | BB1TS808 | RIO_01:33.DI:03 | ESP Ash hopper 2 overheat thermostat | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  | ESP ASH HOPPER 2 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN
BB1TS809 |  | BB1TS809 | RIO_01:34.DI:00 | ESP Ash hopper 1 overheat thermostat | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  | ESP ASH HOPPER 1 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN
BB1TS805 |  | BB1TS805 | RIO_01:34.DI:01 | ESP collection screw heating thermostat | ESP COLLECTION SCREW | HEATING THERMOSTAT |  | ESP COLLECTION SCREW HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN
BB1TS804 |  | BB1TS804 | RIO_01:34.DI:02 | ESP Rotary valve heating thermostat | ESP ROTARY VALVE | HEATING THERMOSTAT |  | ESP ROTARY VALVE HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN
BB1GS855 |  | BB1GS855 | RIO_01:34.DI:03 | Bottom ash valve solenoid valve open limit switch | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS856 |  | BB1GS856 | RIO_01:35.DI:00 | Bottom ash valve solenoid valve close limit switch | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS857 |  | BB1GS857 | RIO_01:35.DI:01 | Bottom ash valve solenoid valve open limit switch | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS858 |  | BB1GS858 | RIO_01:35.DI:02 | Bottom ash valve solenoid valve close limit switch | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS850 |  | BB1GS850 | RIO_01:35.DI:03 | Bottom ash sieve bypass valve close limit switch | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH SIEVE BYPASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS851 |  | BB1GS851 | RIO_01:36.DI:00 | Bottom ash sieve bypass valve open limit switch | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH SIEVE BYPASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1FS003 |  | BB1FS003 | RIO_01:36.DI:01 | Bottom ash cooling flow switch | BOTTOM ASH COOLING | FLOW SWITCH |  | BOTTOM ASH COOLING FLOW SWITCH | FS | FLOW SWITCH | DI | MEAS_BIN
BB1GS801 |  | BB1GS801 | RIO_01:36.DI:02 | Sand filling valve position open limit switch | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | SAND FILLING VALVE POSITION OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS800 |  | BB1GS800 | RIO_01:36.DI:03 | Sand filling valve position close limit switch | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | SAND FILLING VALVE POSITION CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS854 |  | BB1GS854 | RIO_01:37.DI:00 | Bottom ash dropping chute limit switch | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | BOTTOM ASH DROPPING CHUTE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS853 |  | BB1GS853 | RIO_01:37.DI:01 | Bottom ash dropping chute closing device limit switch | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1GS859 |  | BB1GS859 | RIO_01:37.DI:02 | Bottom ash to container in place | BOTTOM ASH TO CONTAINER | IN PLACE |  | BOTTOM ASH TO CONTAINER IN PLACE | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS850 |  | BB1LS850 | RIO_01:37.DI:03 | Bottom ash container level switch | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1LS851 |  | BB1LS851 | RIO_01:38.DI:00 | Bottom ash container level switch | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN
BB1PT800 |  | BB1PT800 | RIO_01:38.DI:01 | Recycled bed material damper pressure switch | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  | RECYCLED BED MATERIAL DAMPER PRESSURE SWITCH | PT | PRESSURE TRANSMITTER | DI | MEAS_BIN
BB1ST856 |  | BB1ST856 | RIO_01:38.DI:02 | Purified sand screw conveyor rotation guard | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | PURIFIED SAND SCREW CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST850 |  | BB1ST850 | RIO_01:38.DI:03 | Bottom ash conveyor rotation guard | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | BOTTOM ASH CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1GS852 |  | BB1GS852 | RIO_01:39.DI:00 | Bottom ash conveyor blockage detector | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | BOTTOM ASH CONVEYOR BLOCKAGE DETECTOR | GS | GATE SWITCH | DI | MEAS_BIN
BB1ST852 |  | BB1ST852 | RIO_01:39.DI:01 | 2nd pass fly ash rotary valve rotation guard | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 2ND PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1ST853 |  | BB1ST853 | RIO_01:39.DI:02 | 3rd pass fly ash rotary valve rotation guard | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 3RD PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN
BB1GS020 |  | BB1GS020 | RIO_01:39.DI:03 | Emergency shower use switch | EMERGENCY SHOWER | USE SWITCH |  | EMERGENCY SHOWER USE SWITCH | GS | GATE SWITCH | DI | MEAS_BIN
BB1LS103 |  | BB1LS103 | <IO NOT ASSIGNED> | Steam drum level switch 1 | STEAM DRUM LEVEL SWITCH 1 |  |  | STEAM DRUM LEVEL SWITCH 1 | LS | LEVEL SWITCH |  | MEAS_BIN_SRS
BB1LS104 |  | BB1LS104 | <IO NOT ASSIGNED> | Steam drum level switch 2 | STEAM DRUM LEVEL SWITCH 2 |  |  | STEAM DRUM LEVEL SWITCH 2 | LS | LEVEL SWITCH |  | MEAS_BIN_SRS
BB1HS101 |  | BB1HS101 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 1 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  | BOILER EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS103 |  | BB1HS103 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 3 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  | BOILER EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS104 |  | BB1HS104 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 4 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  | BOILER EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS102 |  | BB1HS102 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 2 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  | BOILER EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS105 |  | BB1HS105 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 5 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  | BOILER EMERGENCY SHUTDOWN SWITCH 5 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS106 |  | BB1HS106 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 6 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  | BOILER EMERGENCY SHUTDOWN SWITCH 6 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS107 |  | BB1HS107 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 7 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  | BOILER EMERGENCY SHUTDOWN SWITCH 7 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS108 |  | BB1HS108 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 8 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  | BOILER EMERGENCY SHUTDOWN SWITCH 8 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS109 |  | BB1HS109 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 9 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  | BOILER EMERGENCY SHUTDOWN SWITCH 9 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS110 |  | BB1HS110 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 10 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  | BOILER EMERGENCY SHUTDOWN SWITCH 10 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS111 |  | BB1HS111 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 11 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  | BOILER EMERGENCY SHUTDOWN SWITCH 11 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS112 |  | BB1HS112 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 12 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  | BOILER EMERGENCY SHUTDOWN SWITCH 12 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS601 |  | BB1HS601 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 1 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS602 |  | BB1HS602 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 2 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS603 |  | BB1HS603 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 3 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1HS604 |  | BB1HS604 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 4 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS
BB1IV002 | _OPEN | BB1IV002_OPEN | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve OPEN | FEEDWATER PUMP 1 ON-OFF | VALVE OPEN |  | FEEDWATER PUMP 1 ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV002 | _CLOSE | BB1IV002_CLOSE | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve CLOSE | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSE |  | FEEDWATER PUMP 1 ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV002 | _OPENED | BB1IV002_OPENED | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve OPENED | FEEDWATER PUMP 1 ON-OFF | VALVE OPENED |  | FEEDWATER PUMP 1 ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV002 | _CLOSED | BB1IV002_CLOSED | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve CLOSED | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSED |  | FEEDWATER PUMP 1 ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV002 | _FAULT | BB1IV002_FAULT | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve FAULT | FEEDWATER PUMP 1 ON-OFF | VALVE FAULT |  | FEEDWATER PUMP 1 ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV002 | _POSITION | BB1IV002_POSITION | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve POSITION | FEEDWATER PUMP 1 ON-OFF | VALVE POSITION |  | FEEDWATER PUMP 1 ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV003 | _OPEN | BB1IV003_OPEN | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve OPEN | FEED WATER PUMP 2 ON-OFF | VALVE OPEN |  | FEED WATER PUMP 2 ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV003 | _CLOSE | BB1IV003_CLOSE | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve CLOSE | FEED WATER PUMP 2 ON-OFF | VALVE CLOSE |  | FEED WATER PUMP 2 ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV003 | _OPENED | BB1IV003_OPENED | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve OPENED | FEED WATER PUMP 2 ON-OFF | VALVE OPENED |  | FEED WATER PUMP 2 ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV003 | _CLOSED | BB1IV003_CLOSED | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve CLOSED | FEED WATER PUMP 2 ON-OFF | VALVE CLOSED |  | FEED WATER PUMP 2 ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV003 | _FAULT | BB1IV003_FAULT | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve FAULT | FEED WATER PUMP 2 ON-OFF | VALVE FAULT |  | FEED WATER PUMP 2 ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV003 | _POSITION | BB1IV003_POSITION | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve POSITION | FEED WATER PUMP 2 ON-OFF | VALVE POSITION |  | FEED WATER PUMP 2 ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV202 | _OPEN | BB1IV202_OPEN | <IO NOT ASSIGNED> | Main steam valve by-pass valve OPEN | MAIN STEAM VALVE BY-PASS | VALVE OPEN |  | MAIN STEAM VALVE BY-PASS VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV202 | _CLOSE | BB1IV202_CLOSE | <IO NOT ASSIGNED> | Main steam valve by-pass valve CLOSE | MAIN STEAM VALVE BY-PASS | VALVE CLOSE |  | MAIN STEAM VALVE BY-PASS VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV202 | _OPENED | BB1IV202_OPENED | <IO NOT ASSIGNED> | Main steam valve by-pass valve OPENED | MAIN STEAM VALVE BY-PASS | VALVE OPENED |  | MAIN STEAM VALVE BY-PASS VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV202 | _CLOSED | BB1IV202_CLOSED | <IO NOT ASSIGNED> | Main steam valve by-pass valve CLOSED | MAIN STEAM VALVE BY-PASS | VALVE CLOSED |  | MAIN STEAM VALVE BY-PASS VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV202 | _FAULT | BB1IV202_FAULT | <IO NOT ASSIGNED> | Main steam valve by-pass valve FAULT | MAIN STEAM VALVE BY-PASS | VALVE FAULT |  | MAIN STEAM VALVE BY-PASS VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV202 | _POSITION | BB1IV202_POSITION | <IO NOT ASSIGNED> | Main steam valve by-pass valve POSITION | MAIN STEAM VALVE BY-PASS | VALVE POSITION |  | MAIN STEAM VALVE BY-PASS VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1CV201 | _OPEN | BB1CV201_OPEN | <IO NOT ASSIGNED> | Start-up valve OPEN | START-UP VALVE OPEN |  |  | START-UP VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV201 | _CLOSE | BB1CV201_CLOSE | <IO NOT ASSIGNED> | Start-up valve CLOSE | START-UP VALVE CLOSE |  |  | START-UP VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV201 | _OPENED | BB1CV201_OPENED | <IO NOT ASSIGNED> | Start-up valve OPENED | START-UP VALVE OPENED |  |  | START-UP VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV201 | _CLOSED | BB1CV201_CLOSED | <IO NOT ASSIGNED> | Start-up valve CLOSED | START-UP VALVE CLOSED |  |  | START-UP VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV201 | _FAULT | BB1CV201_FAULT | <IO NOT ASSIGNED> | Start-up valve FAULT | START-UP VALVE FAULT |  |  | START-UP VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV201 | _POSITION | BB1CV201_POSITION | <IO NOT ASSIGNED> | Start-up valve POSITION | START-UP VALVE POSITION |  |  | START-UP VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1IV201 | _OPEN | BB1IV201_OPEN | <IO NOT ASSIGNED> | Main steam valve OPEN | MAIN STEAM VALVE OPEN |  |  | MAIN STEAM VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV201 | _CLOSE | BB1IV201_CLOSE | <IO NOT ASSIGNED> | Main steam valve CLOSE | MAIN STEAM VALVE CLOSE |  |  | MAIN STEAM VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV201 | _OPENED | BB1IV201_OPENED | <IO NOT ASSIGNED> | Main steam valve OPENED | MAIN STEAM VALVE OPENED |  |  | MAIN STEAM VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV201 | _CLOSED | BB1IV201_CLOSED | <IO NOT ASSIGNED> | Main steam valve CLOSED | MAIN STEAM VALVE CLOSED |  |  | MAIN STEAM VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV201 | _FAULT | BB1IV201_FAULT | <IO NOT ASSIGNED> | Main steam valve FAULT | MAIN STEAM VALVE FAULT |  |  | MAIN STEAM VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV201 | _POSITION | BB1IV201_POSITION | <IO NOT ASSIGNED> | Main steam valve POSITION | MAIN STEAM VALVE POSITION |  |  | MAIN STEAM VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV200 | _OPEN | BB1IV200_OPEN | <IO NOT ASSIGNED> | Start-up check valve OPEN | START-UP CHECK VALVE | OPEN |  | START-UP CHECK VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV200 | _CLOSE | BB1IV200_CLOSE | <IO NOT ASSIGNED> | Start-up check valve CLOSE | START-UP CHECK VALVE | CLOSE |  | START-UP CHECK VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV200 | _OPENED | BB1IV200_OPENED | <IO NOT ASSIGNED> | Start-up check valve OPENED | START-UP CHECK VALVE | OPENED |  | START-UP CHECK VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV200 | _CLOSED | BB1IV200_CLOSED | <IO NOT ASSIGNED> | Start-up check valve CLOSED | START-UP CHECK VALVE | CLOSED |  | START-UP CHECK VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV200 | _FAULT | BB1IV200_FAULT | <IO NOT ASSIGNED> | Start-up check valve FAULT | START-UP CHECK VALVE | FAULT |  | START-UP CHECK VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV200 | _POSITION | BB1IV200_POSITION | <IO NOT ASSIGNED> | Start-up check valve POSITION | START-UP CHECK VALVE | POSITION |  | START-UP CHECK VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV203 | _OPEN | BB1IV203_OPEN | <IO NOT ASSIGNED> | Sootblowing line on-off valve OPEN | SOOTBLOWING LINE ON-OFF | VALVE OPEN |  | SOOTBLOWING LINE ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV203 | _CLOSE | BB1IV203_CLOSE | <IO NOT ASSIGNED> | Sootblowing line on-off valve CLOSE | SOOTBLOWING LINE ON-OFF | VALVE CLOSE |  | SOOTBLOWING LINE ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV203 | _OPENED | BB1IV203_OPENED | <IO NOT ASSIGNED> | Sootblowing line on-off valve OPENED | SOOTBLOWING LINE ON-OFF | VALVE OPENED |  | SOOTBLOWING LINE ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV203 | _CLOSED | BB1IV203_CLOSED | <IO NOT ASSIGNED> | Sootblowing line on-off valve CLOSED | SOOTBLOWING LINE ON-OFF | VALVE CLOSED |  | SOOTBLOWING LINE ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV203 | _FAULT | BB1IV203_FAULT | <IO NOT ASSIGNED> | Sootblowing line on-off valve FAULT | SOOTBLOWING LINE ON-OFF | VALVE FAULT |  | SOOTBLOWING LINE ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV203 | _POSITION | BB1IV203_POSITION | <IO NOT ASSIGNED> | Sootblowing line on-off valve POSITION | SOOTBLOWING LINE ON-OFF | VALVE POSITION |  | SOOTBLOWING LINE ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1CV003 | _OPEN | BB1CV003_OPEN | <IO NOT ASSIGNED> | Continuous blow down valve OPEN | CONTINUOUS BLOW DOWN | VALVE OPEN |  | CONTINUOUS BLOW DOWN VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV003 | _CLOSE | BB1CV003_CLOSE | <IO NOT ASSIGNED> | Continuous blow down valve CLOSE | CONTINUOUS BLOW DOWN | VALVE CLOSE |  | CONTINUOUS BLOW DOWN VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV003 | _OPENED | BB1CV003_OPENED | <IO NOT ASSIGNED> | Continuous blow down valve OPENED | CONTINUOUS BLOW DOWN | VALVE OPENED |  | CONTINUOUS BLOW DOWN VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _CLOSED | BB1CV003_CLOSED | <IO NOT ASSIGNED> | Continuous blow down valve CLOSED | CONTINUOUS BLOW DOWN | VALVE CLOSED |  | CONTINUOUS BLOW DOWN VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _FAULT | BB1CV003_FAULT | <IO NOT ASSIGNED> | Continuous blow down valve FAULT | CONTINUOUS BLOW DOWN | VALVE FAULT |  | CONTINUOUS BLOW DOWN VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _POSITION | BB1CV003_POSITION | <IO NOT ASSIGNED> | Continuous blow down valve POSITION | CONTINUOUS BLOW DOWN | VALVE POSITION |  | CONTINUOUS BLOW DOWN VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1CV203 | _OPEN | BB1CV203_OPEN | <IO NOT ASSIGNED> | Steam accumulator pressure control valve OPEN | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV203 | _CLOSE | BB1CV203_CLOSE | <IO NOT ASSIGNED> | Steam accumulator pressure control valve CLOSE | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV203 | _OPENED | BB1CV203_OPENED | <IO NOT ASSIGNED> | Steam accumulator pressure control valve OPENED | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPENED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _CLOSED | BB1CV203_CLOSED | <IO NOT ASSIGNED> | Steam accumulator pressure control valve CLOSED | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _FAULT | BB1CV203_FAULT | <IO NOT ASSIGNED> | Steam accumulator pressure control valve FAULT | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | FAULT | STEAM ACCUMULATOR PRESSURE CONTROL VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _POSITION | BB1CV203_POSITION | <IO NOT ASSIGNED> | Steam accumulator pressure control valve POSITION | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | POSITION | STEAM ACCUMULATOR PRESSURE CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1CV202 | _OPEN | BB1CV202_OPEN | <IO NOT ASSIGNED> | Steam pressure reduction valve OPEN | STEAM PRESSURE REDUCTION | VALVE OPEN |  | STEAM PRESSURE REDUCTION VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV202 | _CLOSE | BB1CV202_CLOSE | <IO NOT ASSIGNED> | Steam pressure reduction valve CLOSE | STEAM PRESSURE REDUCTION | VALVE CLOSE |  | STEAM PRESSURE REDUCTION VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV202 | _OPENED | BB1CV202_OPENED | <IO NOT ASSIGNED> | Steam pressure reduction valve OPENED | STEAM PRESSURE REDUCTION | VALVE OPENED |  | STEAM PRESSURE REDUCTION VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _CLOSED | BB1CV202_CLOSED | <IO NOT ASSIGNED> | Steam pressure reduction valve CLOSED | STEAM PRESSURE REDUCTION | VALVE CLOSED |  | STEAM PRESSURE REDUCTION VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _FAULT | BB1CV202_FAULT | <IO NOT ASSIGNED> | Steam pressure reduction valve FAULT | STEAM PRESSURE REDUCTION | VALVE FAULT |  | STEAM PRESSURE REDUCTION VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _POSITION | BB1CV202_POSITION | <IO NOT ASSIGNED> | Steam pressure reduction valve POSITION | STEAM PRESSURE REDUCTION | VALVE POSITION |  | STEAM PRESSURE REDUCTION VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1IV204 | _OPEN | BB1IV204_OPEN | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve OPEN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV204 | _CLOSE | BB1IV204_CLOSE | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve CLOSE | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV204 | _OPENED | BB1IV204_OPENED | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve OPENED | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPENED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _CLOSED | BB1IV204_CLOSED | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve CLOSED | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _FAULT | BB1IV204_FAULT | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve FAULT | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE FAULT | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _POSITION | BB1IV204_POSITION | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve POSITION | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE POSITION | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV205 | _OPEN | BB1IV205_OPEN | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve OPEN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV205 | _CLOSE | BB1IV205_CLOSE | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve CLOSE | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV205 | _OPENED | BB1IV205_OPENED | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve OPENED | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPENED |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _CLOSED | BB1IV205_CLOSED | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve CLOSED | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSED |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _FAULT | BB1IV205_FAULT | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve FAULT | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE FAULT |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _POSITION | BB1IV205_POSITION | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve POSITION | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE POSITION |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV206 | _OPEN | BB1IV206_OPEN | <IO NOT ASSIGNED> | Primary air preheater on-off valve OPEN | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN |  | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV206 | _CLOSE | BB1IV206_CLOSE | <IO NOT ASSIGNED> | Primary air preheater on-off valve CLOSE | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE |  | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV206 | _OPENED | BB1IV206_OPENED | <IO NOT ASSIGNED> | Primary air preheater on-off valve OPENED | PRIMARY AIR PREHEATER | ON-OFF VALVE OPENED |  | PRIMARY AIR PREHEATER ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _CLOSED | BB1IV206_CLOSED | <IO NOT ASSIGNED> | Primary air preheater on-off valve CLOSED | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSED |  | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _FAULT | BB1IV206_FAULT | <IO NOT ASSIGNED> | Primary air preheater on-off valve FAULT | PRIMARY AIR PREHEATER | ON-OFF VALVE FAULT |  | PRIMARY AIR PREHEATER ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _POSITION | BB1IV206_POSITION | <IO NOT ASSIGNED> | Primary air preheater on-off valve POSITION | PRIMARY AIR PREHEATER | ON-OFF VALVE POSITION |  | PRIMARY AIR PREHEATER ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1FM001 | _ESTOP | BB1FM001_ESTOP | <IO NOT ASSIGNED> | Bottom ash sieve feed ESTOP | BOTTOM ASH SIEVE FEED | ESTOP |  | BOTTOM ASH SIEVE FEED ESTOP | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _RUNNING | BB1FM001_RUNNING | <IO NOT ASSIGNED> | Bottom ash sieve feed RUNNING | BOTTOM ASH SIEVE FEED | RUNNING |  | BOTTOM ASH SIEVE FEED RUNNING | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _MAN_AUTO | BB1FM001_MAN_AUTO | <IO NOT ASSIGNED> | Bottom ash sieve feed MAN/AUTO | BOTTOM ASH SIEVE FEED | MAN/AUTO |  | BOTTOM ASH SIEVE FEED MAN/AUTO | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _FAULT | BB1FM001_FAULT | <IO NOT ASSIGNED> | Bottom ash sieve feed THERMAL FAULT | BOTTOM ASH SIEVE FEED | THERMAL FAULT |  | BOTTOM ASH SIEVE FEED THERMAL FAULT | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _VOLTAGE_OK | BB1FM001_VOLTAGE_OK | <IO NOT ASSIGNED> | Bottom ash sieve feed VOLTAGE OK | BOTTOM ASH SIEVE FEED | VOLTAGE OK |  | BOTTOM ASH SIEVE FEED VOLTAGE OK | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _START_STOP | BB1FM001_START_STOP | <IO NOT ASSIGNED> | Bottom ash sieve feed START/STOP | BOTTOM ASH SIEVE FEED | START/STOP |  | BOTTOM ASH SIEVE FEED START/STOP | FM | MOTOR | DO | OESA_3ph
<005> |  | <005> | <IO NOT ASSIGNED> | Sand transmitter 230 Vac feed | SAND TRANSMITTER | 230 VAC FEED |  | SAND TRANSMITTER 230 VAC FEED | 5> | #N/A |  | #N/A
BB1FG300 | _ESP_COLLECTIVE_ALARM | BB1FG300_ESP_COLLECTIVE_ALARM | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_ALARM | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_COLLECTIVE_WARNING | BB1FG300_ESP_COLLECTIVE_WARNING | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_WARNING | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_IN_STANDBY | BB1FG300_ESP_IN_STANDBY | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_IN_STANDBY | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_IN_STANDBY | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_STANDBY | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_IN_OPERATION | BB1FG300_ESP_IN_OPERATION | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_IN_OPERATION | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_IN_OPERATION | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_OPERATION | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI1 | BB1FG300_ESP_SPARE_DI1 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI1 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI2 | BB1FG300_ESP_SPARE_DI2 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI2 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI3 | BB1FG300_ESP_SPARE_DI3 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI3 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI4 | BB1FG300_ESP_SPARE_DI4 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI4 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_EXT_RELEASE_FILTER | BB1FG300_ESP_EXT_RELEASE_FILTER | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_EXT_RELEASE_FILTER | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO1 | BB1FG300_ESP_SPARE_DO1 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO1 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO2 | BB1FG300_ESP_SPARE_DO2 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO2 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO3 | BB1FG300_ESP_SPARE_DO3 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO3 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO4 | BB1FG300_ESP_SPARE_DO4 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO4 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO5 | BB1FG300_ESP_SPARE_DO5 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO5 | FG | ESP | DO | ESP_DI_DO
BB1SI400 |  | BB1SI400 | <IO NOT ASSIGNED> | Primary air fan safety interlock | PRIMARY AIR FAN | SAFETY INTERLOCK |  | PRIMARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI401 |  | BB1SI401 | <IO NOT ASSIGNED> | Secondary air fan safety interlock | SECONDARY AIR FAN | SAFETY INTERLOCK |  | SECONDARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI603 |  | BB1SI603 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI604 |  | BB1SI604 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI605 |  | BB1SI605 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI658 |  | BB1SI658 | <IO NOT ASSIGNED> | Scraper Conveyor 1 safety interlock | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  | SCRAPER CONVEYOR 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI659 |  | BB1SI659 | <IO NOT ASSIGNED> | Belt Conveyor safety interlock | BELT CONVEYOR | SAFETY INTERLOCK |  | BELT CONVEYOR SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI675 |  | BB1SI675 | <IO NOT ASSIGNED> | Disc screen drive 1 safety interlock | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  | DISC SCREEN DRIVE 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI676 |  | BB1SI676 | <IO NOT ASSIGNED> | Disc screen drive 2 safety interlock | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  | DISC SCREEN DRIVE 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI672 |  | BB1SI672 | <IO NOT ASSIGNED> | Scraper Conveyor 2 safety interlock | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  | SCRAPER CONVEYOR 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI550 |  | BB1SI550 | <IO NOT ASSIGNED> | Flue gas fan safety interlock | FLUE GAS FAN | SAFETY INTERLOCK |  | FLUE GAS FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SV601 | _OUT | BB1SV601_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 1 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV601 | _IN | BB1SV601_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 1 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV603 | _OUT | BB1SV603_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 3 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV603 | _IN | BB1SV603_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 3 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV602 | _OUT | BB1SV602_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 2 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV602 | _IN | BB1SV602_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 2 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1EM603 | _LOCAL_MODE | BB1EM603_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM603 | _LOCAL_RUN | BB1EM603_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM603 | _ISOLATOR | BB1EM603_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _LOCAL_MODE | BB1EM604_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _LOCAL_RUN | BB1EM604_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _ISOLATOR | BB1EM604_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _LOCAL_MODE | BB1EM605_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _LOCAL_RUN | BB1EM605_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _ISOLATOR | BB1EM605_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM658 | _LOCAL_MODE | BB1EM658_LOCAL_MODE | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | SCRAPER CONVEYOR 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _LOCAL_RUN_FWD | BB1EM658_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _LOCAL_RUN_REV | BB1EM658_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_RUN_REV | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  | SCRAPER CONVEYOR 1 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _ISOLATOR | BB1EM658_ISOLATOR | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 ISOLATOR | SCRAPER CONVEYOR 1 | ISOLATOR |  | SCRAPER CONVEYOR 1 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_MODE | BB1EM659_LOCAL_MODE | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_MODE | BELT CONVEYOR | LOCAL_MODE |  | BELT CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_RUN_FWD | BB1EM659_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_RUN_FWD | BELT CONVEYOR | LOCAL_RUN_FWD |  | BELT CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_RUN_REV | BB1EM659_LOCAL_RUN_REV | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_RUN_REV | BELT CONVEYOR | LOCAL_RUN_REV |  | BELT CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _ISOLATOR | BB1EM659_ISOLATOR | <IO NOT ASSIGNED> | BELT CONVEYOR ISOLATOR | BELT CONVEYOR | ISOLATOR |  | BELT CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM675 | _LOCAL_MODE | BB1EM675_LOCAL_MODE | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_MODE | DISC SCREEN DRIVE 1 | LOCAL_MODE |  | DISC SCREEN DRIVE 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _LOCAL_RUN_FWD | BB1EM675_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD | DISC SCREEN DRIVE 1 | LOCAL_RUN_FWD |  | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _LOCAL_RUN_REV | BB1EM675_LOCAL_RUN_REV | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_RUN_REV | DISC SCREEN DRIVE 1 | LOCAL_RUN_REV |  | DISC SCREEN DRIVE 1 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _ISOLATOR | BB1EM675_ISOLATOR | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 ISOLATOR | DISC SCREEN DRIVE 1 | ISOLATOR |  | DISC SCREEN DRIVE 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM676 | _LOCAL_MODE | BB1EM676_LOCAL_MODE | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_MODE | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | DISC SCREEN DRIVE 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _LOCAL_RUN_FWD | BB1EM676_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _LOCAL_RUN_REV | BB1EM676_LOCAL_RUN_REV | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_RUN_REV | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | DISC SCREEN DRIVE 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _ISOLATOR | BB1EM676_ISOLATOR | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 ISOLATOR | DISC SCREEN DRIVE 2 | ISOLATOR |  | DISC SCREEN DRIVE 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_MODE | BB1EM672_LOCAL_MODE | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_MODE | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | SCRAPER CONVEYOR 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_RUN_FWD | BB1EM672_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_RUN_REV | BB1EM672_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_RUN_REV | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | SCRAPER CONVEYOR 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _ISOLATOR | BB1EM672_ISOLATOR | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 ISOLATOR | SCRAPER CONVEYOR 2 | ISOLATOR |  | SCRAPER CONVEYOR 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_MODE | BB1EM662_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_MODE | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | FUEL SILO SCREW DISCHARGE LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_RUN_FWD | BB1EM662_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | FUEL SILO SCREW DISCHARGE LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_RUN_REV | BB1EM662_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | FUEL SILO SCREW DISCHARGE LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _ISOLATOR | BB1EM662_ISOLATOR | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGEISOLATOR | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | FUEL SILO SCREW DISCHARGE ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_MODE | BB1EM650_LOCAL_MODE | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_MODE | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | SLEWING MOTOR FOR SCREW LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_RUN_FWD | BB1EM650_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_RUN_REV | BB1EM650_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _ISOLATOR | BB1EM650_ISOLATOR | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW ISOLATOR | SLEWING MOTOR FOR SCREW | ISOLATOR |  | SLEWING MOTOR FOR SCREW ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_MODE | BB1EM663_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_MODE | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | FUEL SILO CROSS CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_RUN_FWD | BB1EM663_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_RUN_REV | BB1EM663_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _ISOLATOR | BB1EM663_ISOLATOR | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR ISOLATOR | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | FUEL SILO CROSS CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_MODE | BB1EM664_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_MODE | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | FUEL FEEDING SCREW 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_RUN_FWD | BB1EM664_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_RUN_REV | BB1EM664_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_RUN_REV | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | FUEL FEEDING SCREW 1 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _ISOLATOR | BB1EM664_ISOLATOR | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 ISOLATOR | FUEL FEEDING SCREW 1 | ISOLATOR |  | FUEL FEEDING SCREW 1 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_MODE | BB1EM665_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_MODE | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | FUEL FEEDING SCREW 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_RUN_FWD | BB1EM665_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_RUN_REV | BB1EM665_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_RUN_REV | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | FUEL FEEDING SCREW 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _ISOLATOR | BB1EM665_ISOLATOR | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 ISOLATOR | FUEL FEEDING SCREW 2 | ISOLATOR |  | FUEL FEEDING SCREW 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_MODE | BB1EM852_LOCAL_MODE | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_MODE | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | BOTTOM ASH CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_RUN_FWD | BB1EM852_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_RUN_REV | BB1EM852_LOCAL_RUN_REV | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_RUN_REV | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | BOTTOM ASH CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _ISOLATOR | BB1EM852_ISOLATOR | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR ISOLATOR | BOTTOM ASH CONVEYOR | ISOLATOR |  | BOTTOM ASH CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM660 | _RUNNING | BB1EM660_RUNNING | <IO NOT ASSIGNED> | Cooling fan for slewing motor RUNNING | COOLING FAN FOR | SLEWING MOTOR RUNNING |  | COOLING FAN FOR SLEWING MOTOR RUNNING | EM | MOTOR | DI | DOL_DIR
BB1EM660 | _FAULT | BB1EM660_FAULT | <IO NOT ASSIGNED> | Cooling fan for slewing motor FAULT | COOLING FAN FOR | SLEWING MOTOR FAULT |  | COOLING FAN FOR SLEWING MOTOR FAULT | EM | MOTOR | DI | DOL_DIR
BB1EM660 | _RUN | BB1EM660_RUN | <IO NOT ASSIGNED> | Cooling fan for slewing motor RUN | COOLING FAN FOR | SLEWING MOTOR RUN |  | COOLING FAN FOR SLEWING MOTOR RUN | EM | MOTOR | DO | DOL_DIR
BB1EM660 | _ISOLATOR | BB1EM660_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan for slewing motor ISOLATOR | COOLING FAN FOR | SLEWING MOTOR ISOLATOR |  | COOLING FAN FOR SLEWING MOTOR ISOLATOR | EM | MOTOR | DI | DOL_DIR
BB1EM654 | _RUNNING | BB1EM654_RUNNING | <IO NOT ASSIGNED> | Lubrication unit RUNNING | LUBRICATION UNIT RUNNING |  |  | LUBRICATION UNIT RUNNING | EM | MOTOR | DI | DOL_DIR
BB1EM654 | _FAULT | BB1EM654_FAULT | <IO NOT ASSIGNED> | Lubrication unit FAULT | LUBRICATION UNIT FAULT |  |  | LUBRICATION UNIT FAULT | EM | MOTOR | DI | DOL_DIR
BB1EM654 | _RUN | BB1EM654_RUN | <IO NOT ASSIGNED> | Lubrication unit RUN | LUBRICATION UNIT RUN |  |  | LUBRICATION UNIT RUN | EM | MOTOR | DO | DOL_DIR
BB1EM654 | _ISOLATOR | BB1EM654_ISOLATOR | <IO NOT ASSIGNED> | Lubrication unit ISOLATOR | LUBRICATION UNIT ISOLATOR |  |  | LUBRICATION UNIT ISOLATOR | EM | MOTOR | DI | DOL_DIR
BB1EM653 | _RUNNING | BB1EM653_RUNNING | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 RUNNING | COOLING FAN FUEL | FEEDING SCREW 1 RUNNING |  | COOLING FAN FUEL FEEDING SCREW 1 RUNNING | EM | MOTOR | DI | DOL_DIR
BB1EM653 | _FAULT | BB1EM653_FAULT | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 FAULT | COOLING FAN FUEL | FEEDING SCREW 1 FAULT |  | COOLING FAN FUEL FEEDING SCREW 1 FAULT | EM | MOTOR | DI | DOL_DIR
BB1EM653 | _RUN | BB1EM653_RUN | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 RUN | COOLING FAN FUEL | FEEDING SCREW 1 RUN |  | COOLING FAN FUEL FEEDING SCREW 1 RUN | EM | MOTOR | DO | DOL_DIR
BB1EM653 | _ISOLATOR | BB1EM653_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 ISOLATOR | COOLING FAN FUEL | FEEDING SCREW 1 ISOLATOR |  | COOLING FAN FUEL FEEDING SCREW 1 ISOLATOR | EM | MOTOR | DI | DOL_DIR
BB1EM655 | _RUNNING | BB1EM655_RUNNING | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 RUNNING | COOLING FAN FUEL | FEEDING SCREW 2 RUNNING |  | COOLING FAN FUEL FEEDING SCREW 2 RUNNING | EM | MOTOR | DI | DOL_DIR
BB1EM655 | _FAULT | BB1EM655_FAULT | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 FAULT | COOLING FAN FUEL | FEEDING SCREW 2 FAULT |  | COOLING FAN FUEL FEEDING SCREW 2 FAULT | EM | MOTOR | DI | DOL_DIR
BB1EM655 | _RUN | BB1EM655_RUN | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 RUN | COOLING FAN FUEL | FEEDING SCREW 2 RUN |  | COOLING FAN FUEL FEEDING SCREW 2 RUN | EM | MOTOR | DO | DOL_DIR
BB1EM655 | _ISOLATOR | BB1EM655_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 ISOLATOR | COOLING FAN FUEL | FEEDING SCREW 2 ISOLATOR |  | COOLING FAN FUEL FEEDING SCREW 2 ISOLATOR | EM | MOTOR | DI | DOL_DIR
BB1EM606 | _ISOLATOR | BB1EM606_ISOLATOR | <IO NOT ASSIGNED> | Dust extraction fan ISOLATOR | DUST EXTRACTION FAN | ISOLATOR |  | DUST EXTRACTION FAN ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EH600 | _ISOLATOR | BB1EH600_ISOLATOR | <IO NOT ASSIGNED> | Electric heater hydraulic unit ISOLATOR | ELECTRIC HEATER | HYDRAULIC UNIT ISOLATOR |  | ELECTRIC HEATER HYDRAULIC UNIT ISOLATOR | EH | HEATER | DI | DOL_DIR_BUS
BB1EM651 | _ISOLATOR | BB1EM651_ISOLATOR | <IO NOT ASSIGNED> | Fuel silo dust filter fanISOLATOR | FUEL SILO DUST FILTER FAN | ISOLATOR |  | FUEL SILO DUST FILTER FAN ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM008 | _ISOLATOR | BB1EM008_ISOLATOR | <IO NOT ASSIGNED> | Conveyor cooling pump ISOLATOR | CONVEYOR COOLING PUMP | ISOLATOR |  | CONVEYOR COOLING PUMP ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM009 | _ISOLATOR | BB1EM009_ISOLATOR | <IO NOT ASSIGNED> | Bottom ash conveyor heat exchanger fan ISOLATOR | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN ISOLAT | OR | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN ISOLAT OR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM408 | _ISOLATOR | BB1EM408_ISOLATOR | <IO NOT ASSIGNED> | Boiler house heater 1 ISOLATOR | BOILER HOUSE HEATER 1 | ISOLATOR |  | BOILER HOUSE HEATER 1 ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM409 | _ISOLATOR | BB1EM409_ISOLATOR | <IO NOT ASSIGNED> | Boiler house heater 2 ISOLATOR | BOILER HOUSE HEATER 2 | ISOLATOR |  | BOILER HOUSE HEATER 2 ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM703 | _RUNNING | BB1EM703_RUNNING | <IO NOT ASSIGNED> | Chemical filling pump 1 RUNNING | CHEMICAL FILLING PUMP 1 | RUNNING |  | CHEMICAL FILLING PUMP 1 RUNNING | EM | MOTOR | DI | DOL_DIRH
BB1EM703 | _FAULT | BB1EM703_FAULT | <IO NOT ASSIGNED> | Chemical filling pump 1 FAULT | CHEMICAL FILLING PUMP 1 | FAULT |  | CHEMICAL FILLING PUMP 1 FAULT | EM | MOTOR | DI | DOL_DIRH
BB1EM703 | _RUN | BB1EM703_RUN | <IO NOT ASSIGNED> | Chemical filling pump 1 RUN | CHEMICAL FILLING PUMP 1 | RUN |  | CHEMICAL FILLING PUMP 1 RUN | EM | MOTOR | DO | DOL_DIRH
BB1EM703 | _LOCAL_MODE | BB1EM703_LOCAL_MODE | <IO NOT ASSIGNED> | Chemical filling pump 1 LOCAL_MODE | CHEMICAL FILLING PUMP 1 | LOCAL_MODE |  | CHEMICAL FILLING PUMP 1 LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH
BB1EM703 | _LOCAL_RUN | BB1EM703_LOCAL_RUN | <IO NOT ASSIGNED> | Chemical filling pump 1 LOCAL_RUN | CHEMICAL FILLING PUMP 1 | LOCAL_RUN |  | CHEMICAL FILLING PUMP 1 LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH
BB1EM703 | _ISOLATOR | BB1EM703_ISOLATOR | <IO NOT ASSIGNED> | Chemical filling pump 1 ISOLATOR | CHEMICAL FILLING PUMP 1 | ISOLATOR |  | CHEMICAL FILLING PUMP 1 ISOLATOR | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _RUNNING | BB1EM704_RUNNING | <IO NOT ASSIGNED> | Chemical filling pump 2 RUNNING | CHEMICAL FILLING PUMP 2 | RUNNING |  | CHEMICAL FILLING PUMP 2 RUNNING | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _FAULT | BB1EM704_FAULT | <IO NOT ASSIGNED> | Chemical filling pump 2 FAULT | CHEMICAL FILLING PUMP 2 | FAULT |  | CHEMICAL FILLING PUMP 2 FAULT | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _RUN | BB1EM704_RUN | <IO NOT ASSIGNED> | Chemical filling pump 2 RUN | CHEMICAL FILLING PUMP 2 | RUN |  | CHEMICAL FILLING PUMP 2 RUN | EM | MOTOR | DO | DOL_DIRH
BB1EM704 | _LOCAL_MODE | BB1EM704_LOCAL_MODE | <IO NOT ASSIGNED> | Chemical filling pump 2 LOCAL_MODE | CHEMICAL FILLING PUMP 2 | LOCAL_MODE |  | CHEMICAL FILLING PUMP 2 LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _LOCAL_RUN | BB1EM704_LOCAL_RUN | <IO NOT ASSIGNED> | Chemical filling pump 2 LOCAL_RUN | CHEMICAL FILLING PUMP 2 | LOCAL_RUN |  | CHEMICAL FILLING PUMP 2 LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _ISOLATOR | BB1EM704_ISOLATOR | <IO NOT ASSIGNED> | Chemical filling pump 2 ISOLATOR | CHEMICAL FILLING PUMP 2 | ISOLATOR |  | CHEMICAL FILLING PUMP 2 ISOLATOR | EM | MOTOR | DI | DOL_DIRH
BB1EM670 | _LOCAL_MODE | BB1EM670_LOCAL_MODE | <IO NOT ASSIGNED> | Belt magnet LOCAL_MODE | BELT MAGNET LOCAL_MODE |  |  | BELT MAGNET LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM670 | _LOCAL_RUN | BB1EM670_LOCAL_RUN | <IO NOT ASSIGNED> | Belt magnet LOCAL_RUN | BELT MAGNET LOCAL_RUN |  |  | BELT MAGNET LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM670 | _ISOLATOR | BB1EM670_ISOLATOR | <IO NOT ASSIGNED> | Belt magnet ISOLATOR | BELT MAGNET ISOLATOR |  |  | BELT MAGNET ISOLATOR | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _LOCAL_MODE | BB1EM652_LOCAL_MODE | <IO NOT ASSIGNED> | Rotating fuel spreader LOCAL_MODE | ROTATING FUEL SPREADER | LOCAL_MODE |  | ROTATING FUEL SPREADER LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _LOCAL_RUN | BB1EM652_LOCAL_RUN | <IO NOT ASSIGNED> | Rotating fuel spreader LOCAL_RUN | ROTATING FUEL SPREADER | LOCAL_RUN |  | ROTATING FUEL SPREADER LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _ISOLATOR | BB1EM652_ISOLATOR | <IO NOT ASSIGNED> | Rotating fuel spreader ISOLATOR | ROTATING FUEL SPREADER | ISOLATOR |  | ROTATING FUEL SPREADER ISOLATOR | EM | MOTOR | DI | DOL_DIRH_BUS
BB1BL200 | _ISOLATOR | BB1BL200_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 1 ISOLATOR | SOOTBLOWER 1 ISOLATOR |  |  | SOOTBLOWER 1 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL201 | _ISOLATOR | BB1BL201_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 2 ISOLATOR | SOOTBLOWER 2 ISOLATOR |  |  | SOOTBLOWER 2 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL202 | _ISOLATOR | BB1BL202_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 3 ISOLATOR | SOOTBLOWER 3 ISOLATOR |  |  | SOOTBLOWER 3 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL203 | _ISOLATOR | BB1BL203_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 4 ISOLATOR | SOOTBLOWER 4 ISOLATOR |  |  | SOOTBLOWER 4 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL204 | _ISOLATOR | BB1BL204_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 5 ISOLATOR | SOOTBLOWER 5 ISOLATOR |  |  | SOOTBLOWER 5 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL205 | _ISOLATOR | BB1BL205_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 6 ISOLATOR | SOOTBLOWER 6 ISOLATOR |  |  | SOOTBLOWER 6 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL206 | _ISOLATOR | BB1BL206_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 7 ISOLATOR | SOOTBLOWER 7 ISOLATOR |  |  | SOOTBLOWER 7 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1EM815 | _ISOLATOR | BB1EM815_ISOLATOR | <IO NOT ASSIGNED> | Fly ash container screw ISOLATOR | FLY ASH CONTAINER SCREW I | SOLATOR |  | FLY ASH CONTAINER SCREW I SOLATOR | EM | MOTOR | DI | DOL_REV_BUS
BB1EM855 | _ISOLATOR | BB1EM855_ISOLATOR | <IO NOT ASSIGNED> | Ash container screw ISOLATOR | ASH CONTAINER SCREW ISOLA | TOR |  | ASH CONTAINER SCREW ISOLA TOR | EM | MOTOR | DI | DOL_REV_BUS
BB1EM401 | _ISOLATOR | BB1EM401_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 1 ISOLATOR | EXHAUST FAN 1 ISOLATOR |  |  | EXHAUST FAN 1 ISOLATOR | EM | MOTOR | DI | FRQ_DIR
BB1EM402 |  | BB1EM402 | <IO NOT ASSIGNED> | Exhaust fan 2 | EXHAUST FAN 2 |  |  | EXHAUST FAN 2 | EM | MOTOR | DO | COMPR
BB1EM402 | _ISOLATOR | BB1EM402_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 2 ISOLATOR | EXHAUST FAN 2 ISOLATOR |  |  | EXHAUST FAN 2 ISOLATOR | EM | MOTOR | DO | COMPR
BB1EM403 |  | BB1EM403 | <IO NOT ASSIGNED> | Exhaust fan 3 | EXHAUST FAN 3 |  |  | EXHAUST FAN 3 | EM | MOTOR | DO | COMPR
BB1EM403 | _ISOLATOR | BB1EM403_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 3 ISOLATOR | EXHAUST FAN 3 ISOLATOR |  |  | EXHAUST FAN 3 ISOLATOR | EM | MOTOR | DO | COMPR
BB1EM673 | _LOCAL_MODE | BB1EM673_LOCAL_MODE | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_MODE | LEVELLING ROLLER 1 | LOCAL_MODE |  | LEVELLING ROLLER 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _LOCAL_RUN_FWD | BB1EM673_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_RUN_FWD | LEVELLING ROLLER 1 | LOCAL_RUN_FWD |  | LEVELLING ROLLER 1 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _LOCAL_RUN_REV | BB1EM673_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_RUN_REV | LEVELLING ROLLER 1 | LOCAL_RUN_REV |  | LEVELLING ROLLER 1 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _ISOLATOR | BB1EM673_ISOLATOR | <IO NOT ASSIGNED> | Levelling roller 1 ISOLATOR | LEVELLING ROLLER 1 | ISOLATOR |  | LEVELLING ROLLER 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_MODE | BB1EM674_LOCAL_MODE | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_MODE | LEVELLING ROLLER 2 | LOCAL_MODE |  | LEVELLING ROLLER 2 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_RUN_FWD | BB1EM674_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_RUN_FWD | LEVELLING ROLLER 2 | LOCAL_RUN_FWD |  | LEVELLING ROLLER 2 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_RUN_REV | BB1EM674_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_RUN_REV | LEVELLING ROLLER 2 | LOCAL_RUN_REV |  | LEVELLING ROLLER 2 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _ISOLATOR | BB1EM674_ISOLATOR | <IO NOT ASSIGNED> | Levelling roller 2 ISOLATOR | LEVELLING ROLLER 2 | ISOLATOR |  | LEVELLING ROLLER 2 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_MODE | BB1EM601_LOCAL_MODE | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_MODE | DUST EXTRACTION | ROTARY FEEDER LOCAL_MODE |  | DUST EXTRACTION ROTARY FEEDER LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_RUN_FWD | BB1EM601_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_RUN_FWD | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_F | WD | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_F WD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_RUN_REV | BB1EM601_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_RUN_REV | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_R | EV | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_R EV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _ISOLATOR | BB1EM601_ISOLATOR | <IO NOT ASSIGNED> | Dust extraction rotary feeder ISOLATOR | DUST EXTRACTION | ROTARY FEEDER ISOLATOR |  | DUST EXTRACTION ROTARY FEEDER ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_MODE | BB1IV650_LOCAL_MODE | <IO NOT ASSIGNED> | Slide gate valve LOCAL_MODE | SLIDE GATE VALVE | LOCAL_MODE |  | SLIDE GATE VALVE LOCAL_MODE | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_RUN_FWD | BB1IV650_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Slide gate valve LOCAL_RUN_FWD | SLIDE GATE VALVE | LOCAL_RUN_FWD |  | SLIDE GATE VALVE LOCAL_RUN_FWD | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_RUN_REV | BB1IV650_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Slide gate valve LOCAL_RUN_REV | SLIDE GATE VALVE | LOCAL_RUN_REV |  | SLIDE GATE VALVE LOCAL_RUN_REV | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _ISOLATOR | BB1IV650_ISOLATOR | <IO NOT ASSIGNED> | Slide gate valve ISOLATOR | SLIDE GATE VALVE | ISOLATOR |  | SLIDE GATE VALVE ISOLATOR | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_MODE | BB1EM657_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 1 LOCAL_MODE |  | FUEL FEEDING ROTARY VALVE 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_RUN_FWD | BB1EM657_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | FWD | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_RUN_REV | BB1EM657_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_RUN_REV | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | REV | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _ISOLATOR | BB1EM657_ISOLATOR | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 ISOLATOR | FUEL FEEDING | ROTARY VALVE 1 ISOLATOR |  | FUEL FEEDING ROTARY VALVE 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_MODE | BB1EM656_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 2 LOCAL_MODE |  | FUEL FEEDING ROTARY VALVE 2 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_RUN_FWD | BB1EM656_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | FWD | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_RUN_REV | BB1EM656_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_RUN_REV | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | REV | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _ISOLATOR | BB1EM656_ISOLATOR | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 ISOLATOR | FUEL FEEDING | ROTARY VALVE 2 ISOLATOR |  | FUEL FEEDING ROTARY VALVE 2 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_MODE | BB1EM856_LOCAL_MODE | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_MODE | PURIFIED SAND | SCREW CONVEYOR LOCAL_MODE |  | PURIFIED SAND SCREW CONVEYOR LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_RUN_FWD | BB1EM856_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_RUN_FWD | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | FWD | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_RUN_REV | BB1EM856_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_RUN_REV | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | REV | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _ISOLATOR | BB1EM856_ISOLATOR | <IO NOT ASSIGNED> | Purified sand screw conveyor ISOLATOR | PURIFIED SAND | SCREW CONVEYOR ISOLATOR |  | PURIFIED SAND SCREW CONVEYOR ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_MODE | BB1EM850_LOCAL_MODE | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_MODE | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  | 2ND PASS FLY ASH ROTARY VALVE LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_RUN_FWD | BB1EM850_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_RUN_ FWD | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_RUN_REV | BB1EM850_LOCAL_RUN_REV | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_RUN_ REV | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | REV | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _ISOLATOR | BB1EM850_ISOLATOR | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve ISOLATOR | 2ND PASS FLY ASH | ROTARY VALVE ISOLATOR |  | 2ND PASS FLY ASH ROTARY VALVE ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_MODE | BB1EM851_LOCAL_MODE | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_MODE | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  | 3RD PASS FLY ASH ROTARY VALVE LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_RUN_FWD | BB1EM851_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_RUN_ FWD | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_RUN_REV | BB1EM851_LOCAL_RUN_REV | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_RUN_ REV | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | REV | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _ISOLATOR | BB1EM851_ISOLATOR | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve ISOLATOR | 3RD PASS FLY ASH | ROTARY VALVE ISOLATOR |  | 3RD PASS FLY ASH ROTARY VALVE ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
|  | <BB1TX001> | <IO NOT ASSIGNED> | BIOMASS BOILER SITE TRANSFORMER | BIOMASS BOILER | SITE TRANSFORMER |  | BIOMASS BOILER SITE TRANSFORMER |  | 0 |  | #N/A
|  | <BB1SA001> | <IO NOT ASSIGNED> | SUREGE ARRESTOR | SUREGE ARRESTOR |  |  | SUREGE ARRESTOR |  | 0 |  | #N/A

## C_CABLE
Cables
_Tag | CableName1 | CableName2 | CableName3 | Notes | CableName4
<004> | <004>/01 | <004>/02 | <004>/03
BB1FS003 | BB1FS003/01 | BB1FS003/02 | BB1FS003/03
BB1GS001 | BB1GS001/01 | BB1GS001/02 | BB1GS001/03
BB1GS002 | BB1GS002/01 | BB1GS002/02 | BB1GS002/03
BB1GS003 | BB1GS003/01 | BB1GS003/02 | BB1GS003/03
BB1GS004 | BB1GS004/01 | BB1GS004/02 | BB1GS004/03
BB1GS005 | BB1GS005/01 | BB1GS005/02 | BB1GS005/03
BB1GS006 | BB1GS006/01 | BB1GS006/02 | BB1GS006/03
BB1GS007 | BB1GS007/01 | BB1GS007/02 | BB1GS007/03
BB1GS008 | BB1GS008/01 | BB1GS008/02 | BB1GS008/03
BB1GS009 | BB1GS009/01 | BB1GS009/02 | BB1GS009/03
BB1GS010 | BB1GS010/01 | BB1GS010/02 | BB1GS010/03
BB1GS011 | BB1GS011/01 | BB1GS011/02 | BB1GS011/03
BB1GS012 | BB1GS012/01 | BB1GS012/02 | BB1GS012/03
BB1GS020 | BB1GS020/01 | BB1GS020/02 | BB1GS020/03
BB1GS200 | BB1GS200/01 | BB1GS200/02 | BB1GS200/03
BB1GS201 | BB1GS201/01 | BB1GS201/02 | BB1GS201/03
BB1GS203 | BB1GS203/01 | BB1GS203/02 | BB1GS203/03
BB1GS204 | BB1GS204/01 | BB1GS204/02 | BB1GS204/03
BB1GS205 | BB1GS205/01 | BB1GS205/02 | BB1GS205/03
BB1GS206 | BB1GS206/01 | BB1GS206/02 | BB1GS206/03
BB1GS207 | BB1GS207/01 | BB1GS207/02 | BB1GS207/03
BB1GS208 | BB1GS208/01 | BB1GS208/02 | BB1GS208/03
BB1GS209 | BB1GS209/01 | BB1GS209/02 | BB1GS209/03
BB1GS210 | BB1GS210/01 | BB1GS210/02 | BB1GS210/03
BB1GS211 | BB1GS211/01 | BB1GS211/02 | BB1GS211/03
BB1GS212 | BB1GS212/01 | BB1GS212/02 | BB1GS212/03
BB1GS213 | BB1GS213/01 | BB1GS213/02 | BB1GS213/03
BB1GS214 | BB1GS214/01 | BB1GS214/02 | BB1GS214/03
BB1GS215 | BB1GS215/01 | BB1GS215/02 | BB1GS215/03
BB1GS216 | BB1GS216/01 | BB1GS216/02 | BB1GS216/03
BB1GS217 | BB1GS217/01 | BB1GS217/02 | BB1GS217/03
BB1GS218 | BB1GS218/01 | BB1GS218/02 | BB1GS218/03
BB1GS219 | BB1GS219/01 | BB1GS219/02 | BB1GS219/03
BB1GS220 | BB1GS220/01 | BB1GS220/02 | BB1GS220/03
BB1GS221 | BB1GS221/01 | BB1GS221/02 | BB1GS221/03
BB1GS222 | BB1GS222/01 | BB1GS222/02 | BB1GS222/03
BB1GS223 | BB1GS223/01 | BB1GS223/02 | BB1GS223/03
BB1GS224 | BB1GS224/01 | BB1GS224/02 | BB1GS224/03
BB1GS225 | BB1GS225/01 | BB1GS225/02 | BB1GS225/03
BB1GS226 | BB1GS226/01 | BB1GS226/02 | BB1GS226/03
BB1GS227 | BB1GS227/01 | BB1GS227/02 | BB1GS227/03
BB1GS228 | BB1GS228/01 | BB1GS228/02 | BB1GS228/03
BB1GS230 | BB1GS230/01 | BB1GS230/02 | BB1GS230/03
BB1GS231 | BB1GS231/01 | BB1GS231/02 | BB1GS231/03
BB1GS232 | BB1GS232/01 | BB1GS232/02 | BB1GS232/03
BB1GS233 | BB1GS233/01 | BB1GS233/02 | BB1GS233/03
BB1GS600 | BB1GS600/01 | BB1GS600/02 | BB1GS600/03
BB1GS601 | BB1GS601/01 | BB1GS601/02 | BB1GS601/03
BB1GS602 | BB1GS602/01 | BB1GS602/02 | BB1GS602/03
BB1GS603 | BB1GS603/01 | BB1GS603/02 | BB1GS603/03
BB1GS604 | BB1GS604/01 | BB1GS604/02 | BB1GS604/03
BB1GS605 | BB1GS605/01 | BB1GS605/02 | BB1GS605/03
BB1GS606 | BB1GS606/01 | BB1GS606/02 | BB1GS606/03
BB1GS607 | BB1GS607/01 | BB1GS607/02 | BB1GS607/03
BB1GS608 | BB1GS608/01 | BB1GS608/02 | BB1GS608/03
BB1GS609 | BB1GS609/01 | BB1GS609/02 | BB1GS609/03
BB1GS610 | BB1GS610/01 | BB1GS610/02 | BB1GS610/03
BB1GS611 | BB1GS611/01 | BB1GS611/02 | BB1GS611/03
BB1GS612 | BB1GS612/01 | BB1GS612/02 | BB1GS612/03
BB1GS613 | BB1GS613/01 | BB1GS613/02 | BB1GS613/03
BB1GS614 | BB1GS614/01 | BB1GS614/02 | BB1GS614/03
BB1GS615 | BB1GS615/01 | BB1GS615/02 | BB1GS615/03
BB1GS616 | BB1GS616/01 | BB1GS616/02 | BB1GS616/03
BB1GS617 | BB1GS617/01 | BB1GS617/02 | BB1GS617/03
BB1GS618 | BB1GS618/01 | BB1GS618/02 | BB1GS618/03
BB1GS619 | BB1GS619/01 | BB1GS619/02 | BB1GS619/03
BB1GS620 | BB1GS620/01 | BB1GS620/02 | BB1GS620/03
BB1GS621 | BB1GS621/01 | BB1GS621/02 | BB1GS621/03
BB1GS622 | BB1GS622/01 | BB1GS622/02 | BB1GS622/03
BB1GS623 | BB1GS623/01 | BB1GS623/02 | BB1GS623/03
BB1GS650 | BB1GS650/01 | BB1GS650/02 | BB1GS650/03
BB1GS651 | BB1GS651/01 | BB1GS651/02 | BB1GS651/03
BB1GS652 | BB1GS652/01 | BB1GS652/02 | BB1GS652/03
BB1GS653 | BB1GS653/01 | BB1GS653/02 | BB1GS653/03
BB1GS654 | BB1GS654/01 | BB1GS654/02 | BB1GS654/03
BB1GS655 | BB1GS655/01 | BB1GS655/02 | BB1GS655/03
BB1GS656 | BB1GS656/01 | BB1GS656/02 | BB1GS656/03
BB1GS659 | BB1GS659/01 | BB1GS659/02 | BB1GS659/03
BB1GS660 | BB1GS660/01 | BB1GS660/02 | BB1GS660/03
BB1GS661 | BB1GS661/01 | BB1GS661/02 | BB1GS661/03
BB1GS662 | BB1GS662/01 | BB1GS662/02 | BB1GS662/03
BB1GS663 | BB1GS663/01 | BB1GS663/02 | BB1GS663/03
BB1GS800 | BB1GS800/01 | BB1GS800/02 | BB1GS800/03
BB1GS801 | BB1GS801/01 | BB1GS801/02 | BB1GS801/03
BB1GS802 | BB1GS802/01 | BB1GS802/02 | BB1GS802/03
BB1GS803 | BB1GS803/01 | BB1GS803/02 | BB1GS803/03
BB1GS850 | BB1GS850/01 | BB1GS850/02 | BB1GS850/03
BB1GS851 | BB1GS851/01 | BB1GS851/02 | BB1GS851/03
BB1GS852 | BB1GS852/01 | BB1GS852/02 | BB1GS852/03
BB1GS853 | BB1GS853/01 | BB1GS853/02 | BB1GS853/03
BB1GS854 | BB1GS854/01 | BB1GS854/02 | BB1GS854/03
BB1GS855 | BB1GS855/01 | BB1GS855/02 | BB1GS855/03
BB1GS856 | BB1GS856/01 | BB1GS856/02 | BB1GS856/03
BB1GS857 | BB1GS857/01 | BB1GS857/02 | BB1GS857/03
BB1GS858 | BB1GS858/01 | BB1GS858/02 | BB1GS858/03
BB1LS600 | BB1LS600/01 | BB1LS600/02 | BB1LS600/03
BB1LS608 | BB1LS608/01 | BB1LS608/02 | BB1LS608/03
BB1LS650 | BB1LS650/01 | BB1LS650/02 | BB1LS650/03
BB1LS651 | BB1LS651/01 | BB1LS651/02 | BB1LS651/03
BB1LS652 | BB1LS652/01 | BB1LS652/02 | BB1LS652/03
BB1LS653 | BB1LS653/01 | BB1LS653/02 | BB1LS653/03
BB1LS654 | BB1LS654/01 | BB1LS654/02 | BB1LS654/03
BB1LS655 | BB1LS655/01 | BB1LS655/02 | BB1LS655/03
BB1LS656 | BB1LS656/01 | BB1LS656/02 | BB1LS656/03
BB1LS657 | BB1LS657/01 | BB1LS657/02 | BB1LS657/03
BB1LS658 | BB1LS658/01 | BB1LS658/02 | BB1LS658/03
BB1LS659 | BB1LS659/01 | BB1LS659/02 | BB1LS659/03
BB1LS660 | BB1LS660/01 | BB1LS660/02 | BB1LS660/03
BB1LS661 | BB1LS661/01 | BB1LS661/02 | BB1LS661/03
BB1LS700 | BB1LS700/01 | BB1LS700/02 | BB1LS700/03
BB1LS701 | BB1LS701/01 | BB1LS701/02 | BB1LS701/03
BB1LS850 | BB1LS850/01 | BB1LS850/02 | BB1LS850/03
BB1LS851 | BB1LS851/01 | BB1LS851/02 | BB1LS851/03
BB1PS600 | BB1PS600/01 | BB1PS600/02 | BB1PS600/03
BB1PS601 | BB1PS601/01 | BB1PS601/02 | BB1PS601/03
BB1PS602 | BB1PS602/01 | BB1PS602/02 | BB1PS602/03
BB1PS603 | BB1PS603/01 | BB1PS603/02 | BB1PS603/03
BB1PS604 | BB1PS604/01 | BB1PS604/02 | BB1PS604/03
BB1PS605 | BB1PS605/01 | BB1PS605/02 | BB1PS605/03
BB1ST649 | BB1ST649/01 | BB1ST649/02 | BB1ST649/03
BB1ST650 | BB1ST650/01 | BB1ST650/02 | BB1ST650/03
BB1ST651 | BB1ST651/01 | BB1ST651/02 | BB1ST651/03
BB1ST652 | BB1ST652/01 | BB1ST652/02 | BB1ST652/03
BB1ST653 | BB1ST653/01 | BB1ST653/02 | BB1ST653/03
BB1ST654 | BB1ST654/01 | BB1ST654/02 | BB1ST654/03
BB1ST655 | BB1ST655/01 | BB1ST655/02 | BB1ST655/03
BB1ST656 | BB1ST656/01 | BB1ST656/02 | BB1ST656/03
BB1ST657 | BB1ST657/01 | BB1ST657/02 | BB1ST657/03
BB1ST659 | BB1ST659/01 | BB1ST659/02 | BB1ST659/03
BB1ST673 | BB1ST673/01 | BB1ST673/02 | BB1ST673/03
BB1ST674 | BB1ST674/01 | BB1ST674/02 | BB1ST674/03
BB1ST675 | BB1ST675/01 | BB1ST675/02 | BB1ST675/03
BB1ST850 | BB1ST850/01 | BB1ST850/02 | BB1ST850/03
BB1ST852 | BB1ST852/01 | BB1ST852/02 | BB1ST852/03
BB1ST853 | BB1ST853/01 | BB1ST853/02 | BB1ST853/03
BB1ST856 | BB1ST856/01 | BB1ST856/02 | BB1ST856/03
BB1TS600 | BB1TS600/01 | BB1TS600/02 | BB1TS600/03
BB1TS608 | BB1TS608/01 | BB1TS608/02 | BB1TS608/03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
| 01 | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03
|  | 02 | 03

## _LookupTables
Code | Type
IL | ALARM |  | Channel | IOTerminal | Type | CatN | CatD2 | CatD | ChannelIndex | LoopNameA | LoopTerminalA | LoopNameB | LoopTerminalB | GndName | GndTerminal | MaxIndex | T1 | T2 | T3 | T1Type | T2Type | T3Type
IJ | ALARM |  | 0 | 0 | DI | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D | 0 | V+ | 1 | [5 empty] | V+ | 0 |  | 24VDC | DI
EM | MOTOR |  | 1 | 2 | DI | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D | 1 | V+ | 3 | [5 empty] | V+ | 1 |  | 24VDC | DI
GS | GATE SWITCH |  | 2 | 4 | DI | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D | 2 | V+ | 5 | [5 empty] | V+ | 2 |  | 24VDC | DI
SV | SOLENOID VALVE |  | 3 | 6 | DI | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D | 3 | V+ | 7 |  |  |  |  | TRUE | V+ | 3 |  | 24VDC | DI
IV | ISOLATING VALVE |  | 0 | 0 | DO | 1734-OB4E*M1 | Digital Output 1 (00,06) | 1734-OB4E | 0 | V- | 4 | [5 empty] | 0 | V- |  | DO | 0VDC
CV | CONTROL VALVE |  | 1 | 1 | DO | 1734-OB4E*M2 | Digital Output 2 (01,07) | 1734-OB4E | 1 | V- | 5 | [5 empty] | 1 | V- |  | DO | 0VDC
BU | BURNER |  | 2 | 2 | DO | 1734-OB4E*M3 | Digital Output 3 (02,04) | 1734-OB4E | 2 | V- | 6 | [5 empty] | 2 | V- |  | DO | 0VDC
PU | PUMP |  | 3 | 3 | DO | 1734-OB4E*M4 | Digital Output 4 (03,05) | 1734-OB4E | 3 | V- | 7 |  |  |  |  | TRUE | 3 | V- |  | DO | 0VDC
DM | DAMPER |  | 0 | 0 | AI | 1734-IE8C#MOP-8AI*M1 | Analog Input 1 (0.24,I0,0.SHD) | 1734-IE8C | 0 | [7 empty] | 0 |  |  | AI
PT | PRESSURE TRANSMITTER |  | 1 | 1 | AI | 1734-IE8C#MOP-8AI*M2 | Analog Input 2 (1.24,I1,1.SHD) | 1734-IE8C | 1 | [7 empty] | 1 |  |  | AI
LT | LEVEL TRANSMITTER |  | 2 | 2 | AI | 1734-IE8C#MOP-8AI*M3 | Analog Input 3 (2.24,I2,2.SHD) | 1734-IE8C | 2 | [7 empty] | 2 |  |  | AI
FT | FLOW TRANSMITTER |  | 3 | 3 | AI | 1734-IE8C#MOP-8AI*M4 | Analog Input 4 (3.24,I3,3.SHD) | 1734-IE8C | 3 | [7 empty] | 3 |  |  | AI
TT | TEMPERATURE TRANSMITTER |  | 4 | 4 | AI | 1734-IE8C#MOP-8AI*M5 | Analog Input 5 (4.24,I4,4.SHD) | 1734-IE8C | 4 | [7 empty] | 4 |  |  | AI
QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | 5 | 5 | AI | 1734-IE8C#MOP-8AI*M6 | Analog Input 6 (5.24,I5,5.SHD) | 1734-IE8C | 5 | [7 empty] | 5 |  |  | AI
TS | TEMPERATURE SWITCH |  | 6 | 6 | AI | 1734-IE8C#MOP-8AI*M7 | Analog Input 7 (6.24,I6,6.0) | 1734-IE8C | 6 | [7 empty] | 6 |  |  | AI
LS | LEVEL SWITCH |  | 7 | 7 | AI | 1734-IE8C#MOP-8AI*M8 | Analog Input 8 (7.24,I7,7.SHD) | 1734-IE8C | 7 | [6 empty] | TRUE | 7 |  |  | AI
PS | PRESSURE SWITCH |  | 0 | 0 | AO | 1734-OE2C*M1 | Analog Output 1 (00,04,02) | 1734-OE2C | 0 | V- | 4 | V+ | 6 | SH | 2 |  | 0 | V- | V+ | AO | 0VDC | 24VDC
ST | SPEED SWITCH/ROTATION GUARD |  | 1 | 1 | AO | 1734-OE2C*M2 | Analog Output 2 (01,05,03) | 1734-OE2C | 1 | V- | 5 | V+ | 7 | SH | 3 | TRUE | 1 | V- | V+ | AO | 0VDC | 24VDC
FS | FLOW SWITCH
HS | EMERGENCY STOP
FM | MOTOR
FL | FILTER
EH | HEATER
DR | DRYER
CP | CONTROL PANEL?
FG | ESP
SI | SAFETY INTERLOCK
BL | BLOWER
Type | CatD | ShortCat
DI | 1734-IB4D | IB4D
DO | 1734-OB4E | OB4E
AI | 1734-IE8C | IE8C
AO | 1734-OE2C | OE2C

## prototype V6 spec
Object Name
objPrefix | objIndex | Column1 | objDesc |  | prefix | index | seperator | attribute | suffix | delimiter | result
P | 0 |  | numbered PLC IO block placeholder |  | P | 1 | _ | NAME |  |  | P1_NAME
D | 0 |  | numbered Device block placeholder |  | D | 1
C | 0 |  | numbered Cable block placeholder |  | C | 1
X | 0 |  | numbered PANEL block place holder |  | X | 1 |  | XIO | TI | _
VS | 0 |  | numbered VSD block placeholder |  | VS | 1
SS | 0 |  | numbered Soft Starter block placeholder |  | SS | 1
IS | 0 |  | numbered ISOLATOR block placeholder |  | IS | 1
Q | 0 |  | numbered PROTECTION block placeholder |  | Q | 1
W |  |  | WIRE
M | 0 |  | numbered MOTOR block placeholder |  | M | 1
Object Attribute |  |  |  | len
Column1 | Column2 | Column3 | Column4 | 4
NAME |  | NAME |  | 4
SLOT |  | SLOT |  | 4 | DRAWING
CHAN |  | CHAN |  | 3 | PROTOTYPE
TAG |  | TAG |  | 5 | X1_PNL
DESC2 |  | DESC2 |  | 5 | X1_PDESC
DESC3 |  | DESC3 |  | 5 | X1_24DC
DESC4 |  | DESC4 |  | 3 | X1_0DC
TAG |  | TAG | 0 | 3 | X1_24ACL
PNL |  | PNL |  | 3 | X1_24ACN
MFG |  | MFG |  | 4 | X1_230ACL1
CATN |  | CATN |  | 4 | X1_230ACN
CATD |  | CATD |  | 3 | X1_XIO
XIO |  | XIO | 0 | 6 | X1_XIO_TI
XIO | TI | XIO_TI |  | 6 | X1_XIO_FI
XIO | FI | XIO_FI |  | 6 | X1_XIO_KI
XIO | KI | XIO_KI |  | 3 | X1_XDB
XDB |  | XDB |  | 6 | X1_XDB_TI
XDB | TI | XDB_TI |  | 6 | X1_XDB_FI
XDB | FI | XDB_FI |  | 6 | X1_XDB_KI
XDB | KI | XDB_KI |  | 6 | X2_PNL
XDB | QI | XDB_QI |  | 5 | X2_PDESC
24VDC |  | 24VDC |  | 4 | X2_24DC
0VDC |  | 0VDC |  | 5 | X2_0DC
24VAC |  | 24VAC |  | 7 | X2_24ACL
24VAC | N | 24VAC_N |  | 7 | X2_24ACN
230V | L1 | 230V_L1 |  | 7 | X2_230ACL1
230V | L2 | 230V_L2 |  | 7 | X2_230ACN
230V | L3 | 230V_L3 |  | 6 | X2_XIO
230V | N | 230V_N |  | #REF! | X2_XIO_TI
TYPE |  | TYPE |  | 4 | X2_XIO_FI
|  |  |  | 0 | X2_XIO_KI
|  |  |  | 0 | X2_XDB
DWG | PREFIX | DWG_PREFIX |  | 10 | X2_XDB_TI
DWG | NUMBER | DWG_NUMBER |  | 10 | X2_XDB_FI
DRAWING |  | DRAWING |  | 7 | X2_XDB_KI
PROTOTYPE |  | PROTOTYPE |  | 9 | P1_NAME
CABLE | TYPE | CABLE_TYPE |  | 10 | P1_RACK
CABLE | DESC | CABLE_DESC |  | 10 | P1_SLOT
|  | 0 |  | 1 | P1_CHAN
|  | 0 |  | 1 | P1_MFG
SET_TO |  | SET_TO |  | 6 | P1_CATN
KW |  | KW |  | 2 | P1_CATD
AMPS |  | AMPS |  | 4 | P1_TAG
VOLTS |  | VOLTS |  | 5 | P1_DESC2
|  |  |  | 0 | P1_DESC3
P1_DESC4
Generic Power Cable Spec |  |  |  |  | P1_T1
VoltageRating | insulation | Cores | Size | Column1 | P1_T2
300/500 | PVC | 1 | 1.5 | Neutral-Screen | P2_NAME
0.6/1kV | XPLE | 36 |  | VSD | P2_RACK
|  |  |  | SWA | P2_SLOT
|  |  |  | FLEX | P2_CHAN
P2_MFG
P2_CATN
P2_CATD
P2_TAG
PVC | P |  |  |  | P2_DESC2
XPLE | X |  |  |  | P2_DESC3
Neutral Screen | NS |  |  |  | P2_DESC4
Steel-Wire-Armour | S |  |  |  | P2_T1
Flex | F |  |  |  | D1_TAG
Marine | M |  |  |  | D1_DESC2
D1_DESC3
Seperator: | - |  |  |  | D1_DESC4
D1_VDESC
VoltageRating | Examples | Description | NOTES |  | D1_TYPE
0 | 120V RMS | Instrumentation/Comms cables. Use for Extra Low Voltage Only |  |  | D1_T1
1 | 300/500 0.6/1kV | Suitible for general 230/400V applications |  |  | D1_T2
2 | >1kV | MV,HV Cables |  |  | D2_TAG
D2_DESC2
Insulation | Examples | Description | NOTES |  | D2_DESC3
P | TPS, R75 | General purpose cable. 75deg max |  |  | D2_DESC4
X | XPLE, R90 | Suitible for general 230/400V applications |  |  | D2_VDESC
X+ |  | Hi temp cable suitible for eg. 120, 150 degrees |  |  | D2_TYPE
D2_T1
D2_T2
Cores | Examples | Description | NOTES |  | C1_MFG
[n]C |  | Number of cores |  |  | C1_CATN
[n]PR |  | Number of Pairs |  |  | C1_CATD
+E |  | plus earth |  |  | C1_TAG
C1_COR1
Properties | Examples | Description | NOTES |  | C1_COR2
V |  | VSD Cable | Can include any number of entries. Can be ommited if not applicible |  | C2_MFG
N |  | Neutral-Screen |  |  | C2_CATN
A |  | Steel-Wire Armour |  |  | C2_CATD
F |  | Flexible |  |  | C2_TAG
M |  | Marine Rated |  |  | C2_COR1
T |  | Twisted-Pair? |  |  | C2_COR2
S |  | Shielded?
Examples
| 0P-3PR-S-1.5 | Instrumentation PVC 3 Pair shielded cable, 1.5mm^2
| 2X-3C+E-VF-35 | Power XPLE 3C+E Flexible VSD cable, 35mm

## MSIO
[10 empty] | MSIO-list | [26 empty] | Date |  | Name |  |  |  | Remarks | [23 empty] | New data with green | Changes with yellow |  | Revision
Revision 3
| Basic information | [8 empty] | Motor | [8 empty] | Supply | [7 empty] | I/O | [9 empty] | Scale |  |  | PLC I/O ( Process) |  |  |  | SIS I/O (Safety) |  |  |  | Bus I/O - Register |  |  |  | Alarm threshold |  |  |  | Instrument |  |  |  | Device |  |  | Supplier | Documentation |  |  | Location |  | Revision
Adresses
Row index | Area | Process | Device | Equipment | TAG | Description | Description 2. language | Short Description (n char) | Column1 | Power (kW) | Current (A) | Speed (rpm) | Voltage (V) | Cos φ | Thermistor | ATEX | Column2 | Column3 | Electrical center | Cubicle | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Signal suffix | W | Signal TAG | Column10 | Column11 | Rack | Slot | Chan. | Addr. | Term. | Min | Max | Unit | DI | DO | AI | AO | SDI | SDO | SAI | SAO | BDI | BDO | BAI | BAO | LL | L | H | HH | Transmitter type | Type of signal | Switch state | Voltage | Manufacturer | Model | Connection | Name | P&ID | Typical | Hook-up | Electrical room | Cabinet | Remarks | Issue
0 |  | BB1 | EM | 001 | BB1EM001 | Feed water pump 1 |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Sulzer/ABB | 4001 | FRQ_DIR |  |  |  | Tag changed | 3
1 | [27 empty] | Running | BB1PU001 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
2 | [27 empty] | MCC Fault | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
3 | [27 empty] | Safety switch | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
4 | [27 empty] | VFD Alarm | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
5 | [27 empty] | Run command | BB1PU001 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
6 | [27 empty] | Current | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
7 | [27 empty] | Speed reference | BB1PU001 | [21 empty] | X | [13 empty] | FRQ_DIR
8 | [27 empty] | Actual speed | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
9 | [27 empty] | Torque | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
10 | [27 empty] | RPM | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
11 |  | BB1 | EM | 002 | BB1EM002 | Feed water pump 2 |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Sulzer/ABB | 4001 | FRQ_DIR |  |  |  | Tag changed | 3
12 | [27 empty] | Running | BB1PU002 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
13 | [27 empty] | MCC Fault | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
14 | [27 empty] | Safety switch | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
15 | [27 empty] | VFD Alarm | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
16 | [27 empty] | Run command | BB1PU002 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
17 | [27 empty] | Current | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
18 | [27 empty] | Speed reference | BB1PU002 | [21 empty] | X | [13 empty] | FRQ_DIR
19 | [27 empty] | Actual speed | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
20 | [27 empty] | Torque | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
21 | [27 empty] | RPM | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
873 |  | BB1 | EM | 703 | BB1EM703 | Chemical filling pump 1 |  | Best guess < 1kW |  |  |  |  | 240 | [26 empty] | 4 | 1 | [22 empty] | 4001 | DOL_DIRH |  |  |  | Pump added | 3
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local run command | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local mode switch | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
873 |  | BB1 | EM | 704 | BB1EM704 | Chemical filling pump 2 |  | Best guess < 1kW |  |  |  |  | 240 | [26 empty] | 4 | 1 | [22 empty] | 4001 | DOL_DIRH |  |  |  | Pump added | 3
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local run command | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local mode switch | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
22 |  | BB1 | PU | 800 | BB1PU800 | Chemical dosing pump 1 |  |  |  | 0,37 |  |  | 230 | [29 empty] | 1 | [20 empty] | 4001 | CHEMICAL_PUMP |  | Field IO |  | Motor details | 1
23 | [27 empty] | Control signal | BB1PU800 | [13 empty] | X | [21 empty] | CHEMICAL_PUMP |  | Field IO
28 |  | BB1 | LS | 700 | BB1LS700 | Chemical tank 1 level switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | LS001 | Field IO |  | Instrument added | 1
29 | [27 empty] | Binary State | BB1LT001 | [10 empty] | X | [24 empty] | MEAS_BIN |  | Field IO
24 |  | BB1 | PU | 801 | BB1PU801 | Chemical dosing pump 2 |  |  |  | 0,37 |  |  | 230 | [29 empty] | 1 | [20 empty] | 4001 | CHEMICAL_PUMP |  | Field IO |  | Motor details | 1
25 | [27 empty] | Control signal | BB1PU801 | [13 empty] | X | [21 empty] | CHEMICAL_PUMP |  | Field IO
28 |  | BB1 | LS | 701 | BB1LS701 | Chemical tank 2 level switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | LS001 | Field IO |  | Instrument added | 1
29 | [27 empty] | Binary State | BB1LT001 | [10 empty] | X | [24 empty] | MEAS_BIN |  | Field IO
26 |  | BB1 | PT | 200 | BB1PT200 | Feed water tank pressure | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [13 empty] | Pressure |  |  |  | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
27 | [27 empty] | Measurement | BB1PT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
28 |  | BB1 | LT | 001 | BB1LT001 | Feed water tank level 1 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | LT001 | Field IO
29 | [27 empty] | Measurement | BB1LT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
30 |  | BB1 | LT | 002 | BB1LT002 | Feed water tank level 2 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | LT001 | Field IO
31 | [27 empty] | Measurement | BB1LT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
32 |  | BB1 | PT | 005 | BB1PT005 | Feed water pressure after valve | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
33 | [27 empty] | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
34 |  | BB1 | FT | 001 | BB1FT001 | Feed water flow and control | [35 empty] | 1 | [21 empty] | 4001 | MEAS_ANA | FT002 | Field IO
35 | [27 empty] | Measurement | BB1FT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
36 |  | BB1 | CV | 200 | BB1CV200 | Steam from drum control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
37 | [27 empty] | Setpoint position | BB1CV200 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
38 | [27 empty] | Position feedback | BB1CV200 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
39 |  | BB1 | TT | 001 | BB1TT001 | Feed water temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4001 | MEAS_ANA | TT001 | Field IO
40 | [27 empty] | Measurement | BB1TT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
41 |  | BB1 | IV | 002 | BB1IV002 | Feedwater pump 1 on-off valve |  |  |  | 0.25 | 1.9 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA10.2-22 + RWG |  | Konwell/Auma | 4001 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
43 |  | BB1 | TT | 002 | BB1TT002 | Feed water pump 2 bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
44 | [27 empty] | Measurement | BB1TT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
45 |  | BB1 | GS | 004 | BB1GS004 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
46 | [27 empty] | Binary state | BB1GS004 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
47 |  | BB1 | PT | 004 | BB1PT004 | Feed water pressure before valve | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
48 | [27 empty] | Measurement | BB1PT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
49 |  | BB1 | GS | 003 | BB1GS003 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
50 | [27 empty] | Binary state | BB1GS003 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
51 |  | BB1 | IV | 003 | BB1IV003 | Feed water pump 2 on-off valve |  |  |  | 0.25 | 1.9 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA10.2-22 + RWG |  | Konwell/Auma | 4001 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
53 |  | BB1 | PT | 002 | BB1PT002 | Feed water pump 2 pressure side pressure | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
54 | [27 empty] | Measurement | BB1PT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
55 |  | BB1 | CV | 001 | BB1CV001 | Make-up water control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
56 | [27 empty] | Setpoint position | BB1CV001 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
57 | [27 empty] | Position feedback | BB1CV001 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
58 |  | BB1 | PT | 006 | BB1PT006 | FW suction line strainer pressure diff. | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67LGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | PT004 | Field IO
59 | [27 empty] | Measurement | BB1PT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
60 |  | BB1 | GS | 001 | BB1GS001 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
61 | [27 empty] | Binary state | BB1GS001 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
62 |  | BB1 | PT | 007 | BB1PT007 | FW suction line strainer pressure diff. | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67LGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | PT004 | Field IO
63 | [27 empty] | Measurement | BB1PT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
64 |  | BB1 | TT | 005 | BB1TT005 | FW pump 2 motor winding temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
65 | [27 empty] | Measurement | BB1TT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
66 |  | BB1 | PT | 001 | BB1PT001 | Feed water pump 1 pressure side pressure | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
67 | [27 empty] | Measurement | BB1PT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
68 |  | BB1 | GS | 002 | BB1GS002 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
69 | [27 empty] | Binary state | BB1GS002 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
70 |  | BB1 | CV | 002 | BB1CV002 | Feed water control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
71 | [27 empty] | Setpoint position | BB1CV002 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
72 | [27 empty] | Position feedback | BB1CV002 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
73 |  | BB1 | TT | 004 | BB1TT004 | FW pump 1 motor winding temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
74 | [27 empty] | Measurement | BB1TT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
75 |  | BB1 | TT | 003 | BB1TT003 | FW pump 1 motor bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA |  | Field IO
76 | [27 empty] | Measurement | BB1TT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
77 |  | BB1 | SV | 410 | BB1SV410 | Feed water tank overflow valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4001 | BIN_VLV | AA005 | Field IO |  | tag changed | 1
78 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1IV001 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | 24 VDC feed added | 1
79 |  | BB1 | GS | 005 | BB1GS005 | FW tank overflow On-Off valve position | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
80 | [27 empty] | Binary state | BB1GS005 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
81 |  | BB1 | GS | 006 | BB1GS006 | FW tank overflow On-Off valve position | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
82 | [27 empty] | Binary state | BB1GS006 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
83 |  | BB1 | GS | 007 | BB1GS007 | Feedwater pump 1 on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
84 | [27 empty] | Binary state | BB1GS007 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
85 |  | BB1 | GS | 008 | BB1GS008 | Feedwater pump 1 on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
86 | [27 empty] | Binary state | BB1GS008 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
87 |  | BB1 | GS | 009 | BB1GS009 | Feed water pump 2 on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
88 | [27 empty] | Binary state | BB1GS009 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
89 |  | BB1 | GS | 010 | BB1GS010 | Feed water pump 2 on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
90 | [27 empty] | Binary state | BB1GS010 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
91 |  | BB1 | LT | 101 | BB1LT101 | Steam drum level 1 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
92 | [27 empty] | Measurement SRS | BB1LS100 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
91 |  | BB1 | LS | 103 | BB1LS103 | Steam drum level switch 1 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | LS003 | SRS |  | Instrument added | 2
92 | [27 empty] | Binary state SRS | BB1LS100 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Instrument added | 2
91 |  | BB1 | LS | 104 | BB1LS104 | Steam drum level switch 2 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | LS003 | SRS |  | Instrument added | 2
92 | [27 empty] | Binary state SRS | BB1LS100 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Instrument added | 2
93 |  | BB1 | IV | 004 | BB1IV004 | Boiler bottom blow down on-off valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4002 | BIN_VLV | AA005 | Field IO
94 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1IV004 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | 24 VDC feed added | 1
83 |  | BB1 | GS | 011 | BB1GS011 | Boiler bottom blow down on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 1
84 | [27 empty] | Binary state | BB1GS007 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
85 |  | BB1 | GS | 012 | BB1GS012 | Boiler bottom blow down on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 1
86 | [27 empty] | Binary state | BB1GS008 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
95 |  | BB1 | PT | 203 | BB1PT203 | Steam drum pressure 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4002 | MEAS_ANA_SRS | PT001.1 | SRS
96 | [27 empty] | Measurement SRS | BB1PT203 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
97 |  | BB1 | TT | 008 | BB1TT008 | Temperature after economizer | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4002 | MEAS_ANA | TT001 | Field IO
98 | [27 empty] | Measurement | BB1TT008 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
99 |  | BB1 | LT | 102 | BB1LT102 | Steam drum level 2 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
100 | [27 empty] | Measurement SRS | BB1LS101 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
101 |  | BB1 | PT | 201 | BB1PT201 | Steam drum pressure 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4002 | MEAS_ANA_SRS | PT001.1 | SRS
102 | [27 empty] | Measurement SRS | BB1PT201 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
103 |  | BB1 | LT | 103 | BB1LT103 | Steam drum level 3 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
104 | [27 empty] | Measurement SRS | BB1LS102 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
105 |  | BB1 | FT | 200 | BB1FT200 | Heating steam to feed water tank flow measurement | [30 empty] | 0 | 5 | t/h |  |  | 1 | [21 empty] | 4002 | MEAS_ANA | FT001 | Field IO
106 | [27 empty] | Measurement | BB1FT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
107 |  | BB1 | HS | 101 | BB1HS101 | Boiler emergency shutdown switch 1 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
108 | [27 empty] | Binary state SRS | BB1HS101 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
109 |  | BB1 | HS | 103 | BB1HS103 | Boiler emergency shutdown switch 3 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
111 |  | BB1 | TT | 009 | BB1TT009 | Temperature before economizer | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4002 | MEAS_ANA | TT001 | Field IO
112 | [27 empty] | Measurement | BB1TT009 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
113 |  | BB1 | HS | 104 | BB1HS104 | Boiler emergency shutdown switch 4 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
114 | [27 empty] | Binary state SRS | BB1HS104 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
115 |  | BB1 | HS | 102 | BB1HS102 | Boiler emergency shutdown switch 2 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
116 | [27 empty] | Binary state SRS | BB1HS102 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
117 |  | BB1 | HS | 105 | BB1HS105 | Boiler emergency shutdown switch 5 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
118 | [27 empty] | Binary state SRS | BB1HS105 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
119 |  | BB1 | HS | 106 | BB1HS106 | Boiler emergency shutdown switch 6 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
120 | [27 empty] | Binary state SRS | BB1HS106 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
121 |  | BB1 | HS | 107 | BB1HS107 | Boiler emergency shutdown switch 7 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
122 | [27 empty] | Binary state SRS | BB1HS107 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
123 |  | BB1 | HS | 108 | BB1HS108 | Boiler emergency shutdown switch 8 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
124 | [27 empty] | Binary state SRS | BB1HS108 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
125 |  | BB1 | HS | 109 | BB1HS109 | Boiler emergency shutdown switch 9 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
126 | [27 empty] | Binary state SRS | BB1HS109 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
127 |  | BB1 | HS | 110 | BB1HS110 | Boiler emergency shutdown switch 10 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
128 | [27 empty] | Binary state SRS | BB1HS110 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
129 |  | BB1 | HS | 111 | BB1HS111 | Boiler emergency shutdown switch 11 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
130 | [27 empty] | Binary state SRS | BB1HS111 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
131 |  | BB1 | HS | 112 | BB1HS112 | Boiler emergency shutdown switch 12 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
132 | [27 empty] | Binary state SRS | BB1HS112 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
133 |  | BB1 | TT | 200 | BB1TT200 | Main steam temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4003 | MEAS_ANA | TT001 | Field IO
134 | [27 empty] | Measurement | BB1TT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
135 |  | BB1 | FT | 202 | BB1FT202 | Main steam flow | [30 empty] | 0 | 30 | t/h |  |  | 1 | [21 empty] | 4003 | MEAS_ANA | FT001 | Field IO
136 | [27 empty] | Measurement | BB1FT202 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
137 |  | BB1 | IV | 202 | BB1IV202 | Main steam valve by-pass valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
138 | [27 empty] | Open direction command | BB1IV202 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
139 | [27 empty] | Close direction command | BB1IV202 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
140 | [27 empty] | Torque limit open direction | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
141 | [27 empty] | Torque limit close direction | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
142 | [27 empty] | Actuator fault | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
143 | [27 empty] | Position | BB1IV202 | [12 empty] | X | [22 empty] | MTR_VLV
144 |  | BB1 | CV | 201 | BB1CV201 | Start-up valve |  |  |  | 0.06 | 0.6 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SAR10.2 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
145 | [27 empty] | Open direction command | BB1CV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
146 | [27 empty] | Close direction command | BB1CV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
147 | [27 empty] | Torque limit open direction | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
148 | [27 empty] | Torque limit close direction | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
149 | [27 empty] | Actuator fault | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
150 | [27 empty] | Position | BB1CV201 | [12 empty] | X | [22 empty] | MTR_VLV
151 |  | BB1 | IV | 201 | BB1IV201 | Main steam valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA14.2-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
152 | [27 empty] | Open direction command | BB1IV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
153 | [27 empty] | Close direction command | BB1IV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
154 | [27 empty] | Torque limit open direction | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
155 | [27 empty] | Torque limit close direction | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
156 | [27 empty] | Actuator fault | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
157 | [27 empty] | Position | BB1IV201 | [12 empty] | X | [22 empty] | MTR_VLV
158 |  | BB1 | FT | 201 | BB1FT201 | Steam flow to sootblowing and air preheater | [30 empty] | 0 | 8 | t/h |  |  | 1 | [21 empty] | 4003 | MEAS_ANA | FT001 | Field IO
159 | [27 empty] | Measurement | BB1FT201 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
160 |  | BB1 | IV | 200 | BB1IV200 | Start-up check valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
167 |  | BB1 | GS | 221 | BB1GS221 | Main steam valve by-pass open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
168 | [27 empty] | Binary state | BB1GS221 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
169 |  | BB1 | GS | 222 | BB1GS222 | Main steam valve by-pass close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
170 | [27 empty] | Binary state | BB1GS222 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
171 |  | BB1 | GS | 223 | BB1GS223 | Main steam line valve open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
172 | [27 empty] | Binary state | BB1GS223 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
173 |  | BB1 | GS | 224 | BB1GS224 | Main steam line valve close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
174 | [27 empty] | Binary state | BB1GS224 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
175 |  | BB1 | GS | 225 | BB1GS225 | Start-up line ON-OFF valve open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
176 | [27 empty] | Binary state | BB1GS225 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
177 |  | BB1 | GS | 226 | BB1GS226 | Start-up line ON-OFF valve close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
178 | [27 empty] | Binary state | BB1GS226 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
179 |  | BB1 | GS | 200 | BB1GS200 | Sootblower 1 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
180 | [27 empty] | Binary state | BB1GS200 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
181 |  | BB1 | GS | 201 | BB1GS201 | Sootblower 1 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
182 | [27 empty] | Binary state | BB1GS201 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
183 |  | BB1 | GS | 203 | BB1GS203 | Sootblower 2 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
184 | [27 empty] | Binary state | BB1GS203 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
185 |  | BB1 | GS | 204 | BB1GS204 | Sootblower 2 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
186 | [27 empty] | Binary state | BB1GS204 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
187 |  | BB1 | GS | 205 | BB1GS205 | Sootblower 3 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
188 | [27 empty] | Binary state | BB1GS205 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
189 |  | BB1 | GS | 206 | BB1GS206 | Sootblower 3 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
190 | [27 empty] | Binary state | BB1GS206 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
191 |  | BB1 | GS | 207 | BB1GS207 | Sootblower 5 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
192 | [27 empty] | Binary state | BB1GS207 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
193 |  | BB1 | GS | 208 | BB1GS208 | Sootblower 5 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
194 | [27 empty] | Binary state | BB1GS208 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
195 |  | BB1 | GS | 209 | BB1GS209 | Sootblower 6 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
196 | [27 empty] | Binary state | BB1GS209 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
197 |  | BB1 | GS | 210 | BB1GS210 | Sootblower 6 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
198 | [27 empty] | Binary state | BB1GS210 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
199 |  | BB1 | GS | 211 | BB1GS211 | Sootblower 7 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
200 | [27 empty] | Binary state | BB1GS211 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
201 |  | BB1 | GS | 212 | BB1GS212 | Sootblower 7 IN limit switch | [6 empty] | 24 | [26 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
202 | [27 empty] | Binary state | BB1GS212 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
203 |  | BB1 | GS | 213 | BB1GS213 | Sootblower 8 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
204 | [27 empty] | Binary state | BB1GS213 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
205 |  | BB1 | GS | 214 | BB1GS214 | Sootblower 8 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
206 | [27 empty] | Binary state | BB1GS214 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
207 |  | BB1 | IV | 203 | BB1IV203 | Sootblowing line on-off valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4004 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
209 |  | BB1 | TT | 201 | BB1TT201 | Sootblowing line temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [21 empty] | 4004 | MEAS_ANA | TT001 | Field IO
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
209 |  | BB1 | TT |  |  | Electrical room temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [22 empty] | MEAS_ANA | TT007 |  |  | Instrument added | 3
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA
209 |  | BB1 | TT |  |  | PLC-cabinet temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [22 empty] | MEAS_ANA | TT007 |  |  | Instrument added | 3
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA
211 |  | BB1 | GS | 227 | BB1GS227 | Sootblowing line on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | MCC
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 228 | BB1GS228 | Sootblowing line on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | MCC
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
215 |  | BB1 | BL | 200 | BB1BL200 | Sootblower 1 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
221 |  | BB1 | BL | 201 | BB1BL201 | Sootblower 2 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
227 |  | BB1 | BL | 202 | BB1BL202 | Sootblower 3 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
233 |  | BB1 | BL | 203 | BB1BL203 | Sootblower 4 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
239 |  | BB1 | BL | 204 | BB1BL204 | Sootblower 5 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
245 |  | BB1 | BL | 205 | BB1BL205 | Sootblower 6 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
251 |  | BB1 | BL | 206 | BB1BL206 | Sootblower 7 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
257 |  | BB1 | TT | 006 | BB1TT006 | Blow down tank temperature and control | [30 empty] | 0 | 100 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4005 | MEAS_ANA | TT001 | Field IO
258 | [27 empty] | Measurement | BB1TT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
259 |  | BB1 | CV | 003 | BB1CV003 | Continuous blow down valve |  |  |  |  | 2 |  | 240 | [26 empty] | 3 | 2 | 1 | [17 empty] | Gestra | BAE 46-1-ANSI + EF10-1 + 1000 ohm |  | Konwell/Gestra | 4005 | MTR_VLV | AA001 |  |  | Model added | 1
260 | [27 empty] | Open direction command | BB1CV003 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
261 | [27 empty] | Close direction command | BB1CV003 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
262 | [27 empty] | Torque limit open direction | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
263 | [27 empty] | Torque limit close direction | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
264 | [27 empty] | Actuator fault | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
265 | [7 empty] | needs R/I converter 0...10 Kohm=4..20 mA | [19 empty] | Position | BB1CV003 | [12 empty] | X | [22 empty] | MTR_VLV
266 |  | BB1 | SV | 001 | BB1SV001 | Blow down tank cooling on/off valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4005 | BIN_VLV | AA005 | Field IO
267 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1SV001 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
268 |  | BB1 | PT | 205 | BB1PT205 | Steam outlet pressure from accumulator | [30 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA_SRS | PT001.1 | SRS |  | Moved to SRS | 2
269 | [27 empty] | Measurement SRS | BB1PT205 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS |  | Moved to SRS | 2
270 |  | BB1 | TT | 202 | BB1TT202 | Steam outlet temperature from accumulator | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
271 | [27 empty] | Measurement | BB1TT202 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
272 |  | BB1 | PT | 207 | BB1PT207 | Accumulator pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
273 | [27 empty] | Measurement | BB1PT207 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
274 |  | BB1 | CV | 203 | BB1CV203 | Steam accumulator pressure control valve |  |  |  | 0.25 | 1.8 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SAR14.2 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
211 |  | BB1 | GS | 231 | BB1GS231 | Steam accumulator pressure control valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | Field IO |  | Signal added | 1
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
213 |  | BB1 | GS | 230 | BB1GS230 | Steam accumulator pressure control valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | Field IO |  | Signal added | 1
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
277 |  | BB1 | TT | 007 | BB1TT007 | Accumulator temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
278 | [27 empty] | Measurement | BB1TT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
279 |  | BB1 | TT | 203 | BB1TT203 | 18bar(g) steam temperature |  | Transmitter wired to energy calculator | [28 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
280 | [27 empty] | Measurement | BB1TT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
281 |  | BB1 | CV | 202 | BB1CV202 | Steam pressure reduction valve |  |  |  | 0.25 | 1.8 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SAR14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 233 | BB1GS233 | Steam pressure reduction valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 232 | BB1GS232 | Steam pressure reduction valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
284 |  | BB1 | PT | 204 | BB1PT204 | Main steam pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
285 | [27 empty] | Measurement | BB1PT204 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
286 |  | BB1 | LT | 004 | BB1LT004 | Steam accumulator level 2 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4006 | MEAS_ANA | LT001 | Field IO
287 | [27 empty] | Measurement | BB1LT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
288 |  | BB1 | IV | 204 | BB1IV204 | Main steam line accumulator bypass on-off valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 217 | BB1GS217 | Main steam line accumulator bypass on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 218 | BB1GS218 | Main steam line accumulator bypass on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
290 |  | BB1 | PT | 208 | BB1PT208 | Accumulator pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
291 | [27 empty] | Measurement | BB1PT208 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
292 |  | BB1 | FT | 203 | BB1FT203 | Steam to existing header flow measurement | [30 empty] | 0 | 25 | t/h |  |  | 1 | [21 empty] | 4006 | MEAS_ANA | FT001 | Field IO
293 | [27 empty] | Measurement | BB1FT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
292 |  | BB1 | QT |  |  | Steam to existing header energy calculator | [6 empty] | 240 | [28 empty] | 1 | [17 empty] | E+H | RMS621-21BBA1221 |  |  | 4006 | MEAS_ANA |  | Field IO |  | Instrument added | 3
293 | [27 empty] | Measurement | BB1FT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
294 |  | BB1 | LT | 003 | BB1LT003 | Steam accumulator level 1 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4006 | MEAS_ANA | LT001 | Field IO
295 | [27 empty] | Measurement | BB1LT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
296 |  | BB1 | IV | 205 | BB1IV205 | Steam accumualtor ON-OFF isolating valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 219 | BB1GS219 | Steam accumualtor ON-OFF isolating valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 220 | BB1GS220 | Steam accumualtor ON-OFF isolating valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
298 |  | BB1 | GS | 217 | BB1GS217 | Steam accumulator by-pass valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
299 | [27 empty] | Binary state | BB1GS217 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
300 |  | BB1 | GS | 218 | BB1GS218 | Steam accumulator by-pass valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
301 | [27 empty] | Binary state | BB1GS218 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
302 |  | BB1 | GS | 220 | BB1GS220 | Steam accumulator ON-OFF valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
303 | [27 empty] | Binary state | BB1GS220 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
304 |  | BB1 | GS | 219 | BB1GS219 | Steam accumulator ON-OFF valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
305 | [27 empty] | Binary state | BB1GS219 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
306 |  | BB1 | QT | 002 | BB1QT002 | pH measurement from feed water tank | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
307 | [27 empty] | Measurement | BB1QT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
308 |  | BB1 | QT | 006 | BB1QT006 | Conductivity measurement from main steam | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
309 | [27 empty] | Measurement | BB1QT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
310 |  | BB1 | QT | 005 | BB1QT005 | Conductivity measurement from saturated steam | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
311 | [27 empty] | Measurement | BB1QT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
312 |  | BB1 | QT | 003 | BB1QT003 | Conductivity measurement from condensate | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
313 | [27 empty] | Measurement | BB1QT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
314 |  | BB1 | QT | 007 | BB1QT007 | Conductivity measurement from feed water line | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
315 | [27 empty] | Measurement | BB1QT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
316 |  | BB1 | QT | 001 | BB1QT001 | Conductivity measurement from feed water tank | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
317 | [27 empty] | Measurement | BB1QT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
318 |  | BB1 | QT | 004 | BB1QT004 | Conductivity measurement from boiler water | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
319 | [27 empty] | Measurement | BB1QT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
320 |  | BB1 | PT | 400 | BB1PT400 | Primary air pressure |  | SIL2 classified transmitter | [28 empty] | 0 | 16 | kPa | [6 empty] | 1 | [13 empty] | E+H | PMC51-AA22IA1EGJGCJA+LAZ1 | G1/2 |  | 4008 | MEAS_ANA_SRS | PT002 | SRS
321 | [27 empty] | Measurement SRS | BB1PT400 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
322 |  | BB1 | TT | 418 | BB1TT418 | Bed temperature 4 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
323 | [27 empty] | Measurement SRS | BB1TT418 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
324 |  | BB1 | PT | 404 | BB1PT404 | Boiler upper part pressure 1 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
325 | [27 empty] | Measurement SRS | BB1PT404 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
326 |  | BB1 | FT | 400 | BB1FT400 | Primary air flow |  | 0...11,21 mbar = 0...4,0 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
327 | [27 empty] | Measurement SRS | BB1FT400 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
328 |  | BB1 | PT | 401 | BB1PT401 | Secondary air pressure |  | SIL2 classified transmitter | [28 empty] | 0 | 6 | kPa | [6 empty] | 1 | [13 empty] | E+H | PMC51-AA22IA1CGJGCJA+LAZ1 | G1/2 |  | 4008 | MEAS_ANA_SRS | PT002 | SRS
329 | [27 empty] | Measurement SRS | BB1PT401 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
330 |  | BB1 | PT | 410 | BB1PT410 | Secondary air pressure inner front wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
331 | [27 empty] | Measurement | BB1PT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
332 |  | BB1 | TT | 551 | BB1TT551 | Flue gas temperature 2 | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
333 | [27 empty] | Measurement | BB1TT551 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
334 |  | BB1 | TT | 400 | BB1TT400 | Primary air temperature before preheater | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFG3000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
335 | [27 empty] | Measurement | BB1TT400 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
336 |  | BB1 | PT | 403 | BB1PT403 | Secondary air pressure inner back wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO
337 | [27 empty] | Measurement | BB1PT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
338 |  | BB1 | FT | 401 | BB1FT401 | Secondary air flow |  | 0...11,55 mbar = 0...4,6 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
339 | [27 empty] | Measurement SRS | BB1FT401 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
340 |  | BB1 | TT | 417 | BB1TT417 | Bed temperature 3 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
341 | [27 empty] | Measurement SRS | BB1TT417 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
342 |  | BB1 | PT | 550 | BB1PT550 | Flue gas pressure at the outlet of the boiler | [30 empty] | -35 | 35 | mbar |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO
343 | [27 empty] | Measurement | BB1PT550 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
344 |  | BB1 | TT | 012 | BB1TT012 | Condensate temperature from primary air preheater | [30 empty] | 0 | 250 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4008 | MEAS_ANA | TT001 | Field IO |  | Max scale changed | 3
345 | [27 empty] | Measurement | BB1TT012 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
346 |  | BB1 | TT | 413 | BB1TT413 | Bed temperature 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
347 | [27 empty] | Measurement SRS | BB1TT413 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
348 |  | BB1 | TT | 550 | BB1TT550 | Flue gas temperature 1 | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
349 | [27 empty] | Measurement | BB1TT550 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
350 |  | BB1 | TT | 412 | BB1TT412 | Boiler temperature after empty draft 2 | [30 empty] | 0 | 500 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
351 | [27 empty] | Measurement | BB1TT412 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
352 |  | BB1 | TT | 414 | BB1TT414 | Bed temperature 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
353 | [27 empty] | Measurement SRS | BB1TT414 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
354 |  | BB1 | PT | 405 | BB1PT405 | Boiler upper part pressure 2 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
355 | [27 empty] | Measurement SRS | BB1PT405 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
356 |  | BB1 | TT | 411 | BB1TT411 | Boiler temperature after empty draft 1 | [30 empty] | 0 | 500 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
357 | [27 empty] | Measurement | BB1TT411 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
358 |  | BB1 | QT | 550 | BB1QT550 | Fluegas oxygen measurement 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 25 | % | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | QT001/dn65 flange with counterflange. 1 meter probe | SRS
359 | [27 empty] | Measurement SRS | BB1QT550 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
360 |  | BB1 | FT | 550 | BB1FT550 | Recirculation gas flow |  | 0...10,19 mbar = 0...1,2 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
361 | [27 empty] | Measurement SRS | BB1FT550 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
362 |  | BB1 | QT | 551 | BB1QT551 | Fluegas oxygen measurement 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 25 | % | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | QT001/dn65 flange with counterflange. 1 meter probe | SRS
363 | [27 empty] | Measurement SRS | BB1QT551 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
364 |  | BB1 | QT | 552 | BB1QT552 | Fluegas CO measurement | [30 empty] | 0 | 5000 | ppm |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | QT001/dn65 flange with counterflange. 1 meter probe | Field IO
365 | [27 empty] | Measurement | BB1QT552 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
366 |  | BB1 | TT | 405 | BB1TT405 | Primary air temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFG3000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
367 | [27 empty] | Measurement | BB1TT405 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
368 |  | BB1 | PT | 406 | BB1PT406 | Boiler upper part pressure |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
369 | [27 empty] | Measurement SRS | BB1PT406 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
370 |  | BB1 | TT | 415 | BB1TT415 | Boiler bed temperature middle level | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEP |  |  | 4008 | MEAS_ANA | TT004 | Field IO
371 | [27 empty] | Measurement | BB1TT415 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
372 |  | BB1 | TT | 416 | BB1TT416 | Boiler bed temperature lower level | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEP |  |  | 4008 | MEAS_ANA | TT004 | Field IO
373 | [27 empty] | Measurement | BB1TT416 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
374 |  | BB1 | TT | 410 | BB1TT410 | Boiler 1st draft temperature | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TAF11-13ADA3GCFP+TEC420-YD12GEP |  |  | 4008 | MEAS_ANA | TT003 | Field IO
375 | [27 empty] | Measurement | BB1TT410 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
376 |  | BB1 | TT | 116 | BB1TT116 | Steam temperature to air preheater | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4008 | MEAS_ANA | TT001 | Field IO
377 | [27 empty] | Measurement | BB1TT116 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
378 |  | BB1 | TT | 308 | BB1TT308 | Furnace temperature connection | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TAF11-13ADA3GCFP+TEC420-YD12GEP |  |  | 4008 | MEAS_ANA | TT003 | Field IO
379 | [27 empty] | Measurement | BB1TT308 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
380 |  | BB1 | DM | 300 | BB1DM300 | Tertiary air damper 1 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
381 | [27 empty] | Setpoint position | BB1DM300 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
382 | [27 empty] | Position feedback | BB1DM300 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
383 |  | BB1 | DM | 400 | BB1DM400 | Primary air damper | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
384 | [27 empty] | Setpoint position | BB1DM400 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
385 | [27 empty] | Position feedback | BB1DM400 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
386 |  | BB1 | DM | 550 | BB1DM550 | Recirculation gas damper | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
387 | [27 empty] | Setpoint position | BB1DM550 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
388 | [27 empty] | Position feedback | BB1DM550 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
389 |  | BB1 | DM | 301 | BB1DM301 | Secondary air damper 4 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
390 | [27 empty] | Setpoint position | BB1DM301 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
391 | [27 empty] | Position feedback | BB1DM301 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
392 |  | BB1 | DM | 302 | BB1DM302 | Secondary air damper 3 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
393 | [27 empty] | Setpoint position | BB1DM302 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
394 | [27 empty] | Position feedback | BB1DM302 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
395 |  | BB1 | DM | 304 | BB1DM304 | Secondary air damper 1 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
396 | [27 empty] | Setpoint position | BB1DM304 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
397 | [27 empty] | Position feedback | BB1DM304 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
398 |  | BB1 | DM | 303 | BB1DM303 | Secondary air damper 2 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
399 | [27 empty] | Setpoint position | BB1DM303 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
400 | [27 empty] | Position feedback | BB1DM303 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
401 |  | BB1 | QT | 553 | BB1QT553 | Boiler room gas detector | [35 empty] | 1 | [21 empty] | 4008 | MEAS_ANA | XS001 | Field IO
402 | [27 empty] | Measurement | BB1QT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
403 |  | BB1 | TT | 408 | BB1TT408 | Secondary air fan motor bearing temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
404 | [27 empty] | Measurement | BB1TT408 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
403 |  | BB1 | TT | 423 | BB1TT423 | Secondary air fan motor bearing temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
404 | [27 empty] | Measurement | BB1TT408 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
405 |  | BB1 | TT | 406 | BB1TT406 | Secondary air fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
406 | [27 empty] | Measurement | BB1TT406 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
407 |  | BB1 | TT | 404 | BB1TT404 | Primary air fan motor bearing temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
408 | [27 empty] | Measurement | BB1TT404 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
407 |  | BB1 | TT | 409 | BB1TT409 | Primary air fan motor bearing temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
408 | [27 empty] | Measurement | BB1TT404 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
409 |  | BB1 | TT | 402 | BB1TT402 | Primary air fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
410 | [27 empty] | Measurement | BB1TT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
411 |  | BB1 | TT | 403 | BB1TT403 | Primary air fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
412 | [27 empty] | Measurement | BB1TT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
411 |  | BB1 | TT | 421 | BB1TT421 | Primary air fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
412 | [27 empty] | Measurement | BB1TT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
413 |  | BB1 | TT | 407 | BB1TT407 | Secondary air fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
414 | [27 empty] | Measurement | BB1TT407 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
413 |  | BB1 | TT | 422 | BB1TT422 | Secondary air fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
414 | [27 empty] | Measurement | BB1TT407 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
415 |  | BB1 | IV | 206 | BB1IV206 | Primary air preheater on-off valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA07.6-22 + RWG |  | Konwell/Auma | 4008 | MTR_VLV | AA003 |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
417 |  | BB1 | CV | 004 | BB1CV004 | Primary air preheater control valve | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
418 | [27 empty] | Setpoint position | BB1CV004 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
419 | [27 empty] | Position feedback | BB1CV004 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
420 |  | BB1 | GS | 215 | BB1GS215 | Primary air preheater on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4008 | MEAS_BIN | XS002/XS004 | MCC
421 | [27 empty] | Binary state | BB1GS215 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
422 |  | BB1 | GS | 216 | BB1GS216 | Primary air preheater on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4008 | MEAS_BIN | XS002/XS004 | MCC
423 | [27 empty] | Binary state | BB1GS216 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
424 |  | BB1 | IL | 001 | BB1IL001 | Alarm horn and light CO alarm | [34 empty] | 1 | [22 empty] | 4008 | ALM_HORN |  | Field IO |  | Description changed | 2
425 | [27 empty] | Command | BB1IL001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
426 |  | BB1 | PT | 409 | BB1PT409 | Secondary air pressure outer front wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
427 | [27 empty] | Measurement | BB1PT400 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
428 |  | BB1 | PT | 411 | BB1PT411 | Secondary air pressure outer back wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
429 | [27 empty] | Measurement | BB1PT401 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
430 |  | BB1 | PT | 407 | BB1PT407 | Tertiary air pressure right wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
431 | [27 empty] | Measurement | BB1PT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
432 |  | BB1 | PT | 408 | BB1PT408 | Tertiary air pressure left wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
433 | [27 empty] | Measurement | BB1PT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
434 |  | BB1 | EM | 400 | BB1EM400 | Primary air fan |  |  |  | 132 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4008 | FRQ_DIR |  |  |  | Size and voltage | 1
435 | [27 empty] | Running | BB1FF400 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
436 | [27 empty] | MCC Fault | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
437 | [27 empty] | Safety switch | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
438 | [27 empty] | VFD Alarm | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
439 | [27 empty] | Run command | BB1FF400 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
440 | [27 empty] | Current | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
441 | [27 empty] | Speed reference | BB1FF400 | [21 empty] | X | [13 empty] | FRQ_DIR
442 | [27 empty] | Actual speed | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
443 | [27 empty] | Torque | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
444 | [27 empty] | RPM | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
445 |  | BB1 | SI | 400 | BB1SI400 | Primary air fan safety interlock | [38 empty] | 1 | [18 empty] | 4008 | FAN_SRS_DO
446 | [27 empty] | Safety interlock | BB1SI400 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 410 | BB1SI410 | Primary air fan run status SRS | [37 empty] | 1 | [19 empty] | 4008 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 400 | BB1ST400 | Primary air fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
447 |  | BB1 | EM | 401 | BB1EM401 | Secondary air fan |  |  |  | 45 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4008 | FRQ_DIR |  |  |  | Size, name and voltage | 1
448 | [27 empty] | Running | BB1FF401 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
449 | [27 empty] | MCC Fault | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
450 | [27 empty] | Safety switch | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
451 | [27 empty] | VFD Alarm | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
452 | [27 empty] | Run command | BB1FF401 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
453 | [27 empty] | Current | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
454 | [27 empty] | Speed reference | BB1FF401 | [21 empty] | X | [13 empty] | FRQ_DIR
455 | [27 empty] | Actual speed | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
456 | [27 empty] | Torque | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
457 | [27 empty] | RPM | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
458 |  | BB1 | SI | 401 | BB1SI401 | Secondary air fan safety interlock | [38 empty] | 1 | [18 empty] | 4008 | FAN_SRS_DO
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 411 | BB1SI411 | Secondary air fan run status SRS | [37 empty] | 1 | [19 empty] | 4008 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 401 | BB1ST401 | Secondary air fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
107 |  | BB1 | HS | 601 | BB1HS601 | Fuel system emergency shutdown switch 1 |  | Near door that leads hydraulic units | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
108 | [27 empty] | Binary state SRS | BB1HS101 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 602 | BB1HS602 | Fuel system emergency shutdown switch 2 |  | Outside near lift doors fuel receiving station | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 603 | BB1HS603 | Fuel system emergency shutdown switch 3 |  | Screening station | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 604 | BB1HS604 | Fuel system emergency shutdown switch 4 |  | Outside, on Fuel silo level near door | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
460 |  | BB1 | GS | 621 | BB1GS621 | Unloading station 3, block 3, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
461 | [27 empty] | Binary state | BB1GS621 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
462 |  | BB1 | GS | 611 | BB1GS611 | Unloading station 2, block 2, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
463 | [27 empty] | Binary state | BB1GS611 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
464 |  | BB1 | GS | 606 | BB1GS606 | Unloading station 1, block 1, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
465 | [27 empty] | Binary state | BB1GS606 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
466 |  | BB1 | GS | 614 | BB1GS614 | Unloading station 2, block 2, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
467 | [27 empty] | Binary state | BB1GS614 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
468 |  | BB1 | GS | 619 | BB1GS619 | Unloading station 3, block 3, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
469 | [27 empty] | Binary state | BB1GS619 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
470 |  | BB1 | GS | 651 | BB1GS651 | Disc screen by-pass damper limit switch to screen | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack | Instrument type added | 1
471 | [27 empty] | Binary state | BB1GS651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
472 |  | BB1 | PS | 602 | BB1PS602 | Hydraulics unit 1, block 3, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
473 | [27 empty] | Binary state | BB1PT602 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
474 |  | BB1 | GS | 615 | BB1GS615 | Unloading station 2, block 2, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
475 | [27 empty] | Binary state | BB1GS615 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
476 |  | BB1 | GS | 623 | BB1GS623 | Unloading station 3, block 3, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
477 | [27 empty] | Binary state | BB1GS623 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
478 |  | BB1 | ST | 651 | BB1ST651 | Scraper conveyor 2, rotation guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
479 | [27 empty] | Binary state | BB1ST651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
480 |  | BB1 | GS | 603 | BB1GS603 | Unloading station 1, block 1, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
481 | [27 empty] | Binary state | BB1GS603 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
482 |  | BB1 | PS | 601 | BB1PS601 | Hydraulics unit 1, block 2, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
483 | [27 empty] | Binary state | BB1PT601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
484 |  | BB1 | GS | 650 | BB1GS650 | Disc screen by-pass damper limit switch by-pass pos. | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack | Instrument type added | 1
485 | [27 empty] | Binary state | BB1GS650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
486 |  | BB1 | GS | 622 | BB1GS622 | Unloading station 3, block 3, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
487 | [27 empty] | Binary state | BB1GS622 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
488 |  | BB1 | GS | 602 | BB1GS602 | Unloading station 1, block 1, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
489 | [27 empty] | Binary state | BB1GS602 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
490 |  | BB1 | LS | 655 | BB1LS655 | Scraper conveyor 2, turning point blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
491 | [27 empty] | Binary state | BB1LS655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
492 |  | BB1 | GS | 607 | BB1GS607 | Unloading station 1, block 1, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
493 | [27 empty] | Binary state | BB1GS607 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
494 |  | BB1 | GS | 605 | BB1GS605 | Unloading station 1, block 1, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
495 | [27 empty] | Binary state | BB1GS605 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
496 |  | BB1 | LS | 652 | BB1LS652 | Unloading station 2, block 2, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
497 | [27 empty] | Binary state | BB1LS652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
498 |  | BB1 | GS | 601 | BB1GS601 | Unloading station 1, block 1, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
499 | [27 empty] | Binary state | BB1GS601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
500 |  | BB1 | LS | 608 | BB1LS608 | Hydraulics unit 1, low oil level alarm | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | LS001 | Field IO | Fuel station IO-rack
501 | [27 empty] | Binary state | BB1LS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
502 |  | BB1 | LS | 656 | BB1LS656 | Scraper conveyor 2, fuel silo side blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO
503 | [27 empty] | Binary state | BB1LS656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
504 |  | BB1 | LS | 600 | BB1LS600 | Hydraulics unit 1, leaking pool limit switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | LS001 | Field IO | Fuel station IO-rack
505 | [27 empty] | Binary state | BB1LS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
506 |  | BB1 | GS | 609 | BB1GS609 | Unloading station 2, block 2, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
507 | [27 empty] | Binary state | BB1GS609 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
508 |  | BB1 | LS | 650 | BB1LS650 | Scraper conveyor 1 bed height level switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
509 | [27 empty] | Binary state | BB1LS650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
510 |  | BB1 | GS | 617 | BB1GS617 | Unloading station 3, block 3, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
511 | [27 empty] | Binary state | BB1GS617 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
512 |  | BB1 | LS | 651 | BB1LS651 | Unloading station 3, block 3, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
513 | [27 empty] | Binary state | BB1LS651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
514 |  | BB1 | GS | 612 | BB1GS612 | Unloading station 2, block 2, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
515 | [27 empty] | Binary state | BB1GS612 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
516 |  | BB1 | LS | 654 | BB1LS654 | Scraper conveyor 1, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
517 | [27 empty] | Binary state | BB1LS654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
518 |  | BB1 | GS | 613 | BB1GS613 | Unloading station 2, block 2, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
519 | [27 empty] | Binary state | BB1GS613 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
520 |  | BB1 | GS | 620 | BB1GS620 | Unloading station 3, block 3, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
521 | [27 empty] | Binary state | BB1GS620 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
522 |  | BB1 | GS | 618 | BB1GS618 | Unloading station 3, block 3, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
523 | [27 empty] | Binary state | BB1GS618 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
524 |  | BB1 | PS | 600 | BB1PS600 | Hydraulics unit 1, block 1, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
525 | [27 empty] | Binary state | BB1PT600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
526 |  | BB1 | GS | 608 | BB1GS608 | Unloading station 2, block 2, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
527 | [27 empty] | Binary state | BB1GS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
528 |  | BB1 | GS | 604 | BB1GS604 | Unloading station 1, block 1, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
529 | [27 empty] | Binary state | BB1GS604 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
530 |  | BB1 | LS | 653 | BB1LS653 | Unloading station 1, block 1, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
531 | [27 empty] | Binary state | BB1LS653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
532 |  | BB1 | GS | 616 | BB1GS616 | Unloading station 3, block 3, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
533 | [27 empty] | Binary state | BB1GS616 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
534 |  | BB1 | GS | 600 | BB1GS600 | Unloading station 1, block 1, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
535 | [27 empty] | Binary state | BB1GS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
536 |  | BB1 | ST | 650 | BB1ST650 | Scraper conveyor 1, rotation guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
537 | [27 empty] | Binary state | BB1ST650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
538 |  | BB1 | TT | 650 | BB1TT650 | Scraper conveyor 1, temperature measurement | [30 empty] | 0 | 150 | °C |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | TT006 | Field IO | Fuel station IO-rack
539 | [27 empty] | Measurement | BB1TT650 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
540 |  | BB1 | GS | 610 | BB1GS610 | Unloading station 2, block 2, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
541 | [27 empty] | Binary state | BB1GS610 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
542 |  | BB1 | LT | 611 | BB1LT611 | Unloading station 1 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
543 | [27 empty] | Measurement | BB1LT509 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
544 |  | BB1 | LT | 612 | BB1LT612 | Unloading station 3 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
545 | [27 empty] | Measurement | BB1LT513 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
546 |  | BB1 | LT | 613 | BB1LT613 | Unloading station 2 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
547 | [27 empty] | Measurement | BB1LT512 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
548 |  | BB1 | SV | 601 | BB1SV601 | Control Valve push feeders unloading station 1 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
549 | [27 empty] | Control out | BB1SV601 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
550 | [27 empty] | Control in | BB1SV601 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
551 |  | BB1 | ST | 675 | BB1ST675 | Leveling roller 3 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
552 | [27 empty] | Binary state | BB1ST703 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
553 |  | BB1 | SV | 603 | BB1SV603 | Control Valve push feeders unloading station 3 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
554 | [27 empty] | Control out | BB1SV603 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
555 | [27 empty] | Control in | BB1SV603 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
556 |  | BB1 | SV | 602 | BB1SV602 | Control Valve push feeders unloading station 2 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
557 | [27 empty] | Control out | BB1SV602 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
558 | [27 empty] | Control in | BB1SV602 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
559 |  | BB1 | TS | 608 | BB1TS608 | High temperature switch hydraulic oil | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack
560 | [27 empty] | Binary state | BB1TS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
561 |  | BB1 | ST | 673 | BB1ST673 | Leveling roller 1 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
562 | [27 empty] | Binary state | BB1ST701 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
563 |  | BB1 | TS | 600 | BB1TS600 | Hydraulics unit, thermostat for heater | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack
564 | [27 empty] | Binary state | BB1TS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
565 |  | BB1 | ST | 674 | BB1ST674 | Leveling roller 2 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
566 | [27 empty] | Binary state | BB1ST702 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
567 |  | BB1 | PS | 605 | BB1PS605 | Hydraulic oil return block 3 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
568 | [27 empty] | Binary state | BB1PS603 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
569 |  | BB1 | PS | 603 | BB1PS603 | Hydraulic oil return block 1 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
570 | [27 empty] | Binary state | BB1PS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
571 |  | BB1 | PS | 604 | BB1PS604 | Hydraulic oil return block 2 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
572 | [27 empty] | Binary state | BB1PS601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
573 |  | BB1 | EM | 603 | BB1EM603 | Fuel reception hydraulic unit 1, pump 1 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
574 | [27 empty] | Running | BB1PU603 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH |  |  |  | Motor details | 1
575 | [27 empty] | MCC Fault | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH |  |  |  | Motor details | 1
576 | [27 empty] | Safety switch | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
577 | [27 empty] | VFD Alarm | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
578 | [27 empty] | Run command | BB1PU603 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
579 | [27 empty] | Current | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
580 | [27 empty] | Speed reference | BB1PU603 | [21 empty] | X | [13 empty] | FRQ_DIRH
581 | [27 empty] | Actual speed | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
582 | [27 empty] | Torque | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
583 | [27 empty] | RPM | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
584 | [27 empty] | Local run command | BB1PU603 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
585 | [27 empty] | Local mode switch | BB1PU603 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 603 | BB1SI603 | Fuel reception hydraulic unit 1, pump 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
586 |  | BB1 | EM | 604 | BB1EM604 | Fuel reception hydraulic unit 1, pump 2 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
587 | [27 empty] | Running | BB1PU604 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH
588 | [27 empty] | MCC Fault | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
589 | [27 empty] | Safety switch | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
590 | [27 empty] | VFD Alarm | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
591 | [27 empty] | Run command | BB1PU604 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
592 | [27 empty] | Current | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
593 | [27 empty] | Speed reference | BB1PU604 | [21 empty] | X | [13 empty] | FRQ_DIRH
594 | [27 empty] | Actual speed | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
595 | [27 empty] | Torque | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
596 | [27 empty] | RPM | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
597 | [27 empty] | Local run command | BB1PU604 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
598 | [27 empty] | Local mode switch | BB1PU604 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 604 | BB1SI604 | Fuel reception hydraulic unit 1, pump 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
599 |  | BB1 | EM | 605 | BB1EM605 | Fuel reception hydraulic unit 1, pump 3 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
600 | [27 empty] | Running | BB1PU605 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH
601 | [27 empty] | MCC Fault | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
602 | [27 empty] | Safety switch | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
603 | [27 empty] | VFD Alarm | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
604 | [27 empty] | Run command | BB1PU605 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
605 | [27 empty] | Current | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
606 | [27 empty] | Speed reference | BB1PU605 | [21 empty] | X | [13 empty] | FRQ_DIRH
607 | [27 empty] | Actual speed | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
608 | [27 empty] | Torque | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
609 | [27 empty] | RPM | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
610 | [27 empty] | Local run command | BB1PU605 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
611 | [27 empty] | Local mode switch | BB1PU605 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 605 | BB1SI605 | Fuel reception hydraulic unit 1, pump 3 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
612 |  | BB1 | EM | 673 | BB1EM673 | Levelling roller 1 |  |  |  | 2,2 |  |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size changed | 3
613 | [27 empty] | Running FWD | BB1EM703 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
614 | [27 empty] | Running BWD | BB1EM703 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
615 | [27 empty] | MCC Fault | BB1EM703 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
616 | [27 empty] | Local FWD command | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
617 | [27 empty] | Local BWD command | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
618 | [27 empty] | Local mode switch | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
619 | [27 empty] | Run command FWD | BB1EM703 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
620 | [27 empty] | Run command BWD | BB1EM703 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
621 | [27 empty] | Current | BB1EM703 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
622 |  | BB1 | EM | 674 | BB1EM674 | Levelling roller 2 |  |  |  | 3 |  |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size changed | 3
623 | [27 empty] | Running FWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
624 | [27 empty] | Running BWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
625 | [27 empty] | MCC Fault | BB1EM704 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
626 | [27 empty] | Local FWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
627 | [27 empty] | Local BWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
628 | [27 empty] | Local mode switch | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
629 | [27 empty] | Run command FWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
630 | [27 empty] | Run command BWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
631 | [27 empty] | Current | BB1EM704 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
632 |  | BB1 | EM | 675 | BB1EM675 | Levelling roller 3 | [57 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor deleted | 2
633 | [27 empty] | Running FWD | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
634 | [27 empty] | Running BWD | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
635 | [27 empty] | MCC Fault | BB1EM703 | [28 empty] | NC | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
636 | [27 empty] | Local FWD command | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
637 | [27 empty] | Local BWD command | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
638 | [27 empty] | Local mode switch | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
639 | [27 empty] | Run command FWD | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
640 | [27 empty] | Run command BWD | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
641 | [27 empty] | Current | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
642 |  | BB1 | EM | 658 | BB1EM658 | Scraper Conveyor 1 |  |  |  | 15 |  |  | 415 | [26 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Tag changed and motor details | 1
643 | [27 empty] | Running FWD | BB1CO653 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
644 | [27 empty] | Running BWD | BB1CO653 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
645 | [27 empty] | MCC Fault | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
646 | [27 empty] | Safety switch | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
647 | [27 empty] | VFD Alarm | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
648 | [27 empty] | Local FWD command | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
649 | [27 empty] | Local BWD command | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
650 | [27 empty] | Local mode switch | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
651 | [27 empty] | Run command FWD | BB1CO653 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
652 | [27 empty] | Run command BWD | BB1CO653 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
653 | [27 empty] | Current | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
654 | [27 empty] | Speed reference | BB1CO653 | [21 empty] | X | [13 empty] | FRQ_REVH
655 | [27 empty] | Actual speed | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
656 | [27 empty] | Torque | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
657 | [27 empty] | RPM | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 658 | BB1SI658 | Scraper Conveyor 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
658 |  | BB1 | EM | 670 | BB1EM670 | Belt magnet |  |  |  | 2.2 | 4.2 | 1500 | 415 | [26 empty] | 2 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIRH_BUS |  |  |  | Motor details and type | 1
659 | [27 empty] | Running FWD | BB1CO654 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
660 | [27 empty] | Running BWD | BB1CO654 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
661 | [27 empty] | MCC Fault | BB1CO654 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
662 | [27 empty] | Local FWD command | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
663 | [27 empty] | Local BWD command | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
664 | [27 empty] | Local mode switch | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
665 | [27 empty] | Run command FWD | BB1CO654 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
666 | [27 empty] | Run command BWD | BB1CO654 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
667 | [27 empty] | Current | BB1CO654 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
685 |  | BB1 | ST | 654 | BB1ST654 | Belt magnet rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 661 | BB1GS661 | Belt magnet deviation detector 1 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCRT115EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 662 | BB1GS662 | Belt magnet deviation detector 2 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCRT115EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
668 |  | BB1 | EM | 659 | BB1EM659 | Belt Conveyor |  |  |  | 4 | 7.6 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Motor details and type | 1
669 | [27 empty] | Running FWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
670 | [27 empty] | Running BWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
671 | [27 empty] | MCC Fault | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
672 | [27 empty] | Safety switch | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
673 | [27 empty] | VFD Alarm | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
674 | [27 empty] | Local FWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
675 | [27 empty] | Local BWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
676 | [27 empty] | Local mode switch | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
677 | [27 empty] | Run command FWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
678 | [27 empty] | Run command BWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
679 | [27 empty] | Current | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
680 | [27 empty] | Speed reference | BB1CO655 | [21 empty] | X | [13 empty] | FRQ_REVH
681 | [27 empty] | Actual speed | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
682 | [27 empty] | Torque | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
683 | [27 empty] | RPM | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
684 | [7 empty] | Brake |  |  |  |  | 240 | [55 empty] | Feed added | 1
458 |  | BB1 | SI | 659 | BB1SI659 | Belt Conveyor safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
685 |  | BB1 | ST | 652 | BB1ST652 | Belt conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 659 | BB1GS659 | Belt conveyor deviation detector 1 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Steute | Ex ES 98 SR-11-3GD |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 660 | BB1GS660 | Belt conveyor deviation detector 2 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Steute | Ex ES 98 SR-11-3GD |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 663 | BB1GS663 | Belt conveyor oversize detector | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
687 |  | BB1 | EM | 675 | BB1EM75 | Disc screen drive 1 |  |  |  | 7.5 | 13.7 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Tag changed | 3
688 | [27 empty] | Running FWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
689 | [27 empty] | Running BWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
690 | [27 empty] | MCC Fault | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
691 | [27 empty] | Safety switch | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
692 | [27 empty] | VFD Alarm | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
693 | [27 empty] | Local FWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
694 | [27 empty] | Local BWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
695 | [27 empty] | Local mode switch | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
696 | [27 empty] | Run command FWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
697 | [27 empty] | Run command BWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
698 | [27 empty] | Current | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
699 | [27 empty] | Speed reference | BB1CO655 | [21 empty] | X | [13 empty] | FRQ_REVH
700 | [27 empty] | Actual speed | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
701 | [27 empty] | Torque | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
702 | [27 empty] | RPM | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 675 | BB1SI675 | Disc screen drive 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
703 |  | BB1 | EM | 676 | BB1EM676 | Disc screen drive 2 |  |  |  | 7.5 | 13.7 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH | XS002 |  |  | Tag changed | 3
704 | [27 empty] | Running FWD | BB1CO656 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
705 | [27 empty] | Running BWD | BB1CO656 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
706 | [27 empty] | MCC Fault | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
707 | [27 empty] | Safety switch | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
708 | [27 empty] | VFD Alarm | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
709 | [27 empty] | Local FWD command | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
710 | [27 empty] | Local BWD command | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
711 | [27 empty] | Local mode switch | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
712 | [27 empty] | Run command FWD | BB1CO656 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
713 | [27 empty] | Run command BWD | BB1CO656 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
714 | [27 empty] | Current | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
715 | [27 empty] | Speed reference | BB1CO656 | [21 empty] | X | [13 empty] | FRQ_REVH
716 | [27 empty] | Actual speed | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
717 | [27 empty] | Torque | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
718 | [27 empty] | RPM | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 676 | BB1SI676 | Disc screen drive 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
719 |  | BB1 | ST | 656 | BB1ST656 | Disc screen drive 1 rotation guard | [33 empty] | 1 | [19 empty] | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument type added | 1
720 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
721 |  | BB1 | ST | 657 | BB1ST657 | Disc screen drive 2 rotation guard | [33 empty] | 1 | [19 empty] | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument type added | 1
722 | [27 empty] | Binary state | BB1ST657 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
723 |  | BB1 | EM | 672 | BB1EM672 | Scraper Conveyor 2 |  |  |  | 18,5 |  |  | 415 | [26 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Motor size changed | 3
724 | [27 empty] | Running FWD | BB1CO657 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
725 | [27 empty] | Running BWD | BB1CO657 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
726 | [27 empty] | MCC Fault | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
727 | [27 empty] | Safety switch | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
728 | [27 empty] | VFD Alarm | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
729 | [27 empty] | Local FWD command | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
730 | [27 empty] | Local BWD command | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
731 | [27 empty] | Local mode switch | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
732 | [27 empty] | Run command FWD | BB1CO657 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
733 | [27 empty] | Run command BWD | BB1CO657 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
734 | [27 empty] | Current | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
735 | [27 empty] | Speed reference | BB1CO657 | [21 empty] | X | [13 empty] | FRQ_REVH
736 | [27 empty] | Actual speed | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
737 | [27 empty] | Torque | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
738 | [27 empty] | RPM | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 672 | BB1SI672 | Scraper Conveyor 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
739 |  | BB1 | IJ | 002 | BB1IJ002 | Scraper Conveyor 1 Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4009 | ALM_HORN |  | Field IO | Fuel station IO-rack
740 | [27 empty] | Command | BB1IJ002 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO | Fuel station IO-rack
741 |  | BB1 | IJ | 001 | BB1IJ001 | Scraper Conveyor 2 Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4009 | ALM_HORN |  | Field IO
742 | [27 empty] | Command | BB1IJ001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
743 |  | BB1 | EM | 601 | BB1EM601 | Dust extraction rotary feeder |  | preliminary size |  | 0,75 | [29 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size added | 3
744 | [27 empty] | Running FWD | BB1RV601 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
745 | [27 empty] | Running BWD | BB1RV601 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
746 | [27 empty] | MCC Fault | BB1RV601 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
747 | [27 empty] | Local FWD command | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
748 | [27 empty] | Local BWD command | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
749 | [27 empty] | Local mode switch | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
750 | [27 empty] | Run command FWD | BB1RV601 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
751 | [27 empty] | Run command BWD | BB1RV601 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
752 | [27 empty] | Current | BB1RV601 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
753 |  | BB1 | EM | 606 | BB1EM606 | Dust extraction fan |  | preliminary size |  | 30 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIR_BUS |  |  |  | Tag and motor size changed | 3
754 | [27 empty] | Running | BB1FF603 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
755 | [27 empty] | MCC Fault | BB1FF603 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
756 | [27 empty] | Run command | BB1FF603 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
757 | [27 empty] | Current | BB1FF603 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
758 |  | BB1 | EH | 600 | BB1EH600 | Electric heater hydraulic unit |  | preliminary size |  | 1,5 | [37 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIR_BUS
759 | [27 empty] | Running | BB1EH600 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
760 | [27 empty] | MCC Fault | BB1EH600 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
761 | [27 empty] | Run command | BB1EH600 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
762 | [27 empty] | Current | BB1EH600 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
763 |  | BB1 | CV | 402 | BB1CV402 | Fuel chute B carrying air control valve 2 | [35 empty] | 1 | 1 | [20 empty] | 4010 | CONT_VLV | AA002 | Field IO
764 | [27 empty] | Setpoint position | BB1CV402 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
765 | [27 empty] | Position feedback | BB1CV402 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
766 |  | BB1 | CV | 403 | BB1CV403 | Fuel chute A carrying air control valve 1 | [35 empty] | 1 | 1 | [20 empty] | 4010 | CONT_VLV | AA002 | Field IO
767 | [27 empty] | Setpoint position | BB1CV403 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
768 | [27 empty] | Position feedback | BB1CV403 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
769 |  | BB1 | GS | 652 | BB1GS652 | Explosion hatch limit switch 1 | [33 empty] | 1 | [19 empty] | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
770 | [27 empty] | Binary state | BB1GS652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
771 |  | BB1 | GS | 653 | BB1GS653 | Explosion hatch limit switch 2 | [33 empty] | 1 | [19 empty] | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
772 | [27 empty] | Binary state | BB1GS653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
773 |  | BB1 | GS | 654 | BB1GS654 | Explosion hatch limit switch 3 | [33 empty] | 0 | [22 empty] | LAITEX | 4010 | MEAS_BIN | XS002 |  |  | Instrument removed | 1
774 | [27 empty] | Binary state | BB1GS654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
775 |  | BB1 | GS | 655 | BB1GS655 | Explosion hatch limit switch 4 | [33 empty] | 0 | [22 empty] | LAITEX | 4010 | MEAS_BIN | XS002 |  |  | Instrument removed | 1
776 | [27 empty] | Binary state | BB1GS655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
777 |  | BB1 | LS | 657 | BB1LS657 | Fuel silo discharge screw blockage switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument type added | 1
778 | [27 empty] | Binary state | BB1LS657 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
779 |  | BB1 | LS | 658 | BB1LS658 | Fuel silo cross conveyor blockage switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Description changed | 2
780 | [27 empty] | Binary state | BB1LS658 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
779 |  | BB1 | LS |  | BB1LS | Fuel silo cross conveyor explosion hatch limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 2
780 | [27 empty] | Binary state | BB1LS658 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
781 |  | BB1 | LS | 659 | BB1LS659 | Fuel feeding screw 1 blockage switch | [33 empty] | 1 | [16 empty] | 3-wire |  |  | Telemechanique | XS630B1PAL10EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | 3-wire | 2
782 | [27 empty] | Binary state | BB1LS659 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
783 |  | BB1 | LS | 660 | BB1LS660 | Fuel feeding screw 2 blockage switch | [33 empty] | 1 | [16 empty] | 3-wire |  |  | Telemechanique | XS630B1PAL10EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | 3-wire | 2
784 | [27 empty] | Binary state | BB1LS660 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
785 |  | BB1 | LT | 650 | BB1LT650 | Fuel silo level radar 1 | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT10-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 | Field IO |  | Instrument type added | 1
786 | [27 empty] | Measurement | BB1LT650 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA |  | Field IO
785 |  | BB1 | LT | 651 | BB1LT651 | Fuel silo level radar 2 | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT10-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 |  |  | Instrument deleted | 2
786 | [27 empty] | Measurement | BB1LT650 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA
787 |  | BB1 | LT | 652 | BB1LT652 | Fuel pocket level | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT20-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 | Field IO |  | Instrument type added | 1
788 | [27 empty] | Measurement | BB1LT652 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA |  | Field IO
789 |  | BB1 | ST | 649 | BB1ST649 | Fuel silo cross conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Description modified | 3
790 | [27 empty] | Binary state | BB1ST649 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
791 |  | BB1 | ST | 652 | BB1ST652 | Rotating fuel spreader rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
792 | [27 empty] | Binary state | BB1ST652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
793 |  | BB1 | ST | 653 | BB1ST653 | Fuel feeding screw 2 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | 2-wire | 2
794 | [27 empty] | Binary state | BB1ST653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
795 |  | BB1 | ST | 654 | BB1ST654 | Fuel feeding rotary feeder 1 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
796 | [27 empty] | Binary state | BB1ST654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
797 |  | BB1 | ST | 655 | BB1ST655 | Fuel feeding rotary feeder 2 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
798 | [27 empty] | Binary state | BB1ST655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
799 |  | BB1 | ST | 659 | BB1ST659 | Fuel feeding screw 1 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | 2-wire | 2
800 | [27 empty] | Binary state | BB1ST659 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
801 |  | BB1 | SV | 400 | BB1SV400 | Sealing air to rotary feeder solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
802 | [27 empty] | Control command | BB1SV400 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
803 |  | BB1 | SV | 406 | BB1SV406 | Sealing air to rotary feeder solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
804 | [27 empty] | Control command | BB1SV406 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
805 |  | BB1 | SV | 950 | BB1SV950 | Fuel silo fire water control valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
806 | [27 empty] | Control command | BB1SV950 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
807 |  | BB1 | SV | 951 | BB1SV951 | Fuel pocket fire water control valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
808 | [27 empty] | Control command | BB1SV951 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
809 |  | BB1 | TT | 652 | BB1TT652 | Fuel silo temperature measurement | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TST41N-MRDD82HA4P |  |  | 4010 | MEAS_ANA | TT006 | Field IO
810 | [27 empty] | Measurement | BB1TT652 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
811 |  | BB1 | TT | 653 | BB1TT653 | Fuel pocket temperature | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TST41N-MRDD82HA4P |  |  | 4010 | MEAS_ANA | TT006 | Field IO
812 | [27 empty] | Measurement | BB1TT653 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
813 |  | BB1 | IV | 650 | BB1IV650 | Slide gate valve |  |  |  | 2.2 | 4.2 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor added | 1
814 | [27 empty] | Running FWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
815 | [27 empty] | Running BWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
816 | [27 empty] | MCC Fault | BB1EM704 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
817 | [27 empty] | Local FWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
818 | [27 empty] | Local BWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
819 | [27 empty] | Local mode switch | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
820 | [27 empty] | Run command FWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
821 | [27 empty] | Run command BWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
822 | [27 empty] | Current | BB1EM704 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
823 |  | BB1 | GS | 655 | BB1GS655 | Slide gate valve open limit switch | [33 empty] | 1 | [19 empty] | Telemecanique | XSAV-11801 |  |  | 4010 | MEAS_BIN |  | Field IO |  | Instrument added | 1
824 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
825 |  | BB1 | GS | 656 | BB1GS656 | Slide gate valve close limit switch | [33 empty] | 1 | [19 empty] | Telemecanique | XSAV-11801 |  |  | 4010 | MEAS_BIN |  | Field IO |  | Instrument added | 1
826 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
827 |  | BB1 | HC | 601 | BB1HC601 | Crane feed |  | 16 A breaker |  |  |  |  | 415 | [55 empty] | Crane added | 1
828 |  | BB1 | FL | 650 | BB1FL650 | Fuel silo dust filter control box feed |  | 10 A breaker |  |  |  |  | 240 | [27 empty] | 1 | [22 empty] | 4010 | MCCB_1ph |  |  |  | Voltage level added | 1
831 | [27 empty] | Cleaning on | BB1FF650 | [11 empty] | X | [16 empty] | Pot.free | [10 empty] | Signal added | 1
829 |  | BB1 | EM | 651 | BB1EM651 | Fuel silo dust filter fan | [41 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIR_BUS
830 | [27 empty] | Running | BB1FF650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
831 | [27 empty] | MCC Fault | BB1FF650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
832 | [27 empty] | Run command | BB1FF650 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
833 | [27 empty] | Current | BB1FF650 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
834 |  | BB1 | EM | 652 | BB1EM652 | Rotating fuel spreader |  |  |  | 0.75 | 1.7 | 1500 | 415 | [26 empty] | 2 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIRH_BUS |  |  |  | Size, current and voltage | 1
835 | [27 empty] | Running | BB1SD650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
836 | [27 empty] | MCC Fault | BB1SD650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
837 | [27 empty] | Local run command | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
838 | [27 empty] | Local mode switch | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
839 | [27 empty] | Run command | BB1SD650 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
840 | [27 empty] | Current | BB1SD650 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
841 |  | BB1 | EM | 662 | BB1EM662 | Fuel silo screw discharger |  |  |  | 22 | 39,5 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
842 | [27 empty] | Running FWD | BB1FD662 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
843 | [27 empty] | Running BWD | BB1FD662 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
844 | [27 empty] | MCC Fault | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
845 | [27 empty] | Safety switch | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
846 | [27 empty] | VFD Alarm | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
847 | [27 empty] | Local FWD command | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
848 | [27 empty] | Local BWD command | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
849 | [27 empty] | Local mode switch | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
850 | [27 empty] | Run command FWD | BB1FD662 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
851 | [27 empty] | Run command BWD | BB1FD662 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
852 | [27 empty] | Current | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
853 | [27 empty] | Speed reference | BB1FD662 | [21 empty] | X | [13 empty] | FRQ_REVH
854 | [27 empty] | Actual speed | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
855 | [27 empty] | Torque | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
856 | [27 empty] | RPM | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
857 |  | BB1 | EM | 650 | BB1EM650 | Slewing motor for screw |  |  |  | 2.2 | 4.2 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
858 | [27 empty] | Running FWD | BB1EM650 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
859 | [27 empty] | Running BWD | BB1EM650 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
860 | [27 empty] | MCC Fault | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
861 | [27 empty] | Safety switch | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
862 | [27 empty] | VFD Alarm | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
863 | [27 empty] | Local FWD command | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
864 | [27 empty] | Local BWD command | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
865 | [27 empty] | Local mode switch | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
866 | [27 empty] | Run command FWD | BB1EM650 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
867 | [27 empty] | Run command BWD | BB1EM650 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
868 | [27 empty] | Current | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
869 | [27 empty] | Speed reference | BB1EM650 | [21 empty] | X | [13 empty] | FRQ_REVH
870 | [27 empty] | Actual speed | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
871 | [27 empty] | Torque | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
872 | [27 empty] | RPM | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
873 |  | BB1 | EM | 660 | BB1EM660 | Cooling fan for slewing motor |  |  |  | 0.09 |  |  | 240 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor added | 1
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
877 |  | BB1 | EM | 654 | BB1EM654 | Lubrication unit |  | Fuse size C6A |  | 0.2 | 0.8 |  | 240 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Tag chanhed | 3
878 | [27 empty] | Running | BB1PU650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
879 | [27 empty] | MCC Fault | BB1PU650 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
880 | [27 empty] | Run command | BB1PU650 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
881 |  | BB1 | LS | 661 | BB1LS661 | Lubrication alarm screw discharger | [33 empty] | 1 | [19 empty] | SKF | KFGS | LAITEX |  | 4010 | MEAS_BIN |  | Field IO |  | Tag changed | 3
882 | [27 empty] | Binary state | BB1QA650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
883 |  | BB1 | EH | 662 | BB1EH662 | Heater for slipring unit |  |  |  | 0.4 | 1.7 |  | 240 | [26 empty] | 1 | [23 empty] | 4010 | MCCB_1ph |  |  |  | Details | 1
884 |  | BB1 | EM | 663 | BB1EM663 | Fuel silo cross conveyor |  |  |  | 4 | 7.6 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
885 | [27 empty] | Running FWD | BB1FD663 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
886 | [27 empty] | Running BWD | BB1FD663 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
887 | [27 empty] | MCC Fault | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
888 | [27 empty] | Safety switch | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
889 | [27 empty] | VFD Alarm | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
890 | [27 empty] | Local FWD command | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
891 | [27 empty] | Local BWD command | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
892 | [27 empty] | Local mode switch | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
893 | [27 empty] | Run command FWD | BB1FD663 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
894 | [27 empty] | Run command BWD | BB1FD663 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
895 | [27 empty] | Current | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
896 | [27 empty] | Speed reference | BB1FD663 | [21 empty] | X | [13 empty] | FRQ_REVH
897 | [27 empty] | Actual speed | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
898 | [27 empty] | Torque | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
899 | [27 empty] | RPM | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
900 |  | BB1 | EM | 664 | BB1EM664 | Fuel feeding screw 1 |  |  |  | 5.5 | 10 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
901 | [27 empty] | Running FWD | BB1FD664 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
902 | [27 empty] | Running BWD | BB1FD664 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
903 | [27 empty] | MCC Fault | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
904 | [27 empty] | Safety switch | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
905 | [27 empty] | VFD Alarm | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
906 | [27 empty] | Local FWD command | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
907 | [27 empty] | Local BWD command | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
908 | [27 empty] | Local mode switch | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
909 | [27 empty] | Run command FWD | BB1FD664 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
910 | [27 empty] | Run command BWD | BB1FD664 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
911 | [27 empty] | Current | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
912 | [27 empty] | Speed reference | BB1FD664 | [21 empty] | X | [13 empty] | FRQ_REVH
913 | [27 empty] | Actual speed | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
914 | [27 empty] | Torque | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
915 | [27 empty] | RPM | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
916 |  | BB1 | EM | 653 | BB1EM653 | Cooling fan fuel feeding screw 1 |  |  |  | 0.15 | 0.33 |  | 415 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor details | 1
917 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
918 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
919 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
920 |  | BB1 | EM | 665 | BB1EM665 | Fuel feeding screw 2 |  |  |  | 5.5 | 10 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
921 | [27 empty] | Running FWD | BB1FD665 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
922 | [27 empty] | Running BWD | BB1FD665 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
923 | [27 empty] | MCC Fault | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
924 | [27 empty] | Safety switch | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
925 | [27 empty] | VFD Alarm | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
926 | [27 empty] | Local FWD command | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
927 | [27 empty] | Local BWD command | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
928 | [27 empty] | Local mode switch | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
929 | [27 empty] | Run command FWD | BB1FD665 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
930 | [27 empty] | Run command BWD | BB1FD665 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
931 | [27 empty] | Current | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
932 | [27 empty] | Speed reference | BB1FD665 | [21 empty] | X | [13 empty] | FRQ_REVH
933 | [27 empty] | Actual speed | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
934 | [27 empty] | Torque | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
935 | [27 empty] | RPM | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
936 |  | BB1 | EM | 655 | BB1EM655 | Cooling fan fuel feeding screw 2 |  |  |  | 0.15 | 0.33 |  | 415 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor details | 1
937 | [27 empty] | Running | BB1FF654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
938 | [27 empty] | MCC Fault | BB1FF654 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
939 | [27 empty] | Run command | BB1FF654 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
940 |  | BB1 | EM | 657 | BB1EM657 | Fuel feeding rotary valve 1 |  |  |  | 7.5 | 13.7 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor details | 1
941 | [27 empty] | Running FWD | BB1RV650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
942 | [27 empty] | Running BWD | BB1RV650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
943 | [27 empty] | MCC Fault | BB1RV650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
944 | [27 empty] | Local FWD command | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
945 | [27 empty] | Local BWD command | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
946 | [27 empty] | Local mode switch | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
947 | [27 empty] | Run command FWD | BB1RV650 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
948 | [27 empty] | Run command BWD | BB1RV650 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
949 | [27 empty] | Current | BB1RV650 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
950 |  | BB1 | EM | 656 | BB1EM656 | Fuel feeding rotary valve 2 |  |  |  | 7.5 | 13.7 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor details | 1
951 | [27 empty] | Running FWD | BB1RV651 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
952 | [27 empty] | Running BWD | BB1RV651 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
953 | [27 empty] | MCC Fault | BB1RV651 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
954 | [27 empty] | Local FWD command | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
955 | [27 empty] | Local BWD command | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
956 | [27 empty] | Local mode switch | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
957 | [27 empty] | Run command FWD | BB1RV651 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
958 | [27 empty] | Run command BWD | BB1RV651 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
959 | [27 empty] | Current | BB1RV651 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
960 |  | BB1 | GS | 802 | BB1GS802 | Bottom ash valve limit switch | [33 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | XS002/XS004 | Field IO
961 | [27 empty] | Binary state | BB1GS802 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
962 |  | BB1 | GS | 803 | BB1GS803 | Bottom ash dropping chute closing device limit switch | [33 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | XS002/XS004 | Field IO
963 | [27 empty] | Binary state | BB1GS803 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
964 |  | BB1 | LS | 852 | BB1LS852 | Fly ash container level switch |  | harting connector |  |  |  |  | 24 VDC | [26 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | LS001 | Field IO
965 | [27 empty] | Binary state | BB1LS852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
966 |  | BB1 | PT | 552 | BB1PT552 | ESP inlet pressure transmitter |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA | PT002
967 | [27 empty] | Measurement | BB1PT552 | [12 empty] | X | [22 empty] | MEAS_ANA
968 |  | BB1 | PT | 553 | BB1PT553 | ESP outlet pressure transmitter |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA | PT002
969 | [27 empty] | Measurement | BB1PT553 | [12 empty] | X | [22 empty] | MEAS_ANA
970 |  | BB1 | QT | 554 | BB1QT554 | Opacity after ESP | [6 empty] | 24 VDC | [23 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | QT001 | Field IO
971 | [27 empty] | Measurement | BB1QT554 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
972 |  | BB1 | ST | 805 | BB1ST805 | Heated ESP collection screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
973 | [27 empty] | Binary state | BB1ST805 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
974 |  | BB1 | ST | 808 | BB1ST808 | ESP hopper 2 screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
975 | [27 empty] | Binary state | BB1ST808 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
976 |  | BB1 | ST | 809 | BB1ST809 | ESP hopper 1 screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
977 | [27 empty] | Binary state | BB1ST809 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
978 |  | BB1 | ST | 804 | BB1ST804 | ESP Rotary valve rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
979 | [27 empty] | Binary state | BB1ST804 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
980 |  | BB1 | TT | 553 | BB1TT553 | Flue gas fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
980 |  | BB1 | TT | 557 | BB1TT557 | Flue gas fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO |  | signal added | 3
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
980 |  | BB1 | TT | 558 | BB1TT558 | Flue gas fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO |  | signal added | 3
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
982 |  | BB1 | TT | 554 | BB1TT554 | Flue gas fan bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
983 | [27 empty] | Measurement | BB1TT554 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
984 |  | BB1 | TT | 555 | BB1TT555 | Flue gas fan bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
985 | [27 empty] | Measurement | BB1TT555 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
986 |  | BB1 | TT | 556 | BB1TT556 | Flue gas temperature before stack | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4011 | MEAS_ANA | TT003 | Field IO
987 | [27 empty] | Measurement | BB1TT556 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
988 |  | BB1 | TT | 850 | BB1TT850 | ESP Ash hopper 1 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
989 | [27 empty] | Measurement | BB1TT850 | [12 empty] | X | [22 empty] | MEAS_ANA
990 |  | BB1 | TT | 851 | BB1TT851 | ESP Ash hopper 2 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
991 | [27 empty] | Measurement | BB1TT851 | [12 empty] | X | [22 empty] | MEAS_ANA
992 |  | BB1 | EH | 808 | BB1EH808 | ESP Ash hopper 2 heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
993 | [27 empty] | RCBO fault | BB1EH808 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
994 | [27 empty] | On command | BB1EH808 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
995 |  | BB1 | EH | 809 | BB1EH809 | ESP Ash hopper 1 heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
996 | [27 empty] | RCBO fault | BB1EH809 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
997 | [27 empty] | On command | BB1EH809 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
998 |  | BB1 | TS | 808 | BB1TS808 | ESP Ash hopper 2 overheat thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS001
999 | [27 empty] | Binary state | BB1TS808 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1000 |  | BB1 | TS | 809 | BB1TS809 | ESP Ash hopper 1 overheat thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS001
1001 | [27 empty] | Binary state | BB1TS809 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1002 |  | BB1 | TS | 501 | BB1TS501 | ESP Insulator 1 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1003 | [27 empty] | Measurement | BB1TS501 | [12 empty] | X | [22 empty] | MEAS_ANA
1004 |  | BB1 | TS | 508 | BB1TS508 | ESP Insulator 2 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1005 | [27 empty] | Measurement | BB1TS508 | [12 empty] | X | [22 empty] | MEAS_ANA
1006 |  | BB1 | TT | 552 | BB1TT552 | Flue gas temperature before ESP |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1007 | [27 empty] | Measurement | BB1TT552 | [12 empty] | X | [22 empty] | MEAS_ANA
1008 |  | BB1 | EM | 509 | BB1EM509 | ESP DE rapping drive 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1009 | [27 empty] | Running | BB1EM509 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1010 | [27 empty] | MCC Fault | BB1EM509 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1011 | [27 empty] | Run command | BB1EM509 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1012 |  | BB1 | EM | 510 | BB1EM510 | ESP CE rapping drive 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1013 | [27 empty] | Running | BB1EM510 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1014 | [27 empty] | MCC Fault | BB1EM510 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1015 | [27 empty] | Run command | BB1EM510 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1016 |  | BB1 | EM | 511 | BB1EM511 | ESP DE rapping drive 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1017 | [27 empty] | Running | BB1EM511 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1018 | [27 empty] | MCC Fault | BB1EM511 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1019 | [27 empty] | Run command | BB1EM511 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1020 |  | BB1 | EM | 512 | BB1EM512 | ESP CE rapping drive 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1021 | [27 empty] | Running | BB1EM512 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1022 | [27 empty] | MCC Fault | BB1EM512 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1023 | [27 empty] | Run command | BB1EM512 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1024 |  | BB1 | EH | 501 | BB1EH501 | ESP insulators heating chamber 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1025 | [27 empty] | Running | BB1EH501 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1026 | [27 empty] | MCC Fault | BB1EH501 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1027 | [27 empty] | Run command | BB1EH501 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1028 |  | BB1 | EH | 505 | BB1EH505 | ESP insulators heating chamber 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1029 | [27 empty] | Running | BB1EH505 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1030 | [27 empty] | MCC Fault | BB1EH505 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1031 | [27 empty] | Run command | BB1EH505 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1032 |  | BB1 | IE | 501 | BB1IE501 | ESP HV Trafo 1 |  | Supply from ESP MCC | [55 empty] | 4011 | OESA_3ph
1033 |  | BB1 | IE | 502 | BB1IE502 | ESP HV Trafo 2 |  | Supply from ESP MCC | [55 empty] | 4011 | OESA_3ph
1034 |  | BB1 | FG | 300 | BB1FG300 | ESP hardwired signals to/from Boiler PLC | [33 empty] | 8 | 6 | [22 empty] | 4011 | ESP_DI_DO
1035 | [27 empty] | Collective Alarm | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1036 | [27 empty] | Collective Warning | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1037 | [27 empty] | ESP in Standby | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1038 | [27 empty] | ESP in Operation | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1039 | [27 empty] | ESP spare DI1 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1040 | [27 empty] | ESP spare DI2 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1041 | [27 empty] | ESP spare DI3 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1042 | [27 empty] | ESP spare DI4 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1043 | [27 empty] | ESP External release filter | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1044 | [27 empty] | ESP spare DO1 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1045 | [27 empty] | ESP spare DO2 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1046 | [27 empty] | ESP spare DO3 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1047 | [27 empty] | ESP spare DO4 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1048 | [27 empty] | ESP spare DO5 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1049 |  | BB1 | EM | 809 | BB1EM809 | ESP ash hopper 1 screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1050 | [27 empty] | Running FWD | BB1EM809 | [10 empty] | X | [24 empty] | DOL_REVH
1051 | [27 empty] | Running BWD | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1052 | [27 empty] | MCC Fault | BB1EM809 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1053 | [27 empty] | Local FWD command | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1054 | [27 empty] | Local BWD command | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1055 | [27 empty] | Local mode switch | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1056 | [27 empty] | Run command FWD | BB1EM809 | [11 empty] | X | [23 empty] | DOL_REVH
1057 | [27 empty] | Run command BWD | BB1EM809 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1058 |  | BB1 | EM | 808 | BB1EM808 | ESP ash hopper 2 screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1059 | [27 empty] | Running FWD | BB1EM808 | [10 empty] | X | [24 empty] | DOL_REVH
1060 | [27 empty] | Running BWD | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1061 | [27 empty] | MCC Fault | BB1EM808 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1062 | [27 empty] | Local FWD command | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1063 | [27 empty] | Local BWD command | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1064 | [27 empty] | Local mode switch | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1065 | [27 empty] | Run command FWD | BB1EM808 | [11 empty] | X | [23 empty] | DOL_REVH
1066 | [27 empty] | Run command BWD | BB1EM808 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1067 |  | BB1 | EM | 805 | BB1EM805 | ESP collection screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1068 | [27 empty] | Running FWD | BB1EM805 | [10 empty] | X | [24 empty] | DOL_REVH
1069 | [27 empty] | Running BWD | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1070 | [27 empty] | MCC Fault | BB1EM805 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1071 | [27 empty] | Local FWD command | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1072 | [27 empty] | Local BWD command | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1073 | [27 empty] | Local mode switch | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1074 | [27 empty] | Run command FWD | BB1EM805 | [11 empty] | X | [23 empty] | DOL_REVH
1075 | [27 empty] | Run command BWD | BB1EM805 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1076 |  | BB1 | EH | 805 | BB1EH805 | ESP collection screw heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1077 | [27 empty] | RCBO fault | BB1EH805 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1078 | [27 empty] | On command | BB1EH805 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1079 |  | BB1 | TS | 805 | BB1TS805 | ESP collection screw heating thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN
1080 | [27 empty] | Binary state | BB1TS805 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1081 |  | BB1 | EM | 804 | BB1EM804 | ESP Rotary valve |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1082 | [27 empty] | Running FWD | BB1EM804 | [10 empty] | X | [24 empty] | DOL_REVH
1083 | [27 empty] | Running BWD | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1084 | [27 empty] | MCC Fault | BB1EM804 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1085 | [27 empty] | Local FWD command | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1086 | [27 empty] | Local BWD command | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1087 | [27 empty] | Local mode switch | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1088 | [27 empty] | Run command FWD | BB1EM804 | [11 empty] | X | [23 empty] | DOL_REVH
1089 | [27 empty] | Run command BWD | BB1EM804 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1090 |  | BB1 | EH | 804 | BB1EH804 | ESP Rotary valve heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1091 | [27 empty] | RCBO fault | BB1EH804 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1092 | [27 empty] | On command | BB1EH804 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1093 |  | BB1 | TS | 804 | BB1TS804 | ESP Rotary valve heating thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN
1094 | [27 empty] | Binary state | BB1TS804 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1095 |  | BB1 | EM | 815 | BB1EM815 | Fly ash container screw | [41 empty] | 3 | 2 | 1 | [13 empty] | 4011 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1101 |  | BB1 | EM | 550 | BB1EM550 | Flue gas fan |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4011 | FRQ_DIR |  |  |  | Size and voltage | 1
1102 | [27 empty] | Running | BB1FF550 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
1103 | [27 empty] | MCC Fault | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1104 | [27 empty] | Safety switch | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1105 | [27 empty] | VFD Alarm | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1106 | [27 empty] | Run command | BB1FF550 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
1107 | [27 empty] | Current | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1108 | [27 empty] | Speed reference | BB1FF550 | [21 empty] | X | [13 empty] | FRQ_DIR
1109 | [27 empty] | Actual speed | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1110 | [27 empty] | Torque | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1111 | [27 empty] | RPM | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1112 |  | BB1 | SI | 550 | BB1SI550 | Flue gas fan safety interlock | [38 empty] | 1 | [18 empty] | 4011 | FAN_SRS_DO
1113 | [27 empty] | Safety interlock | BB1SI550 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 560 | BB1SI560 | Flue gas fan run status SRS | [37 empty] | 1 | [19 empty] | 4011 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 550 | BB1ST550 | Flue gas fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
458 |  | BB1 |  |  | BB1 | Flue gas fan heating |  | RCBO + Contactor |  |  |  |  | 240 | [27 empty] | 1 | [22 empty] | 4011 |  |  |  |  | Heater added | 3
459 | [27 empty] | Heater On control | BB1SI401 | [11 empty] | X | [27 empty] | Heater added | 3
1114 |  | BB1 | CV | 405 | BB1CV405 | Bottom ash valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1115 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV405 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1116 |  | BB1 | GS | 855 | BB1GS855 | Bottom ash valve solenoid valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1117 | [27 empty] | Binary state | BB1GS855 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1118 |  | BB1 | GS | 856 | BB1GS856 | Bottom ash valve solenoid valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1119 | [27 empty] | Binary state | BB1GS856 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1120 |  | BB1 | CV | 406 | BB1CV406 | Bottom ash valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1121 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV406 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1122 |  | BB1 | GS | 857 | BB1GS857 | Bottom ash valve solenoid valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1123 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1124 |  | BB1 | GS | 858 | BB1GS858 | Bottom ash valve solenoid valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1125 | [27 empty] | Binary state | BB1GS858 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1126 |  | BB1 | CV | 412 | BB1CV412 | Bottom ash sieve bypass solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1127 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV412 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1128 |  | BB1 | GS | 850 | BB1GS850 | Bottom ash sieve bypass valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1129 | [27 empty] | Binary state | BB1GS850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1130 |  | BB1 | GS | 851 | BB1GS851 | Bottom ash sieve bypass valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1131 | [27 empty] | Binary state | BB1GS851 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1132 |  | BB1 | CV | 413 | BB1CV413 | Control valve of pneumatic transmitter damper |  | Pneuplan PLC |  |  | Pneuplan PLC |  | 24 | [27 empty] | 2 | [21 empty] | Pneuplan | 4012 | BIN_VLV_2DO | AA004 | Field IO
1133 | [27 empty] | Open command | BB1CV413 | [11 empty] | X | [23 empty] | BIN_VLV_2DO |  | Field IO
1134 | [27 empty] | Close command | BB1CV413 | [11 empty] | X | [23 empty] | BIN_VLV_2DO |  | Field IO
1135 |  | BB1 | CV | 414 | BB1CV414 | Work air to pneumatic transmitter pneumatic valve |  | Pneuplan PLC |  |  | Pneuplan PLC |  | 24 | [27 empty] | 1 | [21 empty] | Pneuplan | 4012 | BIN_VLV | AA004 | Field IO
1136 | [27 empty] | Control command | BB1CV414 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1137 |  | BB1 | FS | 003 | BB1FS003 | Bottom ash cooling flow switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | FS001 | Field IO
1138 | [27 empty] | Binary state | BB1FS003 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1139 |  | BB1 | SV | 405 | BB1SV405 | Sand filling valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA003 | Field IO
1140 | [27 empty] | Control command | BB1SV405 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1141 |  | BB1 | GS | 801 | BB1GS801 | Sand filling valve position open limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | AA005 | Field IO
1142 | [27 empty] | Binary state | BB1GS801 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1143 |  | BB1 | GS | 800 | BB1GS800 | Sand filling valve position close limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS001 | Field IO
1144 | [27 empty] | Binary state | BB1GS800 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1145 |  | BB1 | GS | 854 | BB1GS854 | Bottom ash dropping chute limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO |  | Tag changed | 3
1146 | [27 empty] | Binary state | BB1GS852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1147 |  | BB1 | GS | 853 | BB1GS853 | Bottom ash dropping chute closing device limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO
1148 | [27 empty] | Binary state | BB1GS853 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1149 |  | BB1 | GS | 859 | BB1GS859 | Bottom ash to container in place |  | Harting connector (jumper in container side..> DI=1 connector in place) | [31 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO |  | Tag changed | 3
1150 | [27 empty] | Binary state | BB1GS854 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1151 |  | BB1 | LS | 850 | BB1LS850 | Bottom ash container level switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | LS001 | Field IO
1152 | [27 empty] | Binary state | BB1LS850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1153 |  | BB1 | LS | 851 | BB1LS851 | Bottom ash container level switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | LS001 | Field IO
1154 | [27 empty] | Binary state | BB1LS851 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1155 |  | BB1 | LT | 800 | BB1LT800 | Recycled bed material hopper level switch |  | Pneuplan PLC |  |  | Pneuplan PLC | [30 empty] | 1 | [20 empty] | Pneuplan | 4012 | MEAS_ANA |  | Field IO
1156 | [27 empty] | Measurement | BB1LT800 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1157 |  | BB1 | LT | 802 | BB1LT802 | Sand silo level measurement | [6 empty] | 24 VDC | [23 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4012 | MEAS_ANA | LT003 | Field IO
1158 | [27 empty] | Measurement | BB1LT802 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1159 |  | BB1 | PT | 009 | BB1PT009 | Cooling water pressure before pump | [30 empty] | 0 | 6 | bar(g) |  |  | 1 | [13 empty] | Pressure |  |  |  | E+H | PMP51-AA22IA1PGJGCJA1+Z1 | G1/2 |  | 4012 | MEAS_ANA | PT001.1 | Field IO
1160 | [27 empty] | Measurement | BB1PT009 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1161 |  | BB1 | PT | 800 | BB1PT800 | Recycled bed material damper pressure switch |  | Pneuplan PLC |  |  | Pneuplan PLC | [28 empty] | 1 | [22 empty] | Pneuplan | 4012 | MEAS_BIN |  | Field IO
1162 | [27 empty] | Binary state | BB1PT800 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1153 |  | BB1 | EM | 856 | BB1EM856 | Purified sand screw conveyor | [33 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor added | 2
1154 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1155 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1156 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1157 | [27 empty] | Local FWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1158 | [27 empty] | Local BWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1159 | [27 empty] | Local mode switch | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1160 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1161 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1162 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1151 |  | BB1 | ST | 856 | BB1ST856 | Purified sand screw conveyor rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument added | 2
1152 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO |  | Instrument added | 2
1163 |  | BB1 | EM | 852 | BB1EM852 | Bottom ash conveyor |  |  |  | 2.2 | 4.2 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4012 | FRQ_REVH |  |  |  | Tag changed | 2
1164 | [27 empty] | Running FWD | BB1EM850 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1165 | [27 empty] | Running BWD | BB1EM850 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1166 | [27 empty] | MCC Fault | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1167 | [27 empty] | Safety switch | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1168 | [27 empty] | VFD Alarm | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1169 | [27 empty] | Local FWD command | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1170 | [27 empty] | Local BWD command | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1171 | [27 empty] | Local mode switch | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1172 | [27 empty] | Run command FWD | BB1EM850 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1173 | [27 empty] | Run command BWD | BB1EM850 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1174 | [27 empty] | Current | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1175 | [27 empty] | Speed reference | BB1EM850 | [21 empty] | X | [13 empty] | FRQ_REVH
1176 | [27 empty] | Actual speed | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1177 | [27 empty] | Torque | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1178 | [27 empty] | RPM | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1179 |  | BB1 | ST | 850 | BB1ST850 | Bottom ash conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemecanique | XSAV-11801 |  |  | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
1180 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1179 |  | BB1 | GS | 852 | BB1GS852 | Bottom ash conveyor blockage detector | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemecanique | XS530B1MAL2 |  |  | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument added | 1
1180 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
741 |  | BB1 | IJ | 004 | BB1IJ004 | Bottom ash conveyor Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4012 | ALM_HORN |  | Field IO |  | Instrument added | 2
742 | [27 empty] | Command | BB1IJ001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
1181 |  | BB1 | EM | 850 | BB1EM850 | 2nd pass fly ash rotary valve |  |  |  |  | 0,37 |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor details | 1
1182 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1183 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1184 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1185 | [27 empty] | Local FWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1186 | [27 empty] | Local BWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1187 | [27 empty] | Local mode switch | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1188 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1189 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1190 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1191 |  | BB1 | ST | 852 | BB1ST852 | 2nd pass fly ash rotary valve rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO
1192 | [27 empty] | Binary state | BB1ST852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1193 |  | BB1 | EM | 851 | BB1EM851 | 3rd pass fly ash rotary valve |  |  |  |  | 0,37 |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor details | 1
1194 | [27 empty] | Running FWD | BB1EM851 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1195 | [27 empty] | Running BWD | BB1EM851 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1196 | [27 empty] | MCC Fault | BB1EM851 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1197 | [27 empty] | Local FWD command | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1198 | [27 empty] | Local BWD command | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1199 | [27 empty] | Local mode switch | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1200 | [27 empty] | Run command FWD | BB1EM851 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1201 | [27 empty] | Run command BWD | BB1EM851 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1202 | [27 empty] | Current | BB1EM851 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1203 |  | BB1 | ST | 853 | BB1ST853 | 3rd pass fly ash rotary valve rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO
1204 | [27 empty] | Binary state | BB1ST853 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1205 |  | BB1 | SV | 401 | BB1SV401 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA005 | Field IO
1206 | [27 empty] | Control command | BB1SV401 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1207 |  | BB1 | SV | 402 | BB1SV402 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA005 | Field IO
1208 | [27 empty] | Control command | BB1SV402 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1209 |  | BB1 | SV | 403 | BB1SV403 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 0 | [22 empty] | 4012 | BIN_VLV | AA005 |  |  | Removed | 1
1210 | [27 empty] | Control command | BB1SV403 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  |  |  | Removed | 1
1211 |  | BB1 | SV | 404 | BB1SV404 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 0 | [22 empty] | 4012 | BIN_VLV | AA005 |  |  | Removed | 1
1212 | [27 empty] | Control command | BB1SV404 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  |  |  | Removed | 1
1213 |  | BB1 | TT | 031 | BB1TT031 | Cooling water temperature after bottom ash conveyor | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4012 | MEAS_ANA | TT001 | Field IO
1214 | [27 empty] | Measurement | BB1TT031 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1215 |  | BB1 | EM | 014 | BB1EM008 | Conveyor cooling pump |  |  |  | 1,1 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [12 empty] | Grundfos | 4012 | DOL_DIR_BUS |  |  |  | Motor size changed | 3
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1220 |  | BB1 | EM | 855 | BB1EM855 | Ash container screw |  |  |  | 1,5 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4012 | DOL_REV_BUS |  |  |  | Motor details | 1
1221 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1222 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1224 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS
1225 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS
1227 |  | BB1 | EM | 018 | BB1EM009 | Bottom ash conveyor heat exchanger fan |  | preliminary 6x0,72 kW, 1.42 A |  | 7,5 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4012 | DOL_DIR_BUS |  |  |  | Tag changed | 2
1228 | [27 empty] | Running | BB1FF009 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1229 | [27 empty] | MCC Fault | BB1FF009 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1230 | [27 empty] | Run command | BB1FF009 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1231 | [27 empty] | Current | BB1FF009 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1232 |  | BB1 | FM | 001 | BB1FM001 | Bottom ash sieve feed |  | supply fuse 16A |  | 1,4 |  |  | 415 | [26 empty] | 5 | 1 | [22 empty] | 4012 | OESA_3ph |  |  |  | Details | 1
1236 | [27 empty] | Emergency stop | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1237 | [7 empty] | ask preliminary drawings from KPA | [19 empty] | Running | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
[28 empty] | manual/auto | [11 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1238 | [27 empty] | Thermistor fault | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1239 | [27 empty] | Voltage OK | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1241 | [27 empty] | Start/stop | BB1BU500 | [11 empty] | X | [16 empty] | pot.free | [6 empty] | OESA_3ph |  |  |  | signals added | 1
1233 |  | BB1 | HC | 601 | BB1HC601 | Electrical hoist feed |  |  |  |  | 2,8 |  | 415 | [50 empty] | 4012 | OESA_3ph
1234 |  | BB1 | TN | ??? | BB1TN??? | Sand transmitter 230 Vac feed | [33 empty] | 1 | [23 empty] | 4012 | MCCB_1ph
1235 |  | BB1 | BU | 500 | BB1BU500 | Burner signals | [33 empty] | 5 | 5 | 2 | 2 |  |  |  |  | 6 | 5 | 2 | 2 | [12 empty] | 4013 | BURNER
1236 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1237 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1238 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1239 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1240 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1241 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1242 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1243 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1244 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1245 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1246 | [27 empty] | AI reservation | BB1BU500 | [12 empty] | X | [22 empty] | BURNER
1247 | [27 empty] | AI reservation | BB1BU500 | [12 empty] | X | [22 empty] | BURNER
1248 | [27 empty] | AO reservation | BB1BU500 | [13 empty] | X | [21 empty] | BURNER
1249 | [27 empty] | AO reservation | BB1BU500 | [13 empty] | X | [21 empty] | BURNER
1250 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1251 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1252 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1253 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1254 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1255 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1256 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1257 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1258 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1259 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1260 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1261 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1262 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1263 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1264 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1265 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1266 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1267 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1268 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1269 |  | BB1 | EM | 402 | BB1EM402 | Compressor 1 |  | Preliminary size |  | 30 |  |  | 415 | [26 empty] | 3 | 2 | [22 empty] | 4014 | COMPR |  | Field IO |  | Motor size and tag changed | 3
1270 | [27 empty] | Fault | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1271 | [27 empty] | Running | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1272 | [27 empty] | Reserve | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1273 | [27 empty] | Remote run command | BB1EM400 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1274 | [27 empty] | Fault acknowledge | BB1EM400 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1275 |  | BB1 | EM | 403 | BB1EM403 | Compressor 2 |  | Preliminary size |  | 30 |  |  | 415 | [26 empty] | 3 | 2 | [22 empty] | 4014 | COMPR |  | Field IO |  | Motor size and tag changed | 3
1276 | [27 empty] | Fault | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1277 | [27 empty] | Running | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1278 | [27 empty] | Reserve | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1279 | [27 empty] | Remote run command | BB1EM402 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1280 | [27 empty] | Fault acknowledge | BB1EM402 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1281 |  | BB1 | DR | 400 | BB1DR400 | Compressor 1 dryer |  |  |  | 4 |  |  | 415 | [26 empty] | 1 | [23 empty] | 4014 | MCCB_1ph |  |  |  | motor details | 1
1282 |  | BB1 | DR | 401 | BB1DR401 | Compressor 2 dryer |  |  |  | 4 |  |  | 415 | [26 empty] | 1 | [23 empty] | 4014 | MCCB_1ph |  |  |  | motor details | 1
1283 |  | BB1 | PT | 478 | BB1PT478 | Instrument air pressure | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4014 | MEAS_ANA | PT002 | Field IO
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1283 |  | BB1 | PT | 402 | BB1PT402 | Instrument air pressure after dryer | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4014 | MEAS_ANA | PT002 | Field IO |  | Instrument added | 3
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
1283 |  | BB1 | TT | 430 | BB1TT430 | Instrument air tank temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [19 empty] | G1/2 |  | 4014 | MEAS_ANA | TT003 | Field IO |  | Instrument added | 3
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
1285 |  | BB1 | GS | 020 | BB1GS020 | Emergency shower use switch | [33 empty] | 1 | [23 empty] | 4014 | MEAS_BIN | XS001 | Field IO
1286 | [27 empty] | Binary state | BB1GS020 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1287 |  | BB1 | TT | 401 | BB1TT401 | Boiler room upper part temperature | [35 empty] | 1 | [17 empty] | E+H | TST434-J1A3BP | Wall mount |  | 4014 | MEAS_ANA | TT007 | Field IO
1288 | [27 empty] | Measurement | BB1TT401 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1289 |  | BB1 | EM | 401 | BB1EM401 | Exhaust fan 1 |  |  |  | 1,9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1290 | [27 empty] | Running FWD | BB1EM401 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1291 | [27 empty] | Running BWD | BB1EM401 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1292 | [27 empty] | MCC Fault | BB1EM401 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1293 | [27 empty] | Run command FWD | BB1EM401 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1294 | [27 empty] | Run command BWD | BB1EM401 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1295 | [27 empty] | Current | BB1EM401 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1296 |  | BB1 | EM | 402 | BB1EM402 | Exhaust fan 2 |  |  |  | 1,9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1297 | [27 empty] | Running FWD | BB1EM402 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1298 | [27 empty] | Running BWD | BB1EM402 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1299 | [27 empty] | MCC Fault | BB1EM402 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1300 | [27 empty] | Run command FWD | BB1EM402 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1301 | [27 empty] | Run command BWD | BB1EM402 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1302 | [27 empty] | Current | BB1EM402 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1303 |  | BB1 | EM | 403 | BB1EM403 | Exhaust fan 3 |  |  |  | 1,9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1304 | [27 empty] | Running FWD | BB1EM403 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1305 | [27 empty] | Running BWD | BB1EM403 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1306 | [27 empty] | MCC Fault | BB1EM403 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1307 | [27 empty] | Run command FWD | BB1EM403 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1308 | [27 empty] | Run command BWD | BB1EM403 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1309 | [27 empty] | Current | BB1EM403 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1310 |  | BB1 | EM | 405 | BB1EM405 | Air intake grill 1 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1311 |  |  |  |  | BB1GS401 | [22 empty] | Open limit switch | BB1EM405 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1312 | [27 empty] | Open command | BB1EM405 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1313 |  | BB1 | EM | 406 | BB1EM406 | Air intake grill 2 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1314 |  |  |  |  | BB1GS412 | [22 empty] | Open limit switch | BB1EM406 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1315 | [27 empty] | Open command | BB1EM406 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1316 |  | BB1 | EM | 407 | BB1EM407 | Air intake grill 3 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1317 |  |  |  |  | BB1GS413 | [22 empty] | Open limit switch | BB1EM407 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1318 | [27 empty] | Open command | BB1EM407 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1319 |  | BB1 | EM | 408 | BB1EM408 | Boiler house heater 1 |  |  |  | 15 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4014 | DOL_DIR_BUS |  |  |  | Motor feed type changed | 2
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1323 |  | BB1 | EM | 409 | BB1EM409 | Boiler house heater 2 |  |  |  | 15 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4014 | DOL_DIR_BUS |  |  |  | Motor feed type changed | 2
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Sheet1 (hidden)
TAG | DESCRIPTION | DEVICE_COUNT | DO | DI | AO | AI | SDO | SDI | SAO | SAI
KPA_FLOORX_IO | KPA NON ASSIGNED IO | 485 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR0_IO | KPA LEVEL 0 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR1_IO | KPA LEVEL 1 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR2_IO | KPA LEVEL 2 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR3_IO | KPA LEVEL 3 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR4_IO | KPA LEVEL 4 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FUEL_STATION_IO | KPA FUEL STATION REMOTE IO CABINET | 132 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_MCC | KPA REMOTE IO INTERNAL TO MCC | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_PLC | KPA PLC CABINET | 87 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
ESP_PLC | ESP PLC CABINET | 8 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
ESP_MCC | ESP REMOTE IO INTERNAL TO MCC | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## _Parameters
Parameter | Value
jobNumber | 38025
dwgCategory | ELE
protoPath | S:\Elecdes\prototypes\gen6\INSTRUMENTATION\
protoPathMotor | S:\Elecdes\prototypes\gen6\MOTORS\