## PROTOTYPE_FIELDS
{Note} | Default values for prototypes. Blank fields will not be included when given prototype dbf is generated.
Field | FRQ_REVH | LRUN | THERMISTOR | ISO_FB
PREFIX | ##PREFIX##
DRAWING | ##DRAWING##
PROTOTYPE | S:\Elecdes\prototypes\gen6\MOTORS\FRQ_REVH
X1NAME | ##X1NAME##
X1DESC
X1VDC24
X1VDC0
X1XIO
X1XIOF
X1XIOK
X1V230 | ##X1V230##
X1N230 | ##X1N230##
X1XDB
X1XDBF
X1XDBK
X1XDBQ | ##X1XDBQ##
X2NAME
X2DESC
Q1CATN | ##Q1CATN##
Q1CATD | ##Q1CATD##
Q1NAME1 | ##Q1NAME1##
Q1NAME2 | ##Q1NAME2##
Q1TCATN | ##Q1TCATN##
Q1TCATD | ##Q1TCATD##
Q1TNAME | ##Q1TNAME##
Q1TSETTO | ##Q1TSETTO##
P1NAME |  | ##P1NAME##
P1RACK |  | ##P1RACK##
P1SLOT |  | ##P1SLOT##
P1CHAN |  | ##P1CHAN##
P1MFG |  | 2
P1CATN |  | ##P1CATN##
P1CATD |  | ##P1CATD##
P1CATD2 |  | ##P1CATD2##
P1TAG |  | ##P1TAG##
P1DESC2 |  | ##P1DESC2##
P1DESC3 |  | ##P1DESC3##
P1DESC4 |  | ##P1DESC4##
P1T1 |  | ##P1T1##
P1T2 |  | ##P1T2##
P1T1TYPE |  | ##P1T1TYPE##
P1T2TYPE |  | ##P1T2TYPE##
P2NAME |  | ##P2NAME##
P2RACK |  | ##P2RACK##
P2SLOT |  | ##P2SLOT##
P2CHAN |  | ##P2CHAN##
P2MFG |  | 2
P2CATN |  | ##P2CATN##
P2CATD |  | ##P2CATD##
P2CATD2 |  | ##P2CATD2##
P2TAG |  | ##P2TAG##
P2DESC2 |  | ##P2DESC2##
P2DESC3 |  | ##P2DESC3##
P2DESC4 |  | ##P2DESC4##
P2T1 |  | ##P2T1##
P2T2 |  | ##P2T2##
P2T1TYPE |  | ##P2T1TYPE##
P2T2TYPE |  | ##P2T2TYPE##
P3NAME |  | ##P3NAME##
P3RACK |  | ##P3RACK##
P3SLOT |  | ##P3SLOT##
P3CHAN |  | ##P3CHAN##
P3MFG |  | 2
P3CATN |  | ##P3CATN##
P3CATD |  | ##P3CATD##
P3CATD2 |  | ##P3CATD2##
P3TAG |  | ##P3TAG##
P3DESC2 |  | ##P3DESC2##
P3DESC3 |  | ##P3DESC3##
P3DESC4 |  | ##P3DESC4##
P3T1 |  | ##P3T1##
P3T2 |  | ##P3T2##
P3T1TYPE |  | ##P3T1TYPE##
P3T2TYPE |  | ##P3T2TYPE##
P4NAME |  | ##P4NAME##
P4RACK |  | ##P4RACK##
P4SLOT |  | ##P4SLOT##
P4CHAN |  | ##P4CHAN##
P4MFG |  | 2
P4CATN |  | ##P4CATN##
P4CATD |  | ##P4CATD##
P4CATD2 |  | ##P4CATD2##
P4TAG |  | ##P4TAG##
P4DESC2 |  | ##P4DESC2##
P4DESC3 |  | ##P4DESC3##
P4DESC4 |  | ##P4DESC4##
P4T1 |  | ##P4T1##
P4T2 |  | ##P4T2##
P4T1TYPE |  | ##P4T1TYPE##
P4T2TYPE |  | ##P4T2TYPE##
D1TAG | ##D1TAG##
D1DESC2 | POWERFLEX 753 SERIES VSD
D1DESC3 | ##D1DESC3##
D1DESC4
D1TYPE
D1T1
D1T2
D1MFG
D1CATN | ##D1CATN##
D1CATD | ##D1CATD##
D2TAG | ##D2TAG##
D2DESC2
D2DESC3
D2DESC4
D2TYPE
D2T1
D2T2
D2MFG
D2CATN | ##D2CATN##
D2CATD | ##D2CATD##
D3TAG | ##D3TAG##
D3DESC2 | ##D3DESC2##
D3DESC3 | ##D3DESC3##
D3DESC4 | ##D3DESC4##
D3KW | ##D3KW##
D3TYPE
D3T1
D3T2
D3MFG
D3CATN | ##D3CATN##
D3CATD | ##D3CATD##
C1TAG | ##C1TAG##
C1CATN | ##C1CATN##
C1CATD | ##C1CATD##
C1CORE1 | RD
C1CORE2 | WH
C1CORE3 | BU
C1CORE4 | GN/YL
C1CORE5
C1CORE6
C1CORE7
C2TAG | ##C2TAG##
C2CATN | ##C2CATN##
C2CATD | ##C2CATD##
C2CORE1 | RD
C2CORE2 | WH
C2CORE3 | BU
C2CORE4 | BK
C2CORE5 | GN/YL
C3TAG | ##C3TAG##
C3CATN | ##C3CATN##
C3CATD | ##C3CATD##
C3CORE1 | RD
C3CORE2 | WH
C3CORE3 | BU
C3CORE4 | BK
C3CORE5 | GN/YL
C4TAG | ##C4TAG##
Note on A1: Author: Basic DBF structure outlined on this sheet. Create new prototypes by entering its name into a Column Header.

## TAG_DATA
|  |  | Prototype Mapping |  | Z_DRAWING |  | X_PANEL |  |  |  | 24V Connections |  |  |  |  | 230V Connections | [5 empty] | Q_PROTECTION | [7 empty] | P_IO | [14 empty] | P2 | [44 empty] | D_DEVICES | [6 empty] | VSD |  |  |  |  | Isolator |  |  |  | C_CABLE
Tag | SUB | ProtoTag | Typical | ProtoName | PREFIX | DRAWING | X1NAME | X1DESC | X2NAME | X2DESC | X1VDC24 | X1VDC0 | X1XIO | X1XIOF | X1XIOK | X1V230 | X1N230 | X1XDB | X1XDBF | X1XDBK | X1XDBQ | Q1CATN | Q1CATD | Q1NAME1 | Q1NAME2 | Q1TCATN | Q1TCATD | Q1TNAME | Q1TSETTO | P1NAME | P1RACK | P1SLOT | P1CHAN | P1CATN | P1CATD | P1CATD2 | P1TAG | P1DESC2 | P1DESC3 | P1DESC4 | P1T1 | P1T2 | P1T1TYPE | P1T2TYPE | P2NAME | P2RACK | P2SLOT | P2CHAN | P2CATN | P2CATD | P2CATD2 | P2TAG | P2DESC2 | P2DESC3 | P2DESC4 | P2T1 | P2T2 | P2T1TYPE | P2T2TYPE | P3NAME | P3RACK | P3SLOT | P3CHAN | P3CATN | P3CATD | P3CATD2 | P3TAG | P3DESC2 | P3DESC3 | P3DESC4 | P3T1 | P3T2 | P3T1TYPE | P3T2TYPE | P4NAME | P4RACK | P4SLOT | P4CHAN | P4CATN | P4CATD | P4CATD2 | P4TAG | P4DESC2 | P4DESC3 | P4DESC4 | P4T1 | P4T2 | P4T1TYPE | P4T2TYPE | D3TAG | D3DESC2 | D3DESC3 | D3DESC4 | D3TYPE | D3CATN | D3CATD | D1TAG | D1DESC2 | D1DESC3 | D1CATN | D1CATD | D2TAG | D2CATN | D2CATD | D3KW | C1TAG | C1CATN | C1CATD | C2TAG | C2CATN | C2CATD | C3TAG | C3CATN | C3CATD | C4TAG | Notes
BB1EM658 | A | BB1EM658A | FRQ_REVH | VSD | 38025-ELE | 01-508._L0 | 0 | 0 | 0 | 0 | [5 empty] | Q1508 | 0 | 1508 | F1508 |  | Q1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RIO_ | 01 | 01 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM658_LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 01 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM658_LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 01 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM658_LOCAL_RUN_REV | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 01 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM658_ISOLATOR | SCRAPER CONVEYOR 1 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM658 | SCRAPER CONVEYOR 1 |  |  | MOTOR | MOTOR 15kW | MOTOR 15kW, 3 PHASE | BB1EM658_VSD |  | 15kW, 400VAC | 20F11GC030AA0NNNNN | PowerFlex 753 Series VSD, 15kW, 400VAC | BB1EM658 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 15 | BB1EM658/01 | 0 | 0 | BB1EM658/02 | 0 | 0 | BB1EM658/03 | 0 | 0
BB1EM659 | A | BB1EM659A | FRQ_REVH | VSD | 38025-ELE | 01-509._L0 | 0 | 0 | 0 | 0 | [5 empty] | Q1509 | 0 | 1509 | F1509 |  | Q1509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RIO_ | 01 | 02 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM659_LOCAL_MODE | BELT CONVEYOR | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 02 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM659_LOCAL_RUN_FWD | BELT CONVEYOR | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 02 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM659_LOCAL_RUN_REV | BELT CONVEYOR | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 02 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM659_ISOLATOR | BELT CONVEYOR | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM659 | BELT CONVEYOR |  |  | MOTOR | MOTOR 4kW | MOTOR 4kW, 3 PHASE | BB1EM659_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM659 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 4 | BB1EM659/01 | 0 | 0 | BB1EM659/02 | 0 | 0 | BB1EM659/03 | 0 | 0
BB1EM676 | A | BB1EM676A | FRQ_REVH | VSD | 38025-ELE | 01-505._L0 | KPA_MCC | MAIN MCC | BB1EM676_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1505 | N | 1505 | F1505 |  | Q1505 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | RIO_ | 01 | 03 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM676_LOCAL_MODE | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 03 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM676_LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 03 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM676_LOCAL_RUN_REV | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 03 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM676_ISOLATOR | DISC SCREEN DRIVE 2 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM676 | DISC SCREEN DRIVE 2 |  |  | MOTOR | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE | BB1EM676_VSD |  | 7.5kW, 400VAC | 20F11GC015AA0NNNNN | PowerFlex 753 Series VSD, 7.5kW, 400VAC | BB1EM676 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 7.5 | BB1EM676/01 | 0 | 0 | BB1EM676/02 | 0 | 0 | BB1EM676/03 | 0 | 0
BB1EM672 | A | BB1EM672A | FRQ_REVH | VSD | 38025-ELE | 01-504._L0 | KPA_MCC | MAIN MCC | BB1EM672_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1504 | N | 1504 | F1504 |  | Q1504 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | RIO_ | 01 | 04 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM672_LOCAL_MODE | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 04 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM672_LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 04 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM672_LOCAL_RUN_REV | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 04 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM672_ISOLATOR | SCRAPER CONVEYOR 2 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM672 | SCRAPER CONVEYOR 2 |  |  | MOTOR | MOTOR 18.5kW | MOTOR 18.5kW, 3 PHASE | BB1EM672_VSD |  | 18.5kW, 400VAC | 20F11GC037AA0NNNNN | PowerFlex 753 Series VSD, 18.5kW, 400VAC | BB1EM672 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 18.5 | BB1EM672/01 | 0 | 0 | BB1EM672/02 | 0 | 0 | BB1EM672/03 | 0 | 0
BB1EM662 | A | BB1EM662A | FRQ_REVH | VSD | 38025-ELE | 01-500._L0 | KPA_MCC | MAIN MCC | BB1EM662_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1500 | N | 1500 | F1500 |  | Q1500 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | RIO_ | 01 | 05 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM662_LOCAL_MODE | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 05 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM662_LOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 05 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM662_LOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 05 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM662_ISOLATOR | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM662 | FUEL SILO SCREW DISCHARGE |  |  | MOTOR | MOTOR 22kW | MOTOR 22kW, 3 PHASE | BB1EM662_VSD |  | 22kW, 400VAC | 20F11GC043AA0NNNNN | PowerFlex 753 Series VSD, 22kW, 400VAC | BB1EM662 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 22 | BB1EM662/01 | 0 | 0 | BB1EM662/02 | 0 | 0 | BB1EM662/03 | 0 | 0
BB1EM650 | A | BB1EM650A | FRQ_REVH | VSD | 38025-ELE | 01-507._L0 | 0 | 0 | 0 | 0 | [5 empty] | Q1507 | 0 | 1507 | F1507 |  | Q1507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RIO_ | 01 | 06 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM650_LOCAL_MODE | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 06 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM650_LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 06 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM650_LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 06 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM650_ISOLATOR | SLEWING MOTOR FOR SCREW | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM650 | SLEWING MOTOR FOR SCREW |  |  | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | BB1EM650_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM650 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 2.2 | BB1EM650/01 | 0 | 0 | BB1EM650/02 | 0 | 0 | BB1EM650/03 | 0 | 0
BB1EM663 | A | BB1EM663A | FRQ_REVH | VSD | 38025-ELE | 01-501._L0 | KPA_MCC | MAIN MCC | BB1EM663_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q100 | N | 1501 | F1501 |  | Q1501 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | RIO_ | 01 | 07 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM663_LOCAL_MODE | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 07 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM663_LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 07 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM663_LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 07 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM663_ISOLATOR | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM663 | FUEL SILO CROSS CONVEYOR |  |  | MOTOR | MOTOR 4kW | MOTOR 4kW, 3 PHASE | BB1EM663_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM663 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 4 | BB1EM663/01 | 0 | 0 | BB1EM663/02 | 0 | 0 | BB1EM663/03 | 0 | 0
BB1EM664 | A | BB1EM664A | FRQ_REVH | VSD | 38025-ELE | 01-502._L0 | KPA_MCC | MAIN MCC | BB1EM664_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1502 | N | 1502 | F1502 |  | Q1502 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | RIO_ | 01 | 08 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM664_LOCAL_MODE | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 08 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM664_LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 08 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM664_LOCAL_RUN_REV | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 08 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM664_ISOLATOR | FUEL FEEDING SCREW 1 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM664 | FUEL FEEDING SCREW 1 |  |  | MOTOR | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE | BB1EM664_VSD |  | 5.5kW, 400VAC | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | BB1EM664 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 5.5 | BB1EM664/01 | 0 | 0 | BB1EM664/02 | 0 | 0 | BB1EM664/03 | 0 | 0
BB1EM665 | A | BB1EM665A | FRQ_REVH | VSD | 38025-ELE | 01-503._L0 | KPA_MCC | MAIN MCC | BB1EM665_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q100 | N | 1503 | F1503 |  | Q1503 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 09 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM665_LOCAL_MODE | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 09 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM665_LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 09 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM665_LOCAL_RUN_REV | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 09 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM665_ISOLATOR | FUEL FEEDING SCREW 2 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM665 | FUEL FEEDING SCREW 2 |  |  | MOTOR | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE | BB1EM665_VSD |  | 5.5kW, 400VAC | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | BB1EM665 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 5.5 | BB1EM665/01 | 0 | 0 | BB1EM665/02 | 0 | 0 | BB1EM665/03 | 0 | 0
BB1EM852 | A | BB1EM852A | FRQ_REVH | VSD | 38025-ELE | 01-506._L0 | KPA_MCC | MAIN MCC | BB1EM852_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1506 | N | 1506 | F1506 |  | Q1506 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | RIO_ | 01 | 10 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM852_LOCAL_MODE | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 10 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM852_LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 10 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM852_LOCAL_RUN_REV | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 10 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM852_ISOLATOR | BOTTOM ASH CONVEYOR | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM852 | BOTTOM ASH CONVEYOR |  |  | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | BB1EM852_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM852 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 2.2 | BB1EM852/01 | 0 | 0 | BB1EM852/02 | 0 | 0 | BB1EM852/03 | 0 | 0
BB1EM658 | B | BB1EM658B | FRQ_REVH | LRUN | 38025-ELE | 01-508._L0 | 0 | 0 | 0 | 0 | [5 empty] | Q1508 | 0 | 1508 | F1508 |  | Q1508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RIO_ | 01 | 01 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM658_LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 01 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM658_LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 01 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM658_LOCAL_RUN_REV | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 01 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM658_ISOLATOR | SCRAPER CONVEYOR 1 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM658 | SCRAPER CONVEYOR 1 |  |  | MOTOR | MOTOR 15kW | MOTOR 15kW, 3 PHASE | BB1EM658_VSD |  | 15kW, 400VAC | 20F11GC030AA0NNNNN | PowerFlex 753 Series VSD, 15kW, 400VAC | BB1EM658 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 15 | BB1EM658/01 | 0 | 0 | BB1EM658/02 | 0 | 0 | BB1EM658/03 | 0 | 0
BB1EM659 | B | BB1EM659B | FRQ_REVH | LRUN | 38025-ELE | 01-509._L0 | 0 | 0 | 0 | 0 | [5 empty] | Q1509 | 0 | 1509 | F1509 |  | Q1509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RIO_ | 01 | 02 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM659_LOCAL_MODE | BELT CONVEYOR | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 02 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM659_LOCAL_RUN_FWD | BELT CONVEYOR | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 02 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM659_LOCAL_RUN_REV | BELT CONVEYOR | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 02 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM659_ISOLATOR | BELT CONVEYOR | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM659 | BELT CONVEYOR |  |  | MOTOR | MOTOR 4kW | MOTOR 4kW, 3 PHASE | BB1EM659_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM659 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 4 | BB1EM659/01 | 0 | 0 | BB1EM659/02 | 0 | 0 | BB1EM659/03 | 0 | 0
BB1EM676 | B | BB1EM676B | FRQ_REVH | LRUN | 38025-ELE | 01-505._L0 | KPA_MCC | MAIN MCC | BB1EM676_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1505 | N | 1505 | F1505 |  | Q1505 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | RIO_ | 01 | 03 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM676_LOCAL_MODE | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 03 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM676_LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 03 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM676_LOCAL_RUN_REV | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 03 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM676_ISOLATOR | DISC SCREEN DRIVE 2 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM676 | DISC SCREEN DRIVE 2 |  |  | MOTOR | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE | BB1EM676_VSD |  | 7.5kW, 400VAC | 20F11GC015AA0NNNNN | PowerFlex 753 Series VSD, 7.5kW, 400VAC | BB1EM676 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 7.5 | BB1EM676/01 | 0 | 0 | BB1EM676/02 | 0 | 0 | BB1EM676/03 | 0 | 0
BB1EM672 | B | BB1EM672B | FRQ_REVH | LRUN | 38025-ELE | 01-504._L0 | KPA_MCC | MAIN MCC | BB1EM672_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1504 | N | 1504 | F1504 |  | Q1504 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | RIO_ | 01 | 04 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM672_LOCAL_MODE | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 04 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM672_LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 04 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM672_LOCAL_RUN_REV | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 04 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM672_ISOLATOR | SCRAPER CONVEYOR 2 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM672 | SCRAPER CONVEYOR 2 |  |  | MOTOR | MOTOR 18.5kW | MOTOR 18.5kW, 3 PHASE | BB1EM672_VSD |  | 18.5kW, 400VAC | 20F11GC037AA0NNNNN | PowerFlex 753 Series VSD, 18.5kW, 400VAC | BB1EM672 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 18.5 | BB1EM672/01 | 0 | 0 | BB1EM672/02 | 0 | 0 | BB1EM672/03 | 0 | 0
BB1EM662 | B | BB1EM662B | FRQ_REVH | LRUN | 38025-ELE | 01-500._L0 | KPA_MCC | MAIN MCC | BB1EM662_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1500 | N | 1500 | F1500 |  | Q1500 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | RIO_ | 01 | 05 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM662_LOCAL_MODE | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 05 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM662_LOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 05 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM662_LOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 05 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM662_ISOLATOR | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM662 | FUEL SILO SCREW DISCHARGE |  |  | MOTOR | MOTOR 22kW | MOTOR 22kW, 3 PHASE | BB1EM662_VSD |  | 22kW, 400VAC | 20F11GC043AA0NNNNN | PowerFlex 753 Series VSD, 22kW, 400VAC | BB1EM662 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 22 | BB1EM662/01 | 0 | 0 | BB1EM662/02 | 0 | 0 | BB1EM662/03 | 0 | 0
BB1EM650 | B | BB1EM650B | FRQ_REVH | LRUN | 38025-ELE | 01-507._L0 | 0 | 0 | 0 | 0 | [5 empty] | Q1507 | 0 | 1507 | F1507 |  | Q1507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RIO_ | 01 | 06 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM650_LOCAL_MODE | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 06 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM650_LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 06 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM650_LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 06 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM650_ISOLATOR | SLEWING MOTOR FOR SCREW | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM650 | SLEWING MOTOR FOR SCREW |  |  | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | BB1EM650_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM650 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 2.2 | BB1EM650/01 | 0 | 0 | BB1EM650/02 | 0 | 0 | BB1EM650/03 | 0 | 0
BB1EM663 | B | BB1EM663B | FRQ_REVH | LRUN | 38025-ELE | 01-501._L0 | KPA_MCC | MAIN MCC | BB1EM663_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q100 | N | 1501 | F1501 |  | Q1501 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | RIO_ | 01 | 07 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM663_LOCAL_MODE | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 07 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM663_LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 07 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM663_LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 07 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM663_ISOLATOR | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM663 | FUEL SILO CROSS CONVEYOR |  |  | MOTOR | MOTOR 4kW | MOTOR 4kW, 3 PHASE | BB1EM663_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM663 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 4 | BB1EM663/01 | 0 | 0 | BB1EM663/02 | 0 | 0 | BB1EM663/03 | 0 | 0
BB1EM664 | B | BB1EM664B | FRQ_REVH | LRUN | 38025-ELE | 01-502._L0 | KPA_MCC | MAIN MCC | BB1EM664_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1502 | N | 1502 | F1502 |  | Q1502 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | RIO_ | 01 | 08 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM664_LOCAL_MODE | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 08 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM664_LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 08 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM664_LOCAL_RUN_REV | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 08 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM664_ISOLATOR | FUEL FEEDING SCREW 1 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM664 | FUEL FEEDING SCREW 1 |  |  | MOTOR | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE | BB1EM664_VSD |  | 5.5kW, 400VAC | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | BB1EM664 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 5.5 | BB1EM664/01 | 0 | 0 | BB1EM664/02 | 0 | 0 | BB1EM664/03 | 0 | 0
BB1EM665 | B | BB1EM665B | FRQ_REVH | LRUN | 38025-ELE | 01-503._L0 | KPA_MCC | MAIN MCC | BB1EM665_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q100 | N | 1503 | F1503 |  | Q1503 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 09 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM665_LOCAL_MODE | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 09 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM665_LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 09 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM665_LOCAL_RUN_REV | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 09 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM665_ISOLATOR | FUEL FEEDING SCREW 2 | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM665 | FUEL FEEDING SCREW 2 |  |  | MOTOR | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE | BB1EM665_VSD |  | 5.5kW, 400VAC | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | BB1EM665 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 5.5 | BB1EM665/01 | 0 | 0 | BB1EM665/02 | 0 | 0 | BB1EM665/03 | 0 | 0
BB1EM852 | B | BB1EM852B | FRQ_REVH | LRUN | 38025-ELE | 01-506._L0 | KPA_MCC | MAIN MCC | BB1EM852_PB_STATION | LOCAL/FWD/REV | [5 empty] | Q1506 | N | 1506 | F1506 |  | Q1506 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | RIO_ | 01 | 10 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM852_LOCAL_MODE | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | V+ | 00 | 24VDC | DI | RIO_ | 01 | 10 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM852_LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 10 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM852_LOCAL_RUN_REV | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 10 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM852_ISOLATOR | BOTTOM ASH CONVEYOR | ISOLATOR |  | V+ | 03 | 24VDC | DI | BB1EM852 | BOTTOM ASH CONVEYOR |  |  | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | BB1EM852_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM852 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 2.2 | BB1EM852/01 | 0 | 0 | BB1EM852/02 | 0 | 0 | BB1EM852/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0 | 0_ISO
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0
|  |  | #N/A | [26 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0_VSD |  | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 0/01 | 0 | 0 | 0/02 | 0 | 0 | 0/03 | 0 | 0

## Z_DRAWING
Tag Info | Drawing Filename
_Tag | _Type | Prefix | SubProject | _Base | _Index | _Number | _Append | Drawing | testIndex | Notes
DETAIL | ELE | 38025-ELE | 1 | 100 | 0 | 100 |  | 01-100._L0 | 1100
DETAIL | ELE | 38025-ELE | 1 | 100 | 1 | 101 |  | 01-101._L0 | 1101
DETAIL | ELE | 38025-ELE | 1 | 100 | 2 | 102 |  | 01-102._L0 | 1102
DETAIL | ELE | 38025-ELE | 1 | 100 | 3 | 103 |  | 01-103._L0 | 1103
DETAIL | ELE | 38025-ELE | 1 | 100 | 4 | 104 |  | 01-104._L0 | 1104
DETAIL | ELE | 38025-ELE | 1 | 100 | 5 | 105 |  | 01-105._L0 | 1105
DETAIL | ELE | 38025-ELE | 1 | 100 | 6 | 106 |  | 01-106._L0 | 1106
BB1EM650 | ELE | 38025-ELE | 1 | 500 | 7 | 507 |  | 01-507._L0 | 1507
BB1EM658 | ELE | 38025-ELE | 1 | 500 | 8 | 508 |  | 01-508._L0 | 1508
BB1EM659 | ELE | 38025-ELE | 1 | 500 | 9 | 509 |  | 01-509._L0 | 1509
BB1EM662 | ELE | 38025-ELE | 1 | 500 | 0 | 500 |  | 01-500._L0 | 1500
BB1EM663 | ELE | 38025-ELE | 1 | 500 | 1 | 501 |  | 01-501._L0 | 1501
BB1EM664 | ELE | 38025-ELE | 1 | 500 | 2 | 502 |  | 01-502._L0 | 1502
BB1EM665 | ELE | 38025-ELE | 1 | 500 | 3 | 503 |  | 01-503._L0 | 1503
BB1EM672 | ELE | 38025-ELE | 1 | 500 | 4 | 504 |  | 01-504._L0 | 1504
BB1EM676 | ELE | 38025-ELE | 1 | 500 | 5 | 505 |  | 01-505._L0 | 1505
BB1EM852 | ELE | 38025-ELE | 1 | 500 | 6 | 506 |  | 01-506._L0 | 1506
BB1EM650 | ELE | 38025-ELE | 1 | 500 | 7 | 507 |  | 01-507._L0 | 1507
BB1EM658 | ELE | 38025-ELE | 1 | 500 | 8 | 508 |  | 01-508._L0 | 1508
BB1EM659 | ELE | 38025-ELE | 1 | 500 | 9 | 509 |  | 01-509._L0 | 1509
BB1EM662 | ELE | 38025-ELE | 1 | 400 | 0 | 400 |  | 01-400._L0 | 1400
BB1EM663 | ELE | 38025-ELE | 1 | 400 | 1 | 401 |  | 01-401._L0 | 1401
BB1EM664 | ELE | 38025-ELE | 1 | 400 | 2 | 402 |  | 01-402._L0 | 1402
BB1EM665 | ELE | 38025-ELE | 1 | 400 | 3 | 403 |  | 01-403._L0 | 1403
BB1EM672 | ELE | 38025-ELE | 1 | 400 | 4 | 404 |  | 01-404._L0 | 1404
BB1EM676 | ELE | 38025-ELE | 1 | 400 | 5 | 405 |  | 01-405._L0 | 1405
BB1EM852 | ELE | 38025-ELE | 1 | 400 | 6 | 406 |  | 01-406._L0 | 1406
| ELE | 38025-ELE | 1 | 400 | 7 | 407 |  | 01-407._L0 | 1407
| ELE | 38025-ELE | 1 | 400 | 8 | 408 |  | 01-408._L0 | 1408
| ELE | 38025-ELE | 1 | 400 | 9 | 409 |  | 01-409._L0 | 1409
| ELE | 38025-ELE | 1 | 400 | 10 | 410 |  | 01-410._L0 | 1410
| ELE | 38025-ELE | 1 | 400 | 11 | 411 |  | 01-411._L0 | 1411
| ELE | 38025-ELE | 1 | 400 | 12 | 412 |  | 01-412._L0 | 1412
| ELE | 38025-ELE | 1 | 400 | 13 | 413 |  | 01-413._L0 | 1413
| ELE | 38025-ELE | 1 | 400 | 14 | 414 |  | 01-414._L0 | 1414
| ELE | 38025-ELE | 1 | 400 | 15 | 415 |  | 01-415._L0 | 1415
| ELE | 38025-ELE | 1 | 400 | 16 | 416 |  | 01-416._L0 | 1416
| ELE | 38025-ELE | 1 | 400 | 17 | 417 |  | 01-417._L0 | 1417
| ELE | 38025-ELE | 1 | 400 | 18 | 418 |  | 01-418._L0 | 1418
| ELE | 38025-ELE | 1 | 400 | 19 | 419 |  | 01-419._L0 | 1419
| ELE | 38025-ELE | 1 | 400 | 20 | 420 |  | 01-420._L0 | 1420
| ELE | 38025-ELE | 1 | 400 | 21 | 421 |  | 01-421._L0 | 1421
| ELE | 38025-ELE | 1 | 400 | 22 | 422 |  | 01-422._L0 | 1422
| ELE | 38025-ELE | 1 | 400 | 23 | 423 |  | 01-423._L0 | 1423
| ELE | 38025-ELE | 1 | 400 | 24 | 424 |  | 01-424._L0 | 1424
| ELE | 38025-ELE | 1 | 400 | 25 | 425 |  | 01-425._L0 | 1425
| ELE | 38025-ELE | 1 | 400 | 26 | 426 |  | 01-426._L0 | 1426
| ELE | 38025-ELE | 1 | 400 | 27 | 427 |  | 01-427._L0 | 1427
| ELE | 38025-ELE | 1 | 400 | 28 | 428 |  | 01-428._L0 | 1428
| ELE | 38025-ELE | 1 | 400 | 29 | 429 |  | 01-429._L0 | 1429
| ELE | 38025-ELE | 1 | 400 | 30 | 430 |  | 01-430._L0 | 1430
| ELE | 38025-ELE | 1 | 400 | 31 | 431 |  | 01-431._L0 | 1431
| ELE | 38025-ELE | 1 | 400 | 32 | 432 |  | 01-432._L0 | 1432
| ELE | 38025-ELE | 1 | 400 | 33 | 433 |  | 01-433._L0 | 1433
| ELE | 38025-ELE | 1 | 400 | 34 | 434 |  | 01-434._L0 | 1434
| ELE | 38025-ELE | 1 | 400 | 35 | 435 |  | 01-435._L0 | 1435
| ELE | 38025-ELE | 1 | 400 | 36 | 436 |  | 01-436._L0 | 1436
| ELE | 38025-ELE | 1 | 400 | 37 | 437 |  | 01-437._L0 | 1437
| ELE | 38025-ELE | 1 | 400 | 38 | 438 |  | 01-438._L0 | 1438
| ELE | 38025-ELE | 1 | 400 | 39 | 439 |  | 01-439._L0 | 1439
| ELE | 38025-ELE | 1 | 400 | 40 | 440 |  | 01-440._L0 | 1440
| ELE | 38025-ELE | 1 | 400 | 41 | 441 |  | 01-441._L0 | 1441
| ELE | 38025-ELE | 1 | 400 | 42 | 442 |  | 01-442._L0 | 1442
| ELE | 38025-ELE | 1 | 400 | 43 | 443 |  | 01-443._L0 | 1443
| ELE | 38025-ELE | 1 | 400 | 44 | 444 |  | 01-444._L0 | 1444
| ELE | 38025-ELE | 1 | 400 | 45 | 445 |  | 01-445._L0 | 1445
| ELE | 38025-ELE | 1 | 400 | 46 | 446 |  | 01-446._L0 | 1446
| ELE | 38025-ELE | 1 | 400 | 47 | 447 |  | 01-447._L0 | 1447
| ELE | 38025-ELE | 1 | 400 | 48 | 448 |  | 01-448._L0 | 1448
| ELE | 38025-ELE | 1 | 400 | 49 | 449 |  | 01-449._L0 | 1449
| ELE | 38025-ELE | 1 | 400 | 50 | 450 |  | 01-450._L0 | 1450
| ELE | 38025-ELE | 1 | 400 | 51 | 451 |  | 01-451._L0 | 1451
| ELE | 38025-ELE | 1 | 400 | 52 | 452 |  | 01-452._L0 | 1452
| ELE | 38025-ELE | 1 | 400 | 53 | 453 |  | 01-453._L0 | 1453
| ELE | 38025-ELE | 1 | 400 | 54 | 454 |  | 01-454._L0 | 1454
| ELE | 38025-ELE | 1 | 400 | 55 | 455 |  | 01-455._L0 | 1455
| ELE | 38025-ELE | 1 | 400 | 56 | 456 |  | 01-456._L0 | 1456
| ELE | 38025-ELE | 1 | 400 | 57 | 457 |  | 01-457._L0 | 1457
| ELE | 38025-ELE | 1 | 400 | 58 | 458 |  | 01-458._L0 | 1458
| ELE | 38025-ELE | 1 | 400 | 59 | 459 |  | 01-459._L0 | 1459
| ELE | 38025-ELE | 1 | 400 | 60 | 460 |  | 01-460._L0 | 1460
| ELE | 38025-ELE | 1 | 400 | 61 | 461 |  | 01-461._L0 | 1461
| ELE | 38025-ELE | 1 | 400 | 62 | 462 |  | 01-462._L0 | 1462
| ELE | 38025-ELE | 1 | 400 | 63 | 463 |  | 01-463._L0 | 1463
| ELE | 38025-ELE | 1 | 400 | 64 | 464 |  | 01-464._L0 | 1464
| ELE | 38025-ELE | 1 | 400 | 65 | 465 |  | 01-465._L0 | 1465
| ELE | 38025-ELE | 1 | 400 | 66 | 466 |  | 01-466._L0 | 1466
| ELE | 38025-ELE | 1 | 400 | 67 | 467 |  | 01-467._L0 | 1467
| ELE | 38025-ELE | 1 | 400 | 68 | 468 |  | 01-468._L0 | 1468
| ELE | 38025-ELE | 1 | 400 | 69 | 469 |  | 01-469._L0 | 1469
| ELE | 38025-ELE | 1 | 400 | 70 | 470 |  | 01-470._L0 | 1470
| ELE | 38025-ELE | 1 | 400 | 71 | 471 |  | 01-471._L0 | 1471
| ELE | 38025-ELE | 1 | 400 | 72 | 472 |  | 01-472._L0 | 1472
| ELE | 38025-ELE | 1 | 400 | 73 | 473 |  | 01-473._L0 | 1473
| ELE | 38025-ELE | 1 | 400 | 74 | 474 |  | 01-474._L0 | 1474
| ELE | 38025-ELE | 1 | 400 | 75 | 475 |  | 01-475._L0 | 1475
| ELE | 38025-ELE | 1 | 400 | 76 | 476 |  | 01-476._L0 | 1476
| ELE | 38025-ELE | 1 | 400 | 77 | 477 |  | 01-477._L0 | 1477
| ELE | 38025-ELE | 1 | 400 | 78 | 478 |  | 01-478._L0 | 1478
| ELE | 38025-ELE | 1 | 400 | 79 | 479 |  | 01-479._L0 | 1479
| ELE | 38025-ELE | 1 | 400 | 80 | 480 |  | 01-480._L0 | 1480
| ELE | 38025-ELE | 1 | 400 | 81 | 481 |  | 01-481._L0 | 1481
| ELE | 38025-ELE | 1 | 400 | 82 | 482 |  | 01-482._L0 | 1482
| ELE | 38025-ELE | 1 | 400 | 83 | 483 |  | 01-483._L0 | 1483
| ELE | 38025-ELE | 1 | 400 | 84 | 484 |  | 01-484._L0 | 1484
| ELE | 38025-ELE | 1 | 400 | 85 | 485 |  | 01-485._L0 | 1485
| ELE | 38025-ELE | 1 | 400 | 86 | 486 |  | 01-486._L0 | 1486
| ELE | 38025-ELE | 1 | 400 | 87 | 487 |  | 01-487._L0 | 1487
| ELE | 38025-ELE | 1 | 400 | 88 | 488 |  | 01-488._L0 | 1488
| ELE | 38025-ELE | 1 | 400 | 89 | 489 |  | 01-489._L0 | 1489
| ELE | 38025-ELE | 1 | 400 | 90 | 490 |  | 01-490._L0 | 1490
| ELE | 38025-ELE | 1 | 400 | 91 | 491 |  | 01-491._L0 | 1491
| ELE | 38025-ELE | 1 | 400 | 92 | 492 |  | 01-492._L0 | 1492
| ELE | 38025-ELE | 1 | 400 | 93 | 493 |  | 01-493._L0 | 1493
| ELE | 38025-ELE | 1 | 400 | 94 | 494 |  | 01-494._L0 | 1494
| ELE | 38025-ELE | 1 | 400 | 95 | 495 |  | 01-495._L0 | 1495
| ELE | 38025-ELE | 1 | 400 | 96 | 496 |  | 01-496._L0 | 1496
| ELE | 38025-ELE | 1 | 400 | 97 | 497 |  | 01-497._L0 | 1497
| ELE | 38025-ELE | 1 | 400 | 98 | 498 |  | 01-498._L0 | 1498
| ELE | 38025-ELE | 1 | 400 | 99 | 499 |  | 01-499._L0 | 1499
| ELE | 38025-ELE | 1 | 400 | 100 | 500 |  | 01-500._L0 | 1500
| ELE | 38025-ELE | 1 | 400 | 101 | 501 |  | 01-501._L0 | 1501
| ELE | 38025-ELE | 1 | 400 | 102 | 502 |  | 01-502._L0 | 1502
| ELE | 38025-ELE | 1 | 400 | 103 | 503 |  | 01-503._L0 | 1503
| ELE | 38025-ELE | 1 | 400 | 104 | 504 |  | 01-504._L0 | 1504
| ELE | 38025-ELE | 1 | 400 | 105 | 505 |  | 01-505._L0 | 1505
| ELE | 38025-ELE | 1 | 400 | 106 | 506 |  | 01-506._L0 | 1506
| ELE | 38025-ELE | 1 | 400 | 107 | 507 |  | 01-507._L0 | 1507
| ELE | 38025-ELE | 1 | 400 | 108 | 508 |  | 01-508._L0 | 1508
| ELE | 38025-ELE | 1 | 400 | 109 | 509 |  | 01-509._L0 | 1509
| ELE | 38025-ELE | 1 | 400 | 110 | 510 |  | 01-510._L0 | 1510
| ELE | 38025-ELE | 1 | 400 | 111 | 511 |  | 01-511._L0 | 1511
| ELE | 38025-ELE | 1 | 400 | 112 | 512 |  | 01-512._L0 | 1512
| ELE | 38025-ELE | 1 | 400 | 113 | 513 |  | 01-513._L0 | 1513
| ELE | 38025-ELE | 1 | 400 | 114 | 514 |  | 01-514._L0 | 1514
| ELE | 38025-ELE | 1 | 400 | 115 | 515 |  | 01-515._L0 | 1515
| ELE | 38025-ELE | 1 | 400 | 116 | 516 |  | 01-516._L0 | 1516
| ELE | 38025-ELE | 1 | 400 | 117 | 517 |  | 01-517._L0 | 1517
| ELE | 38025-ELE | 1 | 400 | 118 | 518 |  | 01-518._L0 | 1518
| ELE | 38025-ELE | 1 | 400 | 119 | 519 |  | 01-519._L0 | 1519
| ELE | 38025-ELE | 1 | 400 | 120 | 520 |  | 01-520._L0 | 1520
| ELE | 38025-ELE | 1 | 400 | 121 | 521 |  | 01-521._L0 | 1521
| ELE | 38025-ELE | 1 | 400 | 122 | 522 |  | 01-522._L0 | 1522
| ELE | 38025-ELE | 1 | 400 | 123 | 523 |  | 01-523._L0 | 1523
| ELE | 38025-ELE | 1 | 400 | 124 | 524 |  | 01-524._L0 | 1524
| ELE | 38025-ELE | 1 | 400 | 125 | 525 |  | 01-525._L0 | 1525
| ELE | 38025-ELE | 1 | 400 | 126 | 526 |  | 01-526._L0 | 1526
| ELE | 38025-ELE | 1 | 400 | 127 | 527 |  | 01-527._L0 | 1527
| ELE | 38025-ELE | 1 | 400 | 128 | 528 |  | 01-528._L0 | 1528
| ELE | 38025-ELE | 1 | 400 | 129 | 529 |  | 01-529._L0 | 1529
| ELE | 38025-ELE | 1 | 400 | 130 | 530 |  | 01-530._L0 | 1530
| ELE | 38025-ELE | 1 | 400 | 131 | 531 |  | 01-531._L0 | 1531
| ELE | 38025-ELE | 1 | 400 | 132 | 532 |  | 01-532._L0 | 1532
| ELE | 38025-ELE | 1 | 400 | 133 | 533 |  | 01-533._L0 | 1533
| ELE | 38025-ELE | 1 | 400 | 134 | 534 |  | 01-534._L0 | 1534
| ELE | 38025-ELE | 1 | 400 | 135 | 535 |  | 01-535._L0 | 1535
| ELE | 38025-ELE | 1 | 400 | 136 | 536 |  | 01-536._L0 | 1536
| ELE | 38025-ELE | 1 | 400 | 137 | 537 |  | 01-537._L0 | 1537
| ELE | 38025-ELE | 1 | 400 | 138 | 538 |  | 01-538._L0 | 1538
| ELE | 38025-ELE | 1 | 400 | 139 | 539 |  | 01-539._L0 | 1539
| ELE | 38025-ELE | 1 | 400 | 140 | 540 |  | 01-540._L0 | 1540
| ELE | 38025-ELE | 1 | 400 | 141 | 541 |  | 01-541._L0 | 1541
| ELE | 38025-ELE | 1 | 400 | 142 | 542 |  | 01-542._L0 | 1542
| ELE | 38025-ELE | 1 | 400 | 143 | 543 |  | 01-543._L0 | 1543
| ELE | 38025-ELE | 1 | 400 | 144 | 544 |  | 01-544._L0 | 1544
| ELE | 38025-ELE | 1 | 400 | 145 | 545 |  | 01-545._L0 | 1545
| ELE | 38025-ELE | 1 | 400 | 146 | 546 |  | 01-546._L0 | 1546
| ELE | 38025-ELE | 1 | 400 | 147 | 547 |  | 01-547._L0 | 1547
| ELE | 38025-ELE | 1 | 400 | 148 | 548 |  | 01-548._L0 | 1548
| ELE | 38025-ELE | 1 | 400 | 149 | 549 |  | 01-549._L0 | 1549
| ELE | 38025-ELE | 1 | 400 | 150 | 550 |  | 01-550._L0 | 1550
| ELE | 38025-ELE | 1 | 400 | 151 | 551 |  | 01-551._L0 | 1551
| ELE | 38025-ELE | 1 | 400 | 152 | 552 |  | 01-552._L0 | 1552
| ELE | 38025-ELE | 1 | 400 | 153 | 553 |  | 01-553._L0 | 1553
| ELE | 38025-ELE | 1 | 400 | 154 | 554 |  | 01-554._L0 | 1554
| ELE | 38025-ELE | 1 | 400 | 155 | 555 |  | 01-555._L0 | 1555
| ELE | 38025-ELE | 1 | 400 | 156 | 556 |  | 01-556._L0 | 1556
| ELE | 38025-ELE | 1 | 400 | 157 | 557 |  | 01-557._L0 | 1557
| ELE | 38025-ELE | 1 | 400 | 158 | 558 |  | 01-558._L0 | 1558
| ELE | 38025-ELE | 1 | 400 | 159 | 559 |  | 01-559._L0 | 1559
| ELE | 38025-ELE | 1 | 400 | 160 | 560 |  | 01-560._L0 | 1560
| ELE | 38025-ELE | 1 | 400 | 161 | 561 |  | 01-561._L0 | 1561
| ELE | 38025-ELE | 1 | 400 | 162 | 562 |  | 01-562._L0 | 1562
| ELE | 38025-ELE | 1 | 400 | 163 | 563 |  | 01-563._L0 | 1563
| ELE | 38025-ELE | 1 | 400 | 164 | 564 |  | 01-564._L0 | 1564
| ELE | 38025-ELE | 1 | 400 | 165 | 565 |  | 01-565._L0 | 1565
| ELE | 38025-ELE | 1 | 400 | 166 | 566 |  | 01-566._L0 | 1566
| ELE | 38025-ELE | 1 | 400 | 167 | 567 |  | 01-567._L0 | 1567
| ELE | 38025-ELE | 1 | 400 | 168 | 568 |  | 01-568._L0 | 1568
| ELE | 38025-ELE | 1 | 400 | 169 | 569 |  | 01-569._L0 | 1569
| ELE | 38025-ELE | 1 | 400 | 170 | 570 |  | 01-570._L0 | 1570
| ELE | 38025-ELE | 1 | 400 | 171 | 571 |  | 01-571._L0 | 1571
| ELE | 38025-ELE | 1 | 400 | 172 | 572 |  | 01-572._L0 | 1572
| ELE | 38025-ELE | 1 | 400 | 173 | 573 |  | 01-573._L0 | 1573
| ELE | 38025-ELE | 1 | 400 | 174 | 574 |  | 01-574._L0 | 1574
| ELE | 38025-ELE | 1 | 400 | 175 | 575 |  | 01-575._L0 | 1575
| ELE | 38025-ELE | 1 | 400 | 176 | 576 |  | 01-576._L0 | 1576
| ELE | 38025-ELE | 1 | 400 | 177 | 577 |  | 01-577._L0 | 1577
| ELE | 38025-ELE | 1 | 400 | 178 | 578 |  | 01-578._L0 | 1578
| ELE | 38025-ELE | 1 | 400 | 179 | 579 |  | 01-579._L0 | 1579
| ELE | 38025-ELE | 1 | 400 | 180 | 580 |  | 01-580._L0 | 1580
| ELE | 38025-ELE | 1 | 400 | 181 | 581 |  | 01-581._L0 | 1581
| ELE | 38025-ELE | 1 | 400 | 182 | 582 |  | 01-582._L0 | 1582
| ELE | 38025-ELE | 1 | 400 | 183 | 583 |  | 01-583._L0 | 1583
| ELE | 38025-ELE | 1 | 400 | 184 | 584 |  | 01-584._L0 | 1584
| ELE | 38025-ELE | 1 | 400 | 185 | 585 |  | 01-585._L0 | 1585
| ELE | 38025-ELE | 1 | 400 | 186 | 586 |  | 01-586._L0 | 1586
| ELE | 38025-ELE | 1 | 400 | 187 | 587 |  | 01-587._L0 | 1587
| ELE | 38025-ELE | 1 | 400 | 188 | 588 |  | 01-588._L0 | 1588
| ELE | 38025-ELE | 1 | 400 | 189 | 589 |  | 01-589._L0 | 1589
| ELE | 38025-ELE | 1 | 400 | 190 | 590 |  | 01-590._L0 | 1590
| ELE | 38025-ELE | 1 | 400 | 191 | 591 |  | 01-591._L0 | 1591
| ELE | 38025-ELE | 1 | 400 | 192 | 592 |  | 01-592._L0 | 1592
| ELE | 38025-ELE | 1 | 400 | 193 | 593 |  | 01-593._L0 | 1593
| ELE | 38025-ELE | 1 | 400 | 194 | 594 |  | 01-594._L0 | 1594
| ELE | 38025-ELE | 1 | 400 | 195 | 595 |  | 01-595._L0 | 1595
| ELE | 38025-ELE | 1 | 400 | 196 | 596 |  | 01-596._L0 | 1596
| ELE | 38025-ELE | 1 | 400 | 197 | 597 |  | 01-597._L0 | 1597
| ELE | 38025-ELE | 1 | 400 | 198 | 598 |  | 01-598._L0 | 1598
| ELE | 38025-ELE | 1 | 400 | 199 | 599 |  | 01-599._L0 | 1599
| ELE | 38025-ELE | 1 | 400 | 200 | 600 |  | 01-600._L0 | 1600
| ELE | 38025-ELE | 1 | 400 | 201 | 601 |  | 01-601._L0 | 1601
| ELE | 38025-ELE | 1 | 400 | 202 | 602 |  | 01-602._L0 | 1602
| ELE | 38025-ELE | 1 | 400 | 203 | 603 |  | 01-603._L0 | 1603
| ELE | 38025-ELE | 1 | 400 | 204 | 604 |  | 01-604._L0 | 1604
| ELE | 38025-ELE | 1 | 400 | 205 | 605 |  | 01-605._L0 | 1605
| ELE | 38025-ELE | 1 | 400 | 206 | 606 |  | 01-606._L0 | 1606
| ELE | 38025-ELE | 1 | 400 | 207 | 607 |  | 01-607._L0 | 1607
| ELE | 38025-ELE | 1 | 400 | 208 | 608 |  | 01-608._L0 | 1608
| ELE | 38025-ELE | 1 | 400 | 209 | 609 |  | 01-609._L0 | 1609
| ELE | 38025-ELE | 1 | 400 | 210 | 610 |  | 01-610._L0 | 1610
| ELE | 38025-ELE | 1 | 400 | 211 | 611 |  | 01-611._L0 | 1611
| ELE | 38025-ELE | 1 | 400 | 212 | 612 |  | 01-612._L0 | 1612
| ELE | 38025-ELE | 1 | 400 | 213 | 613 |  | 01-613._L0 | 1613
| ELE | 38025-ELE | 1 | 400 | 214 | 614 |  | 01-614._L0 | 1614
| ELE | 38025-ELE | 1 | 400 | 215 | 615 |  | 01-615._L0 | 1615
| ELE | 38025-ELE | 1 | 400 | 216 | 616 |  | 01-616._L0 | 1616
| ELE | 38025-ELE | 1 | 400 | 217 | 617 |  | 01-617._L0 | 1617
| ELE | 38025-ELE | 1 | 400 | 218 | 618 |  | 01-618._L0 | 1618
| ELE | 38025-ELE | 1 | 400 | 219 | 619 |  | 01-619._L0 | 1619
| ELE | 38025-ELE | 1 | 400 | 220 | 620 |  | 01-620._L0 | 1620
| ELE | 38025-ELE | 1 | 400 | 221 | 621 |  | 01-621._L0 | 1621
| ELE | 38025-ELE | 1 | 400 | 222 | 622 |  | 01-622._L0 | 1622
| ELE | 38025-ELE | 1 | 400 | 223 | 623 |  | 01-623._L0 | 1623
| ELE | 38025-ELE | 1 | 400 | 224 | 624 |  | 01-624._L0 | 1624
| ELE | 38025-ELE | 1 | 400 | 225 | 625 |  | 01-625._L0 | 1625
| ELE | 38025-ELE | 1 | 400 | 226 | 626 |  | 01-626._L0 | 1626
| ELE | 38025-ELE | 1 | 400 | 227 | 627 |  | 01-627._L0 | 1627
| ELE | 38025-ELE | 1 | 400 | 228 | 628 |  | 01-628._L0 | 1628
| ELE | 38025-ELE | 1 | 400 | 229 | 629 |  | 01-629._L0 | 1629
| ELE | 38025-ELE | 1 | 400 | 230 | 630 |  | 01-630._L0 | 1630
| ELE | 38025-ELE | 1 | 400 | 231 | 631 |  | 01-631._L0 | 1631
| ELE | 38025-ELE | 1 | 400 | 232 | 632 |  | 01-632._L0 | 1632
| ELE | 38025-ELE | 1 | 400 | 233 | 633 |  | 01-633._L0 | 1633
| ELE | 38025-ELE | 1 | 400 | 234 | 634 |  | 01-634._L0 | 1634
| ELE | 38025-ELE | 1 | 400 | 235 | 635 |  | 01-635._L0 | 1635
| ELE | 38025-ELE | 1 | 400 | 236 | 636 |  | 01-636._L0 | 1636
| ELE | 38025-ELE | 1 | 400 | 237 | 637 |  | 01-637._L0 | 1637
| ELE | 38025-ELE | 1 | 400 | 238 | 638 |  | 01-638._L0 | 1638
| ELE | 38025-ELE | 1 | 400 | 239 | 639 |  | 01-639._L0 | 1639
| ELE | 38025-ELE | 1 | 400 | 240 | 640 |  | 01-640._L0 | 1640
| ELE | 38025-ELE | 1 | 400 | 241 | 641 |  | 01-641._L0 | 1641
| ELE | 38025-ELE | 1 | 400 | 242 | 642 |  | 01-642._L0 | 1642
| ELE | 38025-ELE | 1 | 400 | 243 | 643 |  | 01-643._L0 | 1643
| ELE | 38025-ELE | 1 | 400 | 244 | 644 |  | 01-644._L0 | 1644
| ELE | 38025-ELE | 1 | 400 | 245 | 645 |  | 01-645._L0 | 1645
| ELE | 38025-ELE | 1 | 400 | 246 | 646 |  | 01-646._L0 | 1646
| ELE | 38025-ELE | 1 | 400 | 247 | 647 |  | 01-647._L0 | 1647
| ELE | 38025-ELE | 1 | 400 | 248 | 648 |  | 01-648._L0 | 1648
| ELE | 38025-ELE | 1 | 400 | 249 | 649 |  | 01-649._L0 | 1649
| ELE | 38025-ELE | 1 | 400 | 250 | 650 |  | 01-650._L0 | 1650
| ELE | 38025-ELE | 1 | 400 | 251 | 651 |  | 01-651._L0 | 1651
| ELE | 38025-ELE | 1 | 400 | 252 | 652 |  | 01-652._L0 | 1652
| ELE | 38025-ELE | 1 | 400 | 253 | 653 |  | 01-653._L0 | 1653
| ELE | 38025-ELE | 1 | 400 | 254 | 654 |  | 01-654._L0 | 1654
| ELE | 38025-ELE | 1 | 400 | 255 | 655 |  | 01-655._L0 | 1655
| ELE | 38025-ELE | 1 | 400 | 256 | 656 |  | 01-656._L0 | 1656
| ELE | 38025-ELE | 1 | 400 | 257 | 657 |  | 01-657._L0 | 1657
| ELE | 38025-ELE | 1 | 400 | 258 | 658 |  | 01-658._L0 | 1658
| ELE | 38025-ELE | 1 | 400 | 259 | 659 |  | 01-659._L0 | 1659
| ELE | 38025-ELE | 1 | 400 | 260 | 660 |  | 01-660._L0 | 1660
| ELE | 38025-ELE | 1 | 400 | 261 | 661 |  | 01-661._L0 | 1661
| ELE | 38025-ELE | 1 | 400 | 262 | 662 |  | 01-662._L0 | 1662
| ELE | 38025-ELE | 1 | 400 | 263 | 663 |  | 01-663._L0 | 1663
| ELE | 38025-ELE | 1 | 400 | 264 | 664 |  | 01-664._L0 | 1664
| ELE | 38025-ELE | 1 | 400 | 265 | 665 |  | 01-665._L0 | 1665
| ELE | 38025-ELE | 1 | 400 | 266 | 666 |  | 01-666._L0 | 1666
| ELE | 38025-ELE | 1 | 400 | 267 | 667 |  | 01-667._L0 | 1667
| ELE | 38025-ELE | 1 | 400 | 268 | 668 |  | 01-668._L0 | 1668
| ELE | 38025-ELE | 1 | 400 | 269 | 669 |  | 01-669._L0 | 1669
| ELE | 38025-ELE | 1 | 400 | 270 | 670 |  | 01-670._L0 | 1670
| ELE | 38025-ELE | 1 | 400 | 271 | 671 |  | 01-671._L0 | 1671
| ELE | 38025-ELE | 1 | 400 | 272 | 672 |  | 01-672._L0 | 1672
| ELE | 38025-ELE | 1 | 400 | 273 | 673 |  | 01-673._L0 | 1673
| ELE | 38025-ELE | 1 | 400 | 274 | 674 |  | 01-674._L0 | 1674
| ELE | 38025-ELE | 1 | 400 | 275 | 675 |  | 01-675._L0 | 1675
| ELE | 38025-ELE | 1 | 400 | 276 | 676 |  | 01-676._L0 | 1676
| ELE | 38025-ELE | 1 | 400 | 277 | 677 |  | 01-677._L0 | 1677
| ELE | 38025-ELE | 1 | 400 | 278 | 678 |  | 01-678._L0 | 1678
| ELE | 38025-ELE | 1 | 400 | 279 | 679 |  | 01-679._L0 | 1679
| ELE | 38025-ELE | 1 | 400 | 280 | 680 |  | 01-680._L0 | 1680
| ELE | 38025-ELE | 1 | 400 | 281 | 681 |  | 01-681._L0 | 1681
| ELE | 38025-ELE | 1 | 400 | 282 | 682 |  | 01-682._L0 | 1682
| ELE | 38025-ELE | 1 | 400 | 283 | 683 |  | 01-683._L0 | 1683
| ELE | 38025-ELE | 1 | 400 | 284 | 684 |  | 01-684._L0 | 1684
| ELE | 38025-ELE | 1 | 400 | 285 | 685 |  | 01-685._L0 | 1685
| ELE | 38025-ELE | 1 | 400 | 286 | 686 |  | 01-686._L0 | 1686
| ELE | 38025-ELE | 1 | 400 | 287 | 687 |  | 01-687._L0 | 1687
| ELE | 38025-ELE | 1 | 400 | 288 | 688 |  | 01-688._L0 | 1688
| ELE | 38025-ELE | 1 | 400 | 289 | 689 |  | 01-689._L0 | 1689
| ELE | 38025-ELE | 1 | 400 | 290 | 690 |  | 01-690._L0 | 1690
| ELE | 38025-ELE | 1 | 400 | 291 | 691 |  | 01-691._L0 | 1691
| ELE | 38025-ELE | 1 | 400 | 292 | 692 |  | 01-692._L0 | 1692
| ELE | 38025-ELE | 1 | 400 | 293 | 693 |  | 01-693._L0 | 1693
| ELE | 38025-ELE | 1 | 400 | 294 | 694 |  | 01-694._L0 | 1694
| ELE | 38025-ELE | 1 | 400 | 295 | 695 |  | 01-695._L0 | 1695
| ELE | 38025-ELE | 1 | 400 | 296 | 696 |  | 01-696._L0 | 1696
Note on A1: Author: Generation of drawing number set is performed on this page

## X_PANEL
Tag | Description | _DeviceCount | 24VDC | 0VDC | Terminal | Fuse | 230VL1 | 230VN | DBTerminal | DBFuse | DBBreaker | Notes
KPA_FLOORX_IO | KPA NON ASSIGNED IO | 412
KPA_FLOOR0_IO | KPA LEVEL 0 REMOTE IO CABINET | 0
KPA_FLOOR1_IO | KPA LEVEL 1 REMOTE IO CABINET | 0
KPA_FLOOR2_IO | KPA LEVEL 2 REMOTE IO CABINET | 0
KPA_FLOOR3_IO | KPA LEVEL 3 REMOTE IO CABINET | 0
KPA_FLOOR4_IO | KPA LEVEL 4 REMOTE IO CABINET | 0
KPA_FUEL_STATION_IO | KPA FUEL STATION REMOTE IO CABINET | 0
KPA_MCC | KPA REMOTE IO INTERNAL TO MCC | 1
KPA_PLC | KPA PLC CABINET | 0
ESP_PLC | ESP PLC CABINET | 0
ESP_MCC | ESP REMOTE IO INTERNAL TO MCC | 0
0
Panel Assignment |  |  | Indices
_Drawing | _Tag | Assignment | 24VDC | 0VDC | Terminal | Fuse | 230V | 230VN | DBTerminal | DBFuse | DBBreaker | Notes | Q1CATN | Q1CATD | Q1NAME1 | Q1NAME2 | Q1TCATN | Q1TCATD | Q1TNAME | Q1TSETTO | X1NAME | X1DESC | X2NAME | X2DESC | C4NAME | C5NAME | W3NAME | W4NAME | W5NAME | W6NAME | W7NAME | W8NAME
01-100._L0 | DETAIL | KPA_FLOORX_IO |  |  | 1100 | F1100 | Q100 |  | 1100 | F1100 | Q100 | INCOMER | [12 empty] | /1 | DETAIL/ISO
01-101._L0 | DETAIL | KPA_MCC |  |  | 1101 | F1101 | Q101 |  | 1101 | F1101 | Q101 | PWR MONITOR | [12 empty] | /1 | DETAIL/ISO
01-102._L0 | DETAIL | KPA_FLOORX_IO |  |  | 1102 | F1102 | Q102 |  | 1102 | F1102 | Q102 | AHF | [12 empty] | /1 | DETAIL/ISO
01-103._L0 | DETAIL | KPA_FLOORX_IO |  |  | 1103 | F1103 | Q103 |  | 1103 | F1103 | Q103 | SURGE PROTECTION | [12 empty] | /1 | DETAIL/ISO
01-104._L0 | DETAIL | KPA_FLOORX_IO |  |  | 1104 | F1104 | Q104 |  | 1104 | F1104 | Q104 | FEEDERS | [12 empty] | /1 | DETAIL/ISO
01-105._L0 | DETAIL | KPA_FLOORX_IO |  |  | 1105 | F1105 | Q108 |  | 1105 | F1105 | Q108 | FEEDERS | [12 empty] | /1 | DETAIL/ISO
01-106._L0 | DETAIL | KPA_FLOORX_IO |  |  | 1106 | F1106 | Q111 |  | 1106 | F1106 | Q111 | FEEDERS | [12 empty] | /1 | DETAIL/ISO
01-507._L0 | BB1EM650 | KPA_FLOORX_IO |  |  | 1507 | F1507 | Q1507 |  | 1507 | F1507 | Q1507 | [13 empty] | /1 | BB1EM650/ISO
01-508._L0 | BB1EM658 | KPA_FLOORX_IO |  |  | 1508 | F1508 | Q1508 |  | 1508 | F1508 | Q1508 | [13 empty] | /1 | BB1EM658/ISO
01-509._L0 | BB1EM659 | KPA_FLOORX_IO |  |  | 1509 | F1509 | Q1509 |  | 1509 | F1509 | Q1509 | [13 empty] | /1 | BB1EM659/ISO
01-500._L0 | BB1EM662 | KPA_FLOORX_IO |  |  | 1500 | F1500 | Q1500 | N | 1500 | F1500 | Q1500 | GV2L10 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | KPA_MCC | MAIN MCC | BB1EM662_PB_STATION | LOCAL/FWD/REV | BB1EM662_PB_STATION/1 | BB1EM662/ISO
01-501._L0 | BB1EM663 | KPA_FLOORX_IO |  |  | 1501 | F1501 | Q100 | N | 1501 | F1501 | Q1501 | NSX100H/MA50 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | KPA_MCC | MAIN MCC | BB1EM663_PB_STATION | LOCAL/FWD/REV | BB1EM663_PB_STATION/1 | BB1EM663/ISO
01-502._L0 | BB1EM664 | KPA_FLOORX_IO |  |  | 1502 | F1502 | Q1502 | N | 1502 | F1502 | Q1502 | GV2L14 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | KPA_MCC | MAIN MCC | BB1EM664_PB_STATION | LOCAL/FWD/REV | BB1EM664_PB_STATION/1 | BB1EM664/ISO
01-503._L0 | BB1EM665 | KPA_FLOORX_IO |  |  | 1503 | F1503 | Q100 | N | 1503 | F1503 | Q1503 | NSX100H/MA100 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | KPA_MCC | MAIN MCC | BB1EM665_PB_STATION | LOCAL/FWD/REV | BB1EM665_PB_STATION/1 | BB1EM665/ISO
01-504._L0 | BB1EM672 | KPA_FLOORX_IO |  |  | 1504 | F1504 | Q1504 | N | 1504 | F1504 | Q1504 | GV2L14 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | KPA_MCC | MAIN MCC | BB1EM672_PB_STATION | LOCAL/FWD/REV | BB1EM672_PB_STATION/1 | BB1EM672/ISO
01-505._L0 | BB1EM676 | KPA_FLOORX_IO |  |  | 1505 | F1505 | Q1505 | N | 1505 | F1505 | Q1505 | GV2L16 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | KPA_MCC | MAIN MCC | BB1EM676_PB_STATION | LOCAL/FWD/REV | BB1EM676_PB_STATION/1 | BB1EM676/ISO
01-506._L0 | BB1EM852 | KPA_FLOORX_IO |  |  | 1506 | F1506 | Q1506 | N | 1506 | F1506 | Q1506 | GV2L16 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | KPA_MCC | MAIN MCC | BB1EM852_PB_STATION | LOCAL/FWD/REV | BB1EM852_PB_STATION/1 | BB1EM852/ISO
01-507._L0 | BB1EM650 | KPA_FLOORX_IO |  |  | 1507 | F1507 | Q100 | N | 1507 | F1507 | Q1507 | NSX100H/MA50 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | KPA_MCC | MAIN MCC | BB1EM650_PB_STATION | LOCAL/FWD/REV | BB1EM650_PB_STATION/1 | BB1EM650/ISO
01-508._L0 | BB1EM658 | KPA_FLOORX_IO |  |  | 1508 | F1508 | Q1508 | N | 1508 | F1508 | Q1508 | GV2L22 | GV2L22 | 3P CIRCUIT BREAKER, TESYS GV2L, 25A | SCHNEIDER GV2L22 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 22A | KPA_MCC | MAIN MCC | BB1EM658_PB_STATION | LOCAL/FWD/REV | BB1EM658_PB_STATION/1 | BB1EM658/ISO
01-509._L0 | BB1EM659 | KPA_FLOORX_IO |  |  | 1509 | F1509 | Q1509 | N | 1509 | F1509 | Q1509 | GV2L10 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | KPA_MCC | MAIN MCC | BB1EM659_PB_STATION | LOCAL/FWD/REV | BB1EM659_PB_STATION/1 | BB1EM659/ISO
01-400._L0 | BB1EM662 | KPA_FLOORX_IO |  |  | 1400 | F1400 | Q1400 |  | 1400 | F1400 | Q1400 | [13 empty] | /1 | BB1EM662/ISO
01-401._L0 | BB1EM663 | KPA_FLOORX_IO |  |  | 1401 | F1401 | Q1401 |  | 1401 | F1401 | Q1401 | [13 empty] | /1 | BB1EM663/ISO
01-402._L0 | BB1EM664 | KPA_FLOORX_IO |  |  | 1402 | F1402 | Q1402 |  | 1402 | F1402 | Q1402 | [13 empty] | /1 | BB1EM664/ISO
01-403._L0 | BB1EM665 | KPA_FLOORX_IO |  |  | 1403 | F1403 | Q1403 |  | 1403 | F1403 | Q1403 | [13 empty] | /1 | BB1EM665/ISO
01-404._L0 | BB1EM672 | KPA_FLOORX_IO |  |  | 1404 | F1404 | Q1404 |  | 1404 | F1404 | Q1404 | [13 empty] | /1 | BB1EM672/ISO
01-405._L0 | BB1EM676 | KPA_FLOORX_IO |  |  | 1405 | F1405 | Q1405 |  | 1405 | F1405 | Q1405 | [13 empty] | /1 | BB1EM676/ISO
01-406._L0 | BB1EM852 | KPA_FLOORX_IO |  |  | 1406 | F1406 | Q1406 |  | 1406 | F1406 | Q1406 | [13 empty] | /1 | BB1EM852/ISO
01-407._L0 | 0 | KPA_FLOORX_IO |  |  | 1407 | F1407 | Q1407 |  | 1407 | F1407 | Q1407 | [13 empty] | /1 | 0/ISO
01-408._L0 | 0 | KPA_FLOORX_IO |  |  | 1408 | F1408 | Q1408 |  | 1408 | F1408 | Q1408 | [13 empty] | /1 | 0/ISO
01-409._L0 | 0 | KPA_FLOORX_IO |  |  | 1409 | F1409 | Q1409 |  | 1409 | F1409 | Q1409 | [13 empty] | /1 | 0/ISO
01-410._L0 | 0 | KPA_FLOORX_IO |  |  | 1410 | F1410 | Q1410 |  | 1410 | F1410 | Q1410 | [13 empty] | /1 | 0/ISO
01-411._L0 | 0 | KPA_FLOORX_IO |  |  | 1411 | F1411 | Q1411 |  | 1411 | F1411 | Q1411 | [13 empty] | /1 | 0/ISO
01-412._L0 | 0 | KPA_FLOORX_IO |  |  | 1412 | F1412 | Q1412 |  | 1412 | F1412 | Q1412 | [13 empty] | /1 | 0/ISO
01-413._L0 | 0 | KPA_FLOORX_IO |  |  | 1413 | F1413 | Q1413 |  | 1413 | F1413 | Q1413 | [13 empty] | /1 | 0/ISO
01-414._L0 | 0 | KPA_FLOORX_IO |  |  | 1414 | F1414 | Q1414 |  | 1414 | F1414 | Q1414 | [13 empty] | /1 | 0/ISO
01-415._L0 | 0 | KPA_FLOORX_IO |  |  | 1415 | F1415 | Q1415 |  | 1415 | F1415 | Q1415 | [13 empty] | /1 | 0/ISO
01-416._L0 | 0 | KPA_FLOORX_IO |  |  | 1416 | F1416 | Q1416 |  | 1416 | F1416 | Q1416 | [13 empty] | /1 | 0/ISO
01-417._L0 | 0 | KPA_FLOORX_IO |  |  | 1417 | F1417 | Q1417 |  | 1417 | F1417 | Q1417 | [13 empty] | /1 | 0/ISO
01-418._L0 | 0 | KPA_FLOORX_IO |  |  | 1418 | F1418 | Q1418 |  | 1418 | F1418 | Q1418 | [13 empty] | /1 | 0/ISO
01-419._L0 | 0 | KPA_FLOORX_IO |  |  | 1419 | F1419 | Q1419 |  | 1419 | F1419 | Q1419 | [13 empty] | /1 | 0/ISO
01-420._L0 | 0 | KPA_FLOORX_IO |  |  | 1420 | F1420 | Q1420 |  | 1420 | F1420 | Q1420 | [13 empty] | /1 | 0/ISO
01-421._L0 | 0 | KPA_FLOORX_IO |  |  | 1421 | F1421 | Q1421 |  | 1421 | F1421 | Q1421 | [13 empty] | /1 | 0/ISO
01-422._L0 | 0 | KPA_FLOORX_IO |  |  | 1422 | F1422 | Q1422 |  | 1422 | F1422 | Q1422 | [13 empty] | /1 | 0/ISO
01-423._L0 | 0 | KPA_FLOORX_IO |  |  | 1423 | F1423 | Q1423 |  | 1423 | F1423 | Q1423 | [13 empty] | /1 | 0/ISO
01-424._L0 | 0 | KPA_FLOORX_IO |  |  | 1424 | F1424 | Q1424 |  | 1424 | F1424 | Q1424 | [13 empty] | /1 | 0/ISO
01-425._L0 | 0 | KPA_FLOORX_IO |  |  | 1425 | F1425 | Q1425 |  | 1425 | F1425 | Q1425 | [13 empty] | /1 | 0/ISO
01-426._L0 | 0 | KPA_FLOORX_IO |  |  | 1426 | F1426 | Q1426 |  | 1426 | F1426 | Q1426 | [13 empty] | /1 | 0/ISO
01-427._L0 | 0 | KPA_FLOORX_IO |  |  | 1427 | F1427 | Q1427 |  | 1427 | F1427 | Q1427 | [13 empty] | /1 | 0/ISO
01-428._L0 | 0 | KPA_FLOORX_IO |  |  | 1428 | F1428 | Q1428 |  | 1428 | F1428 | Q1428 | [13 empty] | /1 | 0/ISO
01-429._L0 | 0 | KPA_FLOORX_IO |  |  | 1429 | F1429 | Q1429 |  | 1429 | F1429 | Q1429 | [13 empty] | /1 | 0/ISO
01-430._L0 | 0 | KPA_FLOORX_IO |  |  | 1430 | F1430 | Q1430 |  | 1430 | F1430 | Q1430 | [13 empty] | /1 | 0/ISO
01-431._L0 | 0 | KPA_FLOORX_IO |  |  | 1431 | F1431 | Q1431 |  | 1431 | F1431 | Q1431 | [13 empty] | /1 | 0/ISO
01-432._L0 | 0 | KPA_FLOORX_IO |  |  | 1432 | F1432 | Q1432 |  | 1432 | F1432 | Q1432 | [13 empty] | /1 | 0/ISO
01-433._L0 | 0 | KPA_FLOORX_IO |  |  | 1433 | F1433 | Q1433 |  | 1433 | F1433 | Q1433 | [13 empty] | /1 | 0/ISO
01-434._L0 | 0 | KPA_FLOORX_IO |  |  | 1434 | F1434 | Q1434 |  | 1434 | F1434 | Q1434 | [13 empty] | /1 | 0/ISO
01-435._L0 | 0 | KPA_FLOORX_IO |  |  | 1435 | F1435 | Q1435 |  | 1435 | F1435 | Q1435 | [13 empty] | /1 | 0/ISO
01-436._L0 | 0 | KPA_FLOORX_IO |  |  | 1436 | F1436 | Q1436 |  | 1436 | F1436 | Q1436 | [13 empty] | /1 | 0/ISO
01-437._L0 | 0 | KPA_FLOORX_IO |  |  | 1437 | F1437 | Q1437 |  | 1437 | F1437 | Q1437 | [13 empty] | /1 | 0/ISO
01-438._L0 | 0 | KPA_FLOORX_IO |  |  | 1438 | F1438 | Q1438 |  | 1438 | F1438 | Q1438 | [13 empty] | /1 | 0/ISO
01-439._L0 | 0 | KPA_FLOORX_IO |  |  | 1439 | F1439 | Q1439 |  | 1439 | F1439 | Q1439 | [13 empty] | /1 | 0/ISO
01-440._L0 | 0 | KPA_FLOORX_IO |  |  | 1440 | F1440 | Q1440 |  | 1440 | F1440 | Q1440 | [13 empty] | /1 | 0/ISO
01-441._L0 | 0 | KPA_FLOORX_IO |  |  | 1441 | F1441 | Q1441 |  | 1441 | F1441 | Q1441 | [13 empty] | /1 | 0/ISO
01-442._L0 | 0 | KPA_FLOORX_IO |  |  | 1442 | F1442 | Q1442 |  | 1442 | F1442 | Q1442 | [13 empty] | /1 | 0/ISO
01-443._L0 | 0 | KPA_FLOORX_IO |  |  | 1443 | F1443 | Q1443 |  | 1443 | F1443 | Q1443 | [13 empty] | /1 | 0/ISO
01-444._L0 | 0 | KPA_FLOORX_IO |  |  | 1444 | F1444 | Q1444 |  | 1444 | F1444 | Q1444 | [13 empty] | /1 | 0/ISO
01-445._L0 | 0 | KPA_FLOORX_IO |  |  | 1445 | F1445 | Q1445 |  | 1445 | F1445 | Q1445 | [13 empty] | /1 | 0/ISO
01-446._L0 | 0 | KPA_FLOORX_IO |  |  | 1446 | F1446 | Q1446 |  | 1446 | F1446 | Q1446 | [13 empty] | /1 | 0/ISO
01-447._L0 | 0 | KPA_FLOORX_IO |  |  | 1447 | F1447 | Q1447 |  | 1447 | F1447 | Q1447 | [13 empty] | /1 | 0/ISO
01-448._L0 | 0 | KPA_FLOORX_IO |  |  | 1448 | F1448 | Q1448 |  | 1448 | F1448 | Q1448 | [13 empty] | /1 | 0/ISO
01-449._L0 | 0 | KPA_FLOORX_IO |  |  | 1449 | F1449 | Q1449 |  | 1449 | F1449 | Q1449 | [13 empty] | /1 | 0/ISO
01-450._L0 | 0 | KPA_FLOORX_IO |  |  | 1450 | F1450 | Q1450 |  | 1450 | F1450 | Q1450 | [13 empty] | /1 | 0/ISO
01-451._L0 | 0 | KPA_FLOORX_IO |  |  | 1451 | F1451 | Q1451 |  | 1451 | F1451 | Q1451 | [13 empty] | /1 | 0/ISO
01-452._L0 | 0 | KPA_FLOORX_IO |  |  | 1452 | F1452 | Q1452 |  | 1452 | F1452 | Q1452 | [13 empty] | /1 | 0/ISO
01-453._L0 | 0 | KPA_FLOORX_IO |  |  | 1453 | F1453 | Q1453 |  | 1453 | F1453 | Q1453 | [13 empty] | /1 | 0/ISO
01-454._L0 | 0 | KPA_FLOORX_IO |  |  | 1454 | F1454 | Q1454 |  | 1454 | F1454 | Q1454 | [13 empty] | /1 | 0/ISO
01-455._L0 | 0 | KPA_FLOORX_IO |  |  | 1455 | F1455 | Q1455 |  | 1455 | F1455 | Q1455 | [13 empty] | /1 | 0/ISO
01-456._L0 | 0 | KPA_FLOORX_IO |  |  | 1456 | F1456 | Q1456 |  | 1456 | F1456 | Q1456 | [13 empty] | /1 | 0/ISO
01-457._L0 | 0 | KPA_FLOORX_IO |  |  | 1457 | F1457 | Q1457 |  | 1457 | F1457 | Q1457 | [13 empty] | /1 | 0/ISO
01-458._L0 | 0 | KPA_FLOORX_IO |  |  | 1458 | F1458 | Q1458 |  | 1458 | F1458 | Q1458 | [13 empty] | /1 | 0/ISO
01-459._L0 | 0 | KPA_FLOORX_IO |  |  | 1459 | F1459 | Q1459 |  | 1459 | F1459 | Q1459 | [13 empty] | /1 | 0/ISO
01-460._L0 | 0 | KPA_FLOORX_IO |  |  | 1460 | F1460 | Q1460 |  | 1460 | F1460 | Q1460 | [13 empty] | /1 | 0/ISO
01-461._L0 | 0 | KPA_FLOORX_IO |  |  | 1461 | F1461 | Q1461 |  | 1461 | F1461 | Q1461 | [13 empty] | /1 | 0/ISO
01-462._L0 | 0 | KPA_FLOORX_IO |  |  | 1462 | F1462 | Q1462 |  | 1462 | F1462 | Q1462 | [13 empty] | /1 | 0/ISO
01-463._L0 | 0 | KPA_FLOORX_IO |  |  | 1463 | F1463 | Q1463 |  | 1463 | F1463 | Q1463 | [13 empty] | /1 | 0/ISO
01-464._L0 | 0 | KPA_FLOORX_IO |  |  | 1464 | F1464 | Q1464 |  | 1464 | F1464 | Q1464 | [13 empty] | /1 | 0/ISO
01-465._L0 | 0 | KPA_FLOORX_IO |  |  | 1465 | F1465 | Q1465 |  | 1465 | F1465 | Q1465 | [13 empty] | /1 | 0/ISO
01-466._L0 | 0 | KPA_FLOORX_IO |  |  | 1466 | F1466 | Q1466 |  | 1466 | F1466 | Q1466 | [13 empty] | /1 | 0/ISO
01-467._L0 | 0 | KPA_FLOORX_IO |  |  | 1467 | F1467 | Q1467 |  | 1467 | F1467 | Q1467 | [13 empty] | /1 | 0/ISO
01-468._L0 | 0 | KPA_FLOORX_IO |  |  | 1468 | F1468 | Q1468 |  | 1468 | F1468 | Q1468 | [13 empty] | /1 | 0/ISO
01-469._L0 | 0 | KPA_FLOORX_IO |  |  | 1469 | F1469 | Q1469 |  | 1469 | F1469 | Q1469 | [13 empty] | /1 | 0/ISO
01-470._L0 | 0 | KPA_FLOORX_IO |  |  | 1470 | F1470 | Q1470 |  | 1470 | F1470 | Q1470 | [13 empty] | /1 | 0/ISO
01-471._L0 | 0 | KPA_FLOORX_IO |  |  | 1471 | F1471 | Q1471 |  | 1471 | F1471 | Q1471 | [13 empty] | /1 | 0/ISO
01-472._L0 | 0 | KPA_FLOORX_IO |  |  | 1472 | F1472 | Q1472 |  | 1472 | F1472 | Q1472 | [13 empty] | /1 | 0/ISO
01-473._L0 | 0 | KPA_FLOORX_IO |  |  | 1473 | F1473 | Q1473 |  | 1473 | F1473 | Q1473 | [13 empty] | /1 | 0/ISO
01-474._L0 | 0 | KPA_FLOORX_IO |  |  | 1474 | F1474 | Q1474 |  | 1474 | F1474 | Q1474 | [13 empty] | /1 | 0/ISO
01-475._L0 | 0 | KPA_FLOORX_IO |  |  | 1475 | F1475 | Q1475 |  | 1475 | F1475 | Q1475 | [13 empty] | /1 | 0/ISO
01-476._L0 | 0 | KPA_FLOORX_IO |  |  | 1476 | F1476 | Q1476 |  | 1476 | F1476 | Q1476 | [13 empty] | /1 | 0/ISO
01-477._L0 | 0 | KPA_FLOORX_IO |  |  | 1477 | F1477 | Q1477 |  | 1477 | F1477 | Q1477 | [13 empty] | /1 | 0/ISO
01-478._L0 | 0 | KPA_FLOORX_IO |  |  | 1478 | F1478 | Q1478 |  | 1478 | F1478 | Q1478 | [13 empty] | /1 | 0/ISO
01-479._L0 | 0 | KPA_FLOORX_IO |  |  | 1479 | F1479 | Q1479 |  | 1479 | F1479 | Q1479 | [13 empty] | /1 | 0/ISO
01-480._L0 | 0 | KPA_FLOORX_IO |  |  | 1480 | F1480 | Q1480 |  | 1480 | F1480 | Q1480 | [13 empty] | /1 | 0/ISO
01-481._L0 | 0 | KPA_FLOORX_IO |  |  | 1481 | F1481 | Q1481 |  | 1481 | F1481 | Q1481 | [13 empty] | /1 | 0/ISO
01-482._L0 | 0 | KPA_FLOORX_IO |  |  | 1482 | F1482 | Q1482 |  | 1482 | F1482 | Q1482 | [13 empty] | /1 | 0/ISO
01-483._L0 | 0 | KPA_FLOORX_IO |  |  | 1483 | F1483 | Q1483 |  | 1483 | F1483 | Q1483 | [13 empty] | /1 | 0/ISO
01-484._L0 | 0 | KPA_FLOORX_IO |  |  | 1484 | F1484 | Q1484 |  | 1484 | F1484 | Q1484 | [13 empty] | /1 | 0/ISO
01-485._L0 | 0 | KPA_FLOORX_IO |  |  | 1485 | F1485 | Q1485 |  | 1485 | F1485 | Q1485 | [13 empty] | /1 | 0/ISO
01-486._L0 | 0 | KPA_FLOORX_IO |  |  | 1486 | F1486 | Q1486 |  | 1486 | F1486 | Q1486 | [13 empty] | /1 | 0/ISO
01-487._L0 | 0 | KPA_FLOORX_IO |  |  | 1487 | F1487 | Q1487 |  | 1487 | F1487 | Q1487 | [13 empty] | /1 | 0/ISO
01-488._L0 | 0 | KPA_FLOORX_IO |  |  | 1488 | F1488 | Q1488 |  | 1488 | F1488 | Q1488 | [13 empty] | /1 | 0/ISO
01-489._L0 | 0 | KPA_FLOORX_IO |  |  | 1489 | F1489 | Q1489 |  | 1489 | F1489 | Q1489 | [13 empty] | /1 | 0/ISO
01-490._L0 | 0 | KPA_FLOORX_IO |  |  | 1490 | F1490 | Q1490 |  | 1490 | F1490 | Q1490 | [13 empty] | /1 | 0/ISO
01-491._L0 | 0 | KPA_FLOORX_IO |  |  | 1491 | F1491 | Q1491 |  | 1491 | F1491 | Q1491 | [13 empty] | /1 | 0/ISO
01-492._L0 | 0 | KPA_FLOORX_IO |  |  | 1492 | F1492 | Q1492 |  | 1492 | F1492 | Q1492 | [13 empty] | /1 | 0/ISO
01-493._L0 | 0 | KPA_FLOORX_IO |  |  | 1493 | F1493 | Q1493 |  | 1493 | F1493 | Q1493 | [13 empty] | /1 | 0/ISO
01-494._L0 | 0 | KPA_FLOORX_IO |  |  | 1494 | F1494 | Q1494 |  | 1494 | F1494 | Q1494 | [13 empty] | /1 | 0/ISO
01-495._L0 | 0 | KPA_FLOORX_IO |  |  | 1495 | F1495 | Q1495 |  | 1495 | F1495 | Q1495 | [13 empty] | /1 | 0/ISO
01-496._L0 | 0 | KPA_FLOORX_IO |  |  | 1496 | F1496 | Q1496 |  | 1496 | F1496 | Q1496 | [13 empty] | /1 | 0/ISO
01-497._L0 | 0 | KPA_FLOORX_IO |  |  | 1497 | F1497 | Q1497 |  | 1497 | F1497 | Q1497 | [13 empty] | /1 | 0/ISO
01-498._L0 | 0 | KPA_FLOORX_IO |  |  | 1498 | F1498 | Q1498 |  | 1498 | F1498 | Q1498 | [13 empty] | /1 | 0/ISO
01-499._L0 | 0 | KPA_FLOORX_IO |  |  | 1499 | F1499 | Q1499 |  | 1499 | F1499 | Q1499 | [13 empty] | /1 | 0/ISO
01-500._L0 | 0 | KPA_FLOORX_IO |  |  | 1500 | F1500 | Q1500 |  | 1500 | F1500 | Q1500 | [13 empty] | /1 | 0/ISO
01-501._L0 | 0 | KPA_FLOORX_IO |  |  | 1501 | F1501 | Q1501 |  | 1501 | F1501 | Q1501 | [13 empty] | /1 | 0/ISO
01-502._L0 | 0 | KPA_FLOORX_IO |  |  | 1502 | F1502 | Q1502 |  | 1502 | F1502 | Q1502 | [13 empty] | /1 | 0/ISO
01-503._L0 | 0 | KPA_FLOORX_IO |  |  | 1503 | F1503 | Q1503 |  | 1503 | F1503 | Q1503 | [13 empty] | /1 | 0/ISO
01-504._L0 | 0 | KPA_FLOORX_IO |  |  | 1504 | F1504 | Q1504 |  | 1504 | F1504 | Q1504 | [13 empty] | /1 | 0/ISO
01-505._L0 | 0 | KPA_FLOORX_IO |  |  | 1505 | F1505 | Q1505 |  | 1505 | F1505 | Q1505 | [13 empty] | /1 | 0/ISO
01-506._L0 | 0 | KPA_FLOORX_IO |  |  | 1506 | F1506 | Q1506 |  | 1506 | F1506 | Q1506 | [13 empty] | /1 | 0/ISO
01-507._L0 | 0 | KPA_FLOORX_IO |  |  | 1507 | F1507 | Q1507 |  | 1507 | F1507 | Q1507 | [13 empty] | /1 | 0/ISO
01-508._L0 | 0 | KPA_FLOORX_IO |  |  | 1508 | F1508 | Q1508 |  | 1508 | F1508 | Q1508 | [13 empty] | /1 | 0/ISO
01-509._L0 | 0 | KPA_FLOORX_IO |  |  | 1509 | F1509 | Q1509 |  | 1509 | F1509 | Q1509 | [13 empty] | /1 | 0/ISO
01-510._L0 | 0 | KPA_FLOORX_IO |  |  | 1510 | F1510 | Q1510 |  | 1510 | F1510 | Q1510 | [13 empty] | /1 | 0/ISO
01-511._L0 | 0 | KPA_FLOORX_IO |  |  | 1511 | F1511 | Q1511 |  | 1511 | F1511 | Q1511 | [13 empty] | /1 | 0/ISO
01-512._L0 | 0 | KPA_FLOORX_IO |  |  | 1512 | F1512 | Q1512 |  | 1512 | F1512 | Q1512 | [13 empty] | /1 | 0/ISO
01-513._L0 | 0 | KPA_FLOORX_IO |  |  | 1513 | F1513 | Q1513 |  | 1513 | F1513 | Q1513 | [13 empty] | /1 | 0/ISO
01-514._L0 | 0 | KPA_FLOORX_IO |  |  | 1514 | F1514 | Q1514 |  | 1514 | F1514 | Q1514 | [13 empty] | /1 | 0/ISO
01-515._L0 | 0 | KPA_FLOORX_IO |  |  | 1515 | F1515 | Q1515 |  | 1515 | F1515 | Q1515 | [13 empty] | /1 | 0/ISO
01-516._L0 | 0 | KPA_FLOORX_IO |  |  | 1516 | F1516 | Q1516 |  | 1516 | F1516 | Q1516 | [13 empty] | /1 | 0/ISO
01-517._L0 | 0 | KPA_FLOORX_IO |  |  | 1517 | F1517 | Q1517 |  | 1517 | F1517 | Q1517 | [13 empty] | /1 | 0/ISO
01-518._L0 | 0 | KPA_FLOORX_IO |  |  | 1518 | F1518 | Q1518 |  | 1518 | F1518 | Q1518 | [13 empty] | /1 | 0/ISO
01-519._L0 | 0 | KPA_FLOORX_IO |  |  | 1519 | F1519 | Q1519 |  | 1519 | F1519 | Q1519 | [13 empty] | /1 | 0/ISO
01-520._L0 | 0 | KPA_FLOORX_IO |  |  | 1520 | F1520 | Q1520 |  | 1520 | F1520 | Q1520 | [13 empty] | /1 | 0/ISO
01-521._L0 | 0 | KPA_FLOORX_IO |  |  | 1521 | F1521 | Q1521 |  | 1521 | F1521 | Q1521 | [13 empty] | /1 | 0/ISO
01-522._L0 | 0 | KPA_FLOORX_IO |  |  | 1522 | F1522 | Q1522 |  | 1522 | F1522 | Q1522 | [13 empty] | /1 | 0/ISO
01-523._L0 | 0 | KPA_FLOORX_IO |  |  | 1523 | F1523 | Q1523 |  | 1523 | F1523 | Q1523 | [13 empty] | /1 | 0/ISO
01-524._L0 | 0 | KPA_FLOORX_IO |  |  | 1524 | F1524 | Q1524 |  | 1524 | F1524 | Q1524 | [13 empty] | /1 | 0/ISO
01-525._L0 | 0 | KPA_FLOORX_IO |  |  | 1525 | F1525 | Q1525 |  | 1525 | F1525 | Q1525 | [13 empty] | /1 | 0/ISO
01-526._L0 | 0 | KPA_FLOORX_IO |  |  | 1526 | F1526 | Q1526 |  | 1526 | F1526 | Q1526 | [13 empty] | /1 | 0/ISO
01-527._L0 | 0 | KPA_FLOORX_IO |  |  | 1527 | F1527 | Q1527 |  | 1527 | F1527 | Q1527 | [13 empty] | /1 | 0/ISO
01-528._L0 | 0 | KPA_FLOORX_IO |  |  | 1528 | F1528 | Q1528 |  | 1528 | F1528 | Q1528 | [13 empty] | /1 | 0/ISO
01-529._L0 | 0 | KPA_FLOORX_IO |  |  | 1529 | F1529 | Q1529 |  | 1529 | F1529 | Q1529 | [13 empty] | /1 | 0/ISO
01-530._L0 | 0 | KPA_FLOORX_IO |  |  | 1530 | F1530 | Q1530 |  | 1530 | F1530 | Q1530 | [13 empty] | /1 | 0/ISO
01-531._L0 | 0 | KPA_FLOORX_IO |  |  | 1531 | F1531 | Q1531 |  | 1531 | F1531 | Q1531 | [13 empty] | /1 | 0/ISO
01-532._L0 | 0 | KPA_FLOORX_IO |  |  | 1532 | F1532 | Q1532 |  | 1532 | F1532 | Q1532 | [13 empty] | /1 | 0/ISO
01-533._L0 | 0 | KPA_FLOORX_IO |  |  | 1533 | F1533 | Q1533 |  | 1533 | F1533 | Q1533 | [13 empty] | /1 | 0/ISO
01-534._L0 | 0 | KPA_FLOORX_IO |  |  | 1534 | F1534 | Q1534 |  | 1534 | F1534 | Q1534 | [13 empty] | /1 | 0/ISO
01-535._L0 | 0 | KPA_FLOORX_IO |  |  | 1535 | F1535 | Q1535 |  | 1535 | F1535 | Q1535 | [13 empty] | /1 | 0/ISO
01-536._L0 | 0 | KPA_FLOORX_IO |  |  | 1536 | F1536 | Q1536 |  | 1536 | F1536 | Q1536 | [13 empty] | /1 | 0/ISO
01-537._L0 | 0 | KPA_FLOORX_IO |  |  | 1537 | F1537 | Q1537 |  | 1537 | F1537 | Q1537 | [13 empty] | /1 | 0/ISO
01-538._L0 | 0 | KPA_FLOORX_IO |  |  | 1538 | F1538 | Q1538 |  | 1538 | F1538 | Q1538 | [13 empty] | /1 | 0/ISO
01-539._L0 | 0 | KPA_FLOORX_IO |  |  | 1539 | F1539 | Q1539 |  | 1539 | F1539 | Q1539 | [13 empty] | /1 | 0/ISO
01-540._L0 | 0 | KPA_FLOORX_IO |  |  | 1540 | F1540 | Q1540 |  | 1540 | F1540 | Q1540 | [13 empty] | /1 | 0/ISO
01-541._L0 | 0 | KPA_FLOORX_IO |  |  | 1541 | F1541 | Q1541 |  | 1541 | F1541 | Q1541 | [13 empty] | /1 | 0/ISO
01-542._L0 | 0 | KPA_FLOORX_IO |  |  | 1542 | F1542 | Q1542 |  | 1542 | F1542 | Q1542 | [13 empty] | /1 | 0/ISO
01-543._L0 | 0 | KPA_FLOORX_IO |  |  | 1543 | F1543 | Q1543 |  | 1543 | F1543 | Q1543 | [13 empty] | /1 | 0/ISO
01-544._L0 | 0 | KPA_FLOORX_IO |  |  | 1544 | F1544 | Q1544 |  | 1544 | F1544 | Q1544 | [13 empty] | /1 | 0/ISO
01-545._L0 | 0 | KPA_FLOORX_IO |  |  | 1545 | F1545 | Q1545 |  | 1545 | F1545 | Q1545 | [13 empty] | /1 | 0/ISO
01-546._L0 | 0 | KPA_FLOORX_IO |  |  | 1546 | F1546 | Q1546 |  | 1546 | F1546 | Q1546 | [13 empty] | /1 | 0/ISO
01-547._L0 | 0 | KPA_FLOORX_IO |  |  | 1547 | F1547 | Q1547 |  | 1547 | F1547 | Q1547 | [13 empty] | /1 | 0/ISO
01-548._L0 | 0 | KPA_FLOORX_IO |  |  | 1548 | F1548 | Q1548 |  | 1548 | F1548 | Q1548 | [13 empty] | /1 | 0/ISO
01-549._L0 | 0 | KPA_FLOORX_IO |  |  | 1549 | F1549 | Q1549 |  | 1549 | F1549 | Q1549 | [13 empty] | /1 | 0/ISO
01-550._L0 | 0 | KPA_FLOORX_IO |  |  | 1550 | F1550 | Q1550 |  | 1550 | F1550 | Q1550 | [13 empty] | /1 | 0/ISO
01-551._L0 | 0 | KPA_FLOORX_IO |  |  | 1551 | F1551 | Q1551 |  | 1551 | F1551 | Q1551 | [13 empty] | /1 | 0/ISO
01-552._L0 | 0 | KPA_FLOORX_IO |  |  | 1552 | F1552 | Q1552 |  | 1552 | F1552 | Q1552 | [13 empty] | /1 | 0/ISO
01-553._L0 | 0 | KPA_FLOORX_IO |  |  | 1553 | F1553 | Q1553 |  | 1553 | F1553 | Q1553 | [13 empty] | /1 | 0/ISO
01-554._L0 | 0 | KPA_FLOORX_IO |  |  | 1554 | F1554 | Q1554 |  | 1554 | F1554 | Q1554 | [13 empty] | /1 | 0/ISO
01-555._L0 | 0 | KPA_FLOORX_IO |  |  | 1555 | F1555 | Q1555 |  | 1555 | F1555 | Q1555 | [13 empty] | /1 | 0/ISO
01-556._L0 | 0 | KPA_FLOORX_IO |  |  | 1556 | F1556 | Q1556 |  | 1556 | F1556 | Q1556 | [13 empty] | /1 | 0/ISO
01-557._L0 | 0 | KPA_FLOORX_IO |  |  | 1557 | F1557 | Q1557 |  | 1557 | F1557 | Q1557 | [13 empty] | /1 | 0/ISO
01-558._L0 | 0 | KPA_FLOORX_IO |  |  | 1558 | F1558 | Q1558 |  | 1558 | F1558 | Q1558 | [13 empty] | /1 | 0/ISO
01-559._L0 | 0 | KPA_FLOORX_IO |  |  | 1559 | F1559 | Q1559 |  | 1559 | F1559 | Q1559 | [13 empty] | /1 | 0/ISO
01-560._L0 | 0 | KPA_FLOORX_IO |  |  | 1560 | F1560 | Q1560 |  | 1560 | F1560 | Q1560 | [13 empty] | /1 | 0/ISO
01-561._L0 | 0 | KPA_FLOORX_IO |  |  | 1561 | F1561 | Q1561 |  | 1561 | F1561 | Q1561 | [13 empty] | /1 | 0/ISO
01-562._L0 | 0 | KPA_FLOORX_IO |  |  | 1562 | F1562 | Q1562 |  | 1562 | F1562 | Q1562 | [13 empty] | /1 | 0/ISO
01-563._L0 | 0 | KPA_FLOORX_IO |  |  | 1563 | F1563 | Q1563 |  | 1563 | F1563 | Q1563 | [13 empty] | /1 | 0/ISO
01-564._L0 | 0 | KPA_FLOORX_IO |  |  | 1564 | F1564 | Q1564 |  | 1564 | F1564 | Q1564 | [13 empty] | /1 | 0/ISO
01-565._L0 | 0 | KPA_FLOORX_IO |  |  | 1565 | F1565 | Q1565 |  | 1565 | F1565 | Q1565 | [13 empty] | /1 | 0/ISO
01-566._L0 | 0 | KPA_FLOORX_IO |  |  | 1566 | F1566 | Q1566 |  | 1566 | F1566 | Q1566 | [13 empty] | /1 | 0/ISO
01-567._L0 | 0 | KPA_FLOORX_IO |  |  | 1567 | F1567 | Q1567 |  | 1567 | F1567 | Q1567 | [13 empty] | /1 | 0/ISO
01-568._L0 | 0 | KPA_FLOORX_IO |  |  | 1568 | F1568 | Q1568 |  | 1568 | F1568 | Q1568 | [13 empty] | /1 | 0/ISO
01-569._L0 | 0 | KPA_FLOORX_IO |  |  | 1569 | F1569 | Q1569 |  | 1569 | F1569 | Q1569 | [13 empty] | /1 | 0/ISO
01-570._L0 | 0 | KPA_FLOORX_IO |  |  | 1570 | F1570 | Q1570 |  | 1570 | F1570 | Q1570 | [13 empty] | /1 | 0/ISO
01-571._L0 | 0 | KPA_FLOORX_IO |  |  | 1571 | F1571 | Q1571 |  | 1571 | F1571 | Q1571 | [13 empty] | /1 | 0/ISO
01-572._L0 | 0 | KPA_FLOORX_IO |  |  | 1572 | F1572 | Q1572 |  | 1572 | F1572 | Q1572 | [13 empty] | /1 | 0/ISO
01-573._L0 | 0 | KPA_FLOORX_IO |  |  | 1573 | F1573 | Q1573 |  | 1573 | F1573 | Q1573 | [13 empty] | /1 | 0/ISO
01-574._L0 | 0 | KPA_FLOORX_IO |  |  | 1574 | F1574 | Q1574 |  | 1574 | F1574 | Q1574 | [13 empty] | /1 | 0/ISO
01-575._L0 | 0 | KPA_FLOORX_IO |  |  | 1575 | F1575 | Q1575 |  | 1575 | F1575 | Q1575 | [13 empty] | /1 | 0/ISO
01-576._L0 | 0 | KPA_FLOORX_IO |  |  | 1576 | F1576 | Q1576 |  | 1576 | F1576 | Q1576 | [13 empty] | /1 | 0/ISO
01-577._L0 | 0 | KPA_FLOORX_IO |  |  | 1577 | F1577 | Q1577 |  | 1577 | F1577 | Q1577 | [13 empty] | /1 | 0/ISO
01-578._L0 | 0 | KPA_FLOORX_IO |  |  | 1578 | F1578 | Q1578 |  | 1578 | F1578 | Q1578 | [13 empty] | /1 | 0/ISO
01-579._L0 | 0 | KPA_FLOORX_IO |  |  | 1579 | F1579 | Q1579 |  | 1579 | F1579 | Q1579 | [13 empty] | /1 | 0/ISO
01-580._L0 | 0 | KPA_FLOORX_IO |  |  | 1580 | F1580 | Q1580 |  | 1580 | F1580 | Q1580 | [13 empty] | /1 | 0/ISO
01-581._L0 | 0 | KPA_FLOORX_IO |  |  | 1581 | F1581 | Q1581 |  | 1581 | F1581 | Q1581 | [13 empty] | /1 | 0/ISO
01-582._L0 | 0 | KPA_FLOORX_IO |  |  | 1582 | F1582 | Q1582 |  | 1582 | F1582 | Q1582 | [13 empty] | /1 | 0/ISO
01-583._L0 | 0 | KPA_FLOORX_IO |  |  | 1583 | F1583 | Q1583 |  | 1583 | F1583 | Q1583 | [13 empty] | /1 | 0/ISO
01-584._L0 | 0 | KPA_FLOORX_IO |  |  | 1584 | F1584 | Q1584 |  | 1584 | F1584 | Q1584 | [13 empty] | /1 | 0/ISO
01-585._L0 | 0 | KPA_FLOORX_IO |  |  | 1585 | F1585 | Q1585 |  | 1585 | F1585 | Q1585 | [13 empty] | /1 | 0/ISO
01-586._L0 | 0 | KPA_FLOORX_IO |  |  | 1586 | F1586 | Q1586 |  | 1586 | F1586 | Q1586 | [13 empty] | /1 | 0/ISO
01-587._L0 | 0 | KPA_FLOORX_IO |  |  | 1587 | F1587 | Q1587 |  | 1587 | F1587 | Q1587 | [13 empty] | /1 | 0/ISO
01-588._L0 | 0 | KPA_FLOORX_IO |  |  | 1588 | F1588 | Q1588 |  | 1588 | F1588 | Q1588 | [13 empty] | /1 | 0/ISO
01-589._L0 | 0 | KPA_FLOORX_IO |  |  | 1589 | F1589 | Q1589 |  | 1589 | F1589 | Q1589 | [13 empty] | /1 | 0/ISO
01-590._L0 | 0 | KPA_FLOORX_IO |  |  | 1590 | F1590 | Q1590 |  | 1590 | F1590 | Q1590 | [13 empty] | /1 | 0/ISO
01-591._L0 | 0 | KPA_FLOORX_IO |  |  | 1591 | F1591 | Q1591 |  | 1591 | F1591 | Q1591 | [13 empty] | /1 | 0/ISO
01-592._L0 | 0 | KPA_FLOORX_IO |  |  | 1592 | F1592 | Q1592 |  | 1592 | F1592 | Q1592 | [13 empty] | /1 | 0/ISO
01-593._L0 | 0 | KPA_FLOORX_IO |  |  | 1593 | F1593 | Q1593 |  | 1593 | F1593 | Q1593 | [13 empty] | /1 | 0/ISO
01-594._L0 | 0 | KPA_FLOORX_IO |  |  | 1594 | F1594 | Q1594 |  | 1594 | F1594 | Q1594 | [13 empty] | /1 | 0/ISO
01-595._L0 | 0 | KPA_FLOORX_IO |  |  | 1595 | F1595 | Q1595 |  | 1595 | F1595 | Q1595 | [13 empty] | /1 | 0/ISO
01-596._L0 | 0 | KPA_FLOORX_IO |  |  | 1596 | F1596 | Q1596 |  | 1596 | F1596 | Q1596 | [13 empty] | /1 | 0/ISO
01-597._L0 | 0 | KPA_FLOORX_IO |  |  | 1597 | F1597 | Q1597 |  | 1597 | F1597 | Q1597 | [13 empty] | /1 | 0/ISO
01-598._L0 | 0 | KPA_FLOORX_IO |  |  | 1598 | F1598 | Q1598 |  | 1598 | F1598 | Q1598 | [13 empty] | /1 | 0/ISO
01-599._L0 | 0 | KPA_FLOORX_IO |  |  | 1599 | F1599 | Q1599 |  | 1599 | F1599 | Q1599 | [13 empty] | /1 | 0/ISO
01-600._L0 | 0 | KPA_FLOORX_IO |  |  | 1600 | F1600 | Q1600 |  | 1600 | F1600 | Q1600 | [13 empty] | /1 | 0/ISO
01-601._L0 | 0 | KPA_FLOORX_IO |  |  | 1601 | F1601 | Q1601 |  | 1601 | F1601 | Q1601 | [13 empty] | /1 | 0/ISO
01-602._L0 | 0 | KPA_FLOORX_IO |  |  | 1602 | F1602 | Q1602 |  | 1602 | F1602 | Q1602 | [13 empty] | /1 | 0/ISO
01-603._L0 | 0 | KPA_FLOORX_IO |  |  | 1603 | F1603 | Q1603 |  | 1603 | F1603 | Q1603 | [13 empty] | /1 | 0/ISO
01-604._L0 | 0 | KPA_FLOORX_IO |  |  | 1604 | F1604 | Q1604 |  | 1604 | F1604 | Q1604 | [13 empty] | /1 | 0/ISO
01-605._L0 | 0 | KPA_FLOORX_IO |  |  | 1605 | F1605 | Q1605 |  | 1605 | F1605 | Q1605 | [13 empty] | /1 | 0/ISO
01-606._L0 | 0 | KPA_FLOORX_IO |  |  | 1606 | F1606 | Q1606 |  | 1606 | F1606 | Q1606 | [13 empty] | /1 | 0/ISO
01-607._L0 | 0 | KPA_FLOORX_IO |  |  | 1607 | F1607 | Q1607 |  | 1607 | F1607 | Q1607 | [13 empty] | /1 | 0/ISO
01-608._L0 | 0 | KPA_FLOORX_IO |  |  | 1608 | F1608 | Q1608 |  | 1608 | F1608 | Q1608 | [13 empty] | /1 | 0/ISO
01-609._L0 | 0 | KPA_FLOORX_IO |  |  | 1609 | F1609 | Q1609 |  | 1609 | F1609 | Q1609 | [13 empty] | /1 | 0/ISO
01-610._L0 | 0 | KPA_FLOORX_IO |  |  | 1610 | F1610 | Q1610 |  | 1610 | F1610 | Q1610 | [13 empty] | /1 | 0/ISO
01-611._L0 | 0 | KPA_FLOORX_IO |  |  | 1611 | F1611 | Q1611 |  | 1611 | F1611 | Q1611 | [13 empty] | /1 | 0/ISO
01-612._L0 | 0 | KPA_FLOORX_IO |  |  | 1612 | F1612 | Q1612 |  | 1612 | F1612 | Q1612 | [13 empty] | /1 | 0/ISO
01-613._L0 | 0 | KPA_FLOORX_IO |  |  | 1613 | F1613 | Q1613 |  | 1613 | F1613 | Q1613 | [13 empty] | /1 | 0/ISO
01-614._L0 | 0 | KPA_FLOORX_IO |  |  | 1614 | F1614 | Q1614 |  | 1614 | F1614 | Q1614 | [13 empty] | /1 | 0/ISO
01-615._L0 | 0 | KPA_FLOORX_IO |  |  | 1615 | F1615 | Q1615 |  | 1615 | F1615 | Q1615 | [13 empty] | /1 | 0/ISO
01-616._L0 | 0 | KPA_FLOORX_IO |  |  | 1616 | F1616 | Q1616 |  | 1616 | F1616 | Q1616 | [13 empty] | /1 | 0/ISO
01-617._L0 | 0 | KPA_FLOORX_IO |  |  | 1617 | F1617 | Q1617 |  | 1617 | F1617 | Q1617 | [13 empty] | /1 | 0/ISO
01-618._L0 | 0 | KPA_FLOORX_IO |  |  | 1618 | F1618 | Q1618 |  | 1618 | F1618 | Q1618 | [13 empty] | /1 | 0/ISO
01-619._L0 | 0 | KPA_FLOORX_IO |  |  | 1619 | F1619 | Q1619 |  | 1619 | F1619 | Q1619 | [13 empty] | /1 | 0/ISO
01-620._L0 | 0 | KPA_FLOORX_IO |  |  | 1620 | F1620 | Q1620 |  | 1620 | F1620 | Q1620 | [13 empty] | /1 | 0/ISO
01-621._L0 | 0 | KPA_FLOORX_IO |  |  | 1621 | F1621 | Q1621 |  | 1621 | F1621 | Q1621 | [13 empty] | /1 | 0/ISO
01-622._L0 | 0 | KPA_FLOORX_IO |  |  | 1622 | F1622 | Q1622 |  | 1622 | F1622 | Q1622 | [13 empty] | /1 | 0/ISO
01-623._L0 | 0 | KPA_FLOORX_IO |  |  | 1623 | F1623 | Q1623 |  | 1623 | F1623 | Q1623 | [13 empty] | /1 | 0/ISO
01-624._L0 | 0 | KPA_FLOORX_IO |  |  | 1624 | F1624 | Q1624 |  | 1624 | F1624 | Q1624 | [13 empty] | /1 | 0/ISO
01-625._L0 | 0 | KPA_FLOORX_IO |  |  | 1625 | F1625 | Q1625 |  | 1625 | F1625 | Q1625 | [13 empty] | /1 | 0/ISO
01-626._L0 | 0 | KPA_FLOORX_IO |  |  | 1626 | F1626 | Q1626 |  | 1626 | F1626 | Q1626 | [13 empty] | /1 | 0/ISO
01-627._L0 | 0 | KPA_FLOORX_IO |  |  | 1627 | F1627 | Q1627 |  | 1627 | F1627 | Q1627 | [13 empty] | /1 | 0/ISO
01-628._L0 | 0 | KPA_FLOORX_IO |  |  | 1628 | F1628 | Q1628 |  | 1628 | F1628 | Q1628 | [13 empty] | /1 | 0/ISO
01-629._L0 | 0 | KPA_FLOORX_IO |  |  | 1629 | F1629 | Q1629 |  | 1629 | F1629 | Q1629 | [13 empty] | /1 | 0/ISO
01-630._L0 | 0 | KPA_FLOORX_IO |  |  | 1630 | F1630 | Q1630 |  | 1630 | F1630 | Q1630 | [13 empty] | /1 | 0/ISO
01-631._L0 | 0 | KPA_FLOORX_IO |  |  | 1631 | F1631 | Q1631 |  | 1631 | F1631 | Q1631 | [13 empty] | /1 | 0/ISO
01-632._L0 | 0 | KPA_FLOORX_IO |  |  | 1632 | F1632 | Q1632 |  | 1632 | F1632 | Q1632 | [13 empty] | /1 | 0/ISO
01-633._L0 | 0 | KPA_FLOORX_IO |  |  | 1633 | F1633 | Q1633 |  | 1633 | F1633 | Q1633 | [13 empty] | /1 | 0/ISO
01-634._L0 | 0 | KPA_FLOORX_IO |  |  | 1634 | F1634 | Q1634 |  | 1634 | F1634 | Q1634 | [13 empty] | /1 | 0/ISO
01-635._L0 | 0 | KPA_FLOORX_IO |  |  | 1635 | F1635 | Q1635 |  | 1635 | F1635 | Q1635 | [13 empty] | /1 | 0/ISO
01-636._L0 | 0 | KPA_FLOORX_IO |  |  | 1636 | F1636 | Q1636 |  | 1636 | F1636 | Q1636 | [13 empty] | /1 | 0/ISO
01-637._L0 | 0 | KPA_FLOORX_IO |  |  | 1637 | F1637 | Q1637 |  | 1637 | F1637 | Q1637 | [13 empty] | /1 | 0/ISO
01-638._L0 | 0 | KPA_FLOORX_IO |  |  | 1638 | F1638 | Q1638 |  | 1638 | F1638 | Q1638 | [13 empty] | /1 | 0/ISO
01-639._L0 | 0 | KPA_FLOORX_IO |  |  | 1639 | F1639 | Q1639 |  | 1639 | F1639 | Q1639 | [13 empty] | /1 | 0/ISO
01-640._L0 | 0 | KPA_FLOORX_IO |  |  | 1640 | F1640 | Q1640 |  | 1640 | F1640 | Q1640 | [13 empty] | /1 | 0/ISO
01-641._L0 | 0 | KPA_FLOORX_IO |  |  | 1641 | F1641 | Q1641 |  | 1641 | F1641 | Q1641 | [13 empty] | /1 | 0/ISO
01-642._L0 | 0 | KPA_FLOORX_IO |  |  | 1642 | F1642 | Q1642 |  | 1642 | F1642 | Q1642 | [13 empty] | /1 | 0/ISO
01-643._L0 | 0 | KPA_FLOORX_IO |  |  | 1643 | F1643 | Q1643 |  | 1643 | F1643 | Q1643 | [13 empty] | /1 | 0/ISO
01-644._L0 | 0 | KPA_FLOORX_IO |  |  | 1644 | F1644 | Q1644 |  | 1644 | F1644 | Q1644 | [13 empty] | /1 | 0/ISO
01-645._L0 | 0 | KPA_FLOORX_IO |  |  | 1645 | F1645 | Q1645 |  | 1645 | F1645 | Q1645 | [13 empty] | /1 | 0/ISO
01-646._L0 | 0 | KPA_FLOORX_IO |  |  | 1646 | F1646 | Q1646 |  | 1646 | F1646 | Q1646 | [13 empty] | /1 | 0/ISO
01-647._L0 | 0 | KPA_FLOORX_IO |  |  | 1647 | F1647 | Q1647 |  | 1647 | F1647 | Q1647 | [13 empty] | /1 | 0/ISO
01-648._L0 | 0 | KPA_FLOORX_IO |  |  | 1648 | F1648 | Q1648 |  | 1648 | F1648 | Q1648 | [13 empty] | /1 | 0/ISO
01-649._L0 | 0 | KPA_FLOORX_IO |  |  | 1649 | F1649 | Q1649 |  | 1649 | F1649 | Q1649 | [13 empty] | /1 | 0/ISO
01-650._L0 | 0 | KPA_FLOORX_IO |  |  | 1650 | F1650 | Q1650 |  | 1650 | F1650 | Q1650 | [13 empty] | /1 | 0/ISO
01-651._L0 | 0 | KPA_FLOORX_IO |  |  | 1651 | F1651 | Q1651 |  | 1651 | F1651 | Q1651 | [13 empty] | /1 | 0/ISO
01-652._L0 | 0 | KPA_FLOORX_IO |  |  | 1652 | F1652 | Q1652 |  | 1652 | F1652 | Q1652 | [13 empty] | /1 | 0/ISO
01-653._L0 | 0 | KPA_FLOORX_IO |  |  | 1653 | F1653 | Q1653 |  | 1653 | F1653 | Q1653 | [13 empty] | /1 | 0/ISO
01-654._L0 | 0 | KPA_FLOORX_IO |  |  | 1654 | F1654 | Q1654 |  | 1654 | F1654 | Q1654 | [13 empty] | /1 | 0/ISO
01-655._L0 | 0 | KPA_FLOORX_IO |  |  | 1655 | F1655 | Q1655 |  | 1655 | F1655 | Q1655 | [13 empty] | /1 | 0/ISO
01-656._L0 | 0 | KPA_FLOORX_IO |  |  | 1656 | F1656 | Q1656 |  | 1656 | F1656 | Q1656 | [13 empty] | /1 | 0/ISO
01-657._L0 | 0 | KPA_FLOORX_IO |  |  | 1657 | F1657 | Q1657 |  | 1657 | F1657 | Q1657 | [13 empty] | /1 | 0/ISO
01-658._L0 | 0 | KPA_FLOORX_IO |  |  | 1658 | F1658 | Q1658 |  | 1658 | F1658 | Q1658 | [13 empty] | /1 | 0/ISO
01-659._L0 | 0 | KPA_FLOORX_IO |  |  | 1659 | F1659 | Q1659 |  | 1659 | F1659 | Q1659 | [13 empty] | /1 | 0/ISO
01-660._L0 | 0 | KPA_FLOORX_IO |  |  | 1660 | F1660 | Q1660 |  | 1660 | F1660 | Q1660 | [13 empty] | /1 | 0/ISO
01-661._L0 | 0 | KPA_FLOORX_IO |  |  | 1661 | F1661 | Q1661 |  | 1661 | F1661 | Q1661 | [13 empty] | /1 | 0/ISO
01-662._L0 | 0 | KPA_FLOORX_IO |  |  | 1662 | F1662 | Q1662 |  | 1662 | F1662 | Q1662 | [13 empty] | /1 | 0/ISO
01-663._L0 | 0 | KPA_FLOORX_IO |  |  | 1663 | F1663 | Q1663 |  | 1663 | F1663 | Q1663 | [13 empty] | /1 | 0/ISO
01-664._L0 | 0 | KPA_FLOORX_IO |  |  | 1664 | F1664 | Q1664 |  | 1664 | F1664 | Q1664 | [13 empty] | /1 | 0/ISO
01-665._L0 | 0 | KPA_FLOORX_IO |  |  | 1665 | F1665 | Q1665 |  | 1665 | F1665 | Q1665 | [13 empty] | /1 | 0/ISO
01-666._L0 | 0 | KPA_FLOORX_IO |  |  | 1666 | F1666 | Q1666 |  | 1666 | F1666 | Q1666 | [13 empty] | /1 | 0/ISO
01-667._L0 | 0 | KPA_FLOORX_IO |  |  | 1667 | F1667 | Q1667 |  | 1667 | F1667 | Q1667 | [13 empty] | /1 | 0/ISO
01-668._L0 | 0 | KPA_FLOORX_IO |  |  | 1668 | F1668 | Q1668 |  | 1668 | F1668 | Q1668 | [13 empty] | /1 | 0/ISO
01-669._L0 | 0 | KPA_FLOORX_IO |  |  | 1669 | F1669 | Q1669 |  | 1669 | F1669 | Q1669 | [13 empty] | /1 | 0/ISO
01-670._L0 | 0 | KPA_FLOORX_IO |  |  | 1670 | F1670 | Q1670 |  | 1670 | F1670 | Q1670 | [13 empty] | /1 | 0/ISO
01-671._L0 | 0 | KPA_FLOORX_IO |  |  | 1671 | F1671 | Q1671 |  | 1671 | F1671 | Q1671 | [13 empty] | /1 | 0/ISO
01-672._L0 | 0 | KPA_FLOORX_IO |  |  | 1672 | F1672 | Q1672 |  | 1672 | F1672 | Q1672 | [13 empty] | /1 | 0/ISO
01-673._L0 | 0 | KPA_FLOORX_IO |  |  | 1673 | F1673 | Q1673 |  | 1673 | F1673 | Q1673 | [13 empty] | /1 | 0/ISO
01-674._L0 | 0 | KPA_FLOORX_IO |  |  | 1674 | F1674 | Q1674 |  | 1674 | F1674 | Q1674 | [13 empty] | /1 | 0/ISO
01-675._L0 | 0 | KPA_FLOORX_IO |  |  | 1675 | F1675 | Q1675 |  | 1675 | F1675 | Q1675 | [13 empty] | /1 | 0/ISO
01-676._L0 | 0 | KPA_FLOORX_IO |  |  | 1676 | F1676 | Q1676 |  | 1676 | F1676 | Q1676 | [13 empty] | /1 | 0/ISO
01-677._L0 | 0 | KPA_FLOORX_IO |  |  | 1677 | F1677 | Q1677 |  | 1677 | F1677 | Q1677 | [13 empty] | /1 | 0/ISO
01-678._L0 | 0 | KPA_FLOORX_IO |  |  | 1678 | F1678 | Q1678 |  | 1678 | F1678 | Q1678 | [13 empty] | /1 | 0/ISO
01-679._L0 | 0 | KPA_FLOORX_IO |  |  | 1679 | F1679 | Q1679 |  | 1679 | F1679 | Q1679 | [13 empty] | /1 | 0/ISO
01-680._L0 | 0 | KPA_FLOORX_IO |  |  | 1680 | F1680 | Q1680 |  | 1680 | F1680 | Q1680 | [13 empty] | /1 | 0/ISO
01-681._L0 | 0 | KPA_FLOORX_IO |  |  | 1681 | F1681 | Q1681 |  | 1681 | F1681 | Q1681 | [13 empty] | /1 | 0/ISO
01-682._L0 | 0 | KPA_FLOORX_IO |  |  | 1682 | F1682 | Q1682 |  | 1682 | F1682 | Q1682 | [13 empty] | /1 | 0/ISO
01-683._L0 | 0 | KPA_FLOORX_IO |  |  | 1683 | F1683 | Q1683 |  | 1683 | F1683 | Q1683 | [13 empty] | /1 | 0/ISO
01-684._L0 | 0 | KPA_FLOORX_IO |  |  | 1684 | F1684 | Q1684 |  | 1684 | F1684 | Q1684 | [13 empty] | /1 | 0/ISO
01-685._L0 | 0 | KPA_FLOORX_IO |  |  | 1685 | F1685 | Q1685 |  | 1685 | F1685 | Q1685 | [13 empty] | /1 | 0/ISO
01-686._L0 | 0 | KPA_FLOORX_IO |  |  | 1686 | F1686 | Q1686 |  | 1686 | F1686 | Q1686 | [13 empty] | /1 | 0/ISO
01-687._L0 | 0 | KPA_FLOORX_IO |  |  | 1687 | F1687 | Q1687 |  | 1687 | F1687 | Q1687 | [13 empty] | /1 | 0/ISO
01-688._L0 | 0 | KPA_FLOORX_IO |  |  | 1688 | F1688 | Q1688 |  | 1688 | F1688 | Q1688 | [13 empty] | /1 | 0/ISO
01-689._L0 | 0 | KPA_FLOORX_IO |  |  | 1689 | F1689 | Q1689 |  | 1689 | F1689 | Q1689 | [13 empty] | /1 | 0/ISO
01-690._L0 | 0 | KPA_FLOORX_IO |  |  | 1690 | F1690 | Q1690 |  | 1690 | F1690 | Q1690 | [13 empty] | /1 | 0/ISO
01-691._L0 | 0 | KPA_FLOORX_IO |  |  | 1691 | F1691 | Q1691 |  | 1691 | F1691 | Q1691 | [13 empty] | /1 | 0/ISO
01-692._L0 | 0 | KPA_FLOORX_IO |  |  | 1692 | F1692 | Q1692 |  | 1692 | F1692 | Q1692 | [13 empty] | /1 | 0/ISO
01-693._L0 | 0 | KPA_FLOORX_IO |  |  | 1693 | F1693 | Q1693 |  | 1693 | F1693 | Q1693 | [13 empty] | /1 | 0/ISO
01-694._L0 | 0 | KPA_FLOORX_IO |  |  | 1694 | F1694 | Q1694 |  | 1694 | F1694 | Q1694 | [13 empty] | /1 | 0/ISO
01-695._L0 | 0 | KPA_FLOORX_IO |  |  | 1695 | F1695 | Q1695 |  | 1695 | F1695 | Q1695 | [13 empty] | /1 | 0/ISO
01-696._L0 | 0 | KPA_FLOORX_IO |  |  | 1696 | F1696 | Q1696 |  | 1696 | F1696 | Q1696 | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO
0 | 0 |  |  |  | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | [13 empty] | /1 | 0/ISO

## W_WIRE
Tag | _Typical | W1 | W2 | WireNameLoopA | WireNameLoopB | WireNameIO | WireNameUserA | WireNameUserB | Notes
<004> | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
BB1FS003 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS001 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS002 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS003 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS004 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS005 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS006 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS007 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS008 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS009 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS010 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS011 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS012 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS020 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS200 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS201 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS203 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS204 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS205 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS206 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS207 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS208 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS209 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS210 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS211 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS212 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS213 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS214 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS215 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS216 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS217 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS218 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS219 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS220 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS221 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS222 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS223 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS224 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS225 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS226 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS227 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS228 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS230 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS231 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS232 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS233 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS600 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS601 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS602 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS603 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS604 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS605 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS606 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS607 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS608 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS609 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS610 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS611 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS612 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS613 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS614 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS615 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS616 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS617 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS618 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS619 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS620 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS621 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS622 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS623 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS650 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS651 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS652 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS653 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS654 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS655 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS656 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS659 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS660 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS661 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS662 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS663 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS800 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS801 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS802 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS803 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS850 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS851 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS852 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS853 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS854 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS855 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS856 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS857 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS858 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS600 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS608 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS650 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS651 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS652 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS653 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS654 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS655 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS656 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS657 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS658 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS659 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS660 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS661 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS700 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS701 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS850 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS851 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS600 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS601 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS602 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS603 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS604 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS605 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST649 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST650 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST651 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST652 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST653 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST654 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST655 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST656 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST657 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST659 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST673 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST674 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST675 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST850 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST852 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST853 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST856 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1TS600 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1TS608 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
BB1EM658_LOCAL_MODE | #N/A |  |  | RIO_01:01.DI:V+ |  | RIO_01:01.DI:00 | /K1
BB1EM658_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:01.DI:V+ |  | RIO_01:01.DI:01 | /K1
BB1EM658_LOCAL_RUN_REV | #N/A |  |  | RIO_01:01.DI:V+ |  | RIO_01:01.DI:02 | /K1
BB1EM658_ISOLATOR | #N/A |  |  | RIO_01:01.DI:V+ |  | RIO_01:01.DI:03 | /K1
BB1EM659_LOCAL_MODE | #N/A |  |  | RIO_01:02.DI:V+ |  | RIO_01:02.DI:00 | /K1
BB1EM659_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:02.DI:V+ |  | RIO_01:02.DI:01 | /K1
BB1EM659_LOCAL_RUN_REV | #N/A |  |  | RIO_01:02.DI:V+ |  | RIO_01:02.DI:02 | /K1
BB1EM659_ISOLATOR | #N/A |  |  | RIO_01:02.DI:V+ |  | RIO_01:02.DI:03 | /K1
BB1EM676_LOCAL_MODE | #N/A |  |  | RIO_01:03.DI:V+ |  | RIO_01:03.DI:00 | /K1
BB1EM676_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:03.DI:V+ |  | RIO_01:03.DI:01 | /K1
BB1EM676_LOCAL_RUN_REV | #N/A |  |  | RIO_01:03.DI:V+ |  | RIO_01:03.DI:02 | /K1
BB1EM676_ISOLATOR | #N/A |  |  | RIO_01:03.DI:V+ |  | RIO_01:03.DI:03 | /K1
BB1EM672_LOCAL_MODE | #N/A |  |  | RIO_01:04.DI:V+ |  | RIO_01:04.DI:00 | /K1
BB1EM672_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:04.DI:V+ |  | RIO_01:04.DI:01 | /K1
BB1EM672_LOCAL_RUN_REV | #N/A |  |  | RIO_01:04.DI:V+ |  | RIO_01:04.DI:02 | /K1
BB1EM672_ISOLATOR | #N/A |  |  | RIO_01:04.DI:V+ |  | RIO_01:04.DI:03 | /K1
BB1EM662_LOCAL_MODE | #N/A |  |  | RIO_01:05.DI:V+ |  | RIO_01:05.DI:00 | /K1
BB1EM662_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:05.DI:V+ |  | RIO_01:05.DI:01 | /K1
BB1EM662_LOCAL_RUN_REV | #N/A |  |  | RIO_01:05.DI:V+ |  | RIO_01:05.DI:02 | /K1
BB1EM662_ISOLATOR | #N/A |  |  | RIO_01:05.DI:V+ |  | RIO_01:05.DI:03 | /K1
BB1EM650_LOCAL_MODE | #N/A |  |  | RIO_01:06.DI:V+ |  | RIO_01:06.DI:00 | /K1
BB1EM650_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:06.DI:V+ |  | RIO_01:06.DI:01 | /K1
BB1EM650_LOCAL_RUN_REV | #N/A |  |  | RIO_01:06.DI:V+ |  | RIO_01:06.DI:02 | /K1
BB1EM650_ISOLATOR | #N/A |  |  | RIO_01:06.DI:V+ |  | RIO_01:06.DI:03 | /K1
BB1EM663_LOCAL_MODE | #N/A |  |  | RIO_01:07.DI:V+ |  | RIO_01:07.DI:00 | /K1
BB1EM663_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:07.DI:V+ |  | RIO_01:07.DI:01 | /K1
BB1EM663_LOCAL_RUN_REV | #N/A |  |  | RIO_01:07.DI:V+ |  | RIO_01:07.DI:02 | /K1
BB1EM663_ISOLATOR | #N/A |  |  | RIO_01:07.DI:V+ |  | RIO_01:07.DI:03 | /K1
BB1EM664_LOCAL_MODE | #N/A |  |  | RIO_01:08.DI:V+ |  | RIO_01:08.DI:00 | /K1
BB1EM664_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:08.DI:V+ |  | RIO_01:08.DI:01 | /K1
BB1EM664_LOCAL_RUN_REV | #N/A |  |  | RIO_01:08.DI:V+ |  | RIO_01:08.DI:02 | /K1
BB1EM664_ISOLATOR | #N/A |  |  | RIO_01:08.DI:V+ |  | RIO_01:08.DI:03 | /K1
BB1EM665_LOCAL_MODE | #N/A |  |  | RIO_01:09.DI:V+ |  | RIO_01:09.DI:00 | /K1
BB1EM665_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:09.DI:V+ |  | RIO_01:09.DI:01 | /K1
BB1EM665_LOCAL_RUN_REV | #N/A |  |  | RIO_01:09.DI:V+ |  | RIO_01:09.DI:02 | /K1
BB1EM665_ISOLATOR | #N/A |  |  | RIO_01:09.DI:V+ |  | RIO_01:09.DI:03 | /K1
BB1EM852_LOCAL_MODE | #N/A |  |  | RIO_01:10.DI:V+ |  | RIO_01:10.DI:00 | /K1
BB1EM852_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:10.DI:V+ |  | RIO_01:10.DI:01 | /K1
BB1EM852_LOCAL_RUN_REV | #N/A |  |  | RIO_01:10.DI:V+ |  | RIO_01:10.DI:02 | /K1
BB1EM852_ISOLATOR | #N/A |  |  | RIO_01:10.DI:V+ |  | RIO_01:10.DI:03 | /K1
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A

## P_IO
IO Mapping |  |  |  | Description |  | Panel | Addressing | [10 empty] | Terminals | [5 empty] | Terminal Type/Names |  |  |  |  | Catalog
PLCTag | CardType | IOType | _Typical | Description2 | Description3 | Description4 | Panel | _PLC | _RackRaw | _SlotRaw | _ChannelRaw | _IsMax | Rack | Slot | Channel | LoopAddressA | LoopAddressB | AddressIO | TerminalIO | LoopTerminalA | LoopTerminalB | GndTerminal | T1 | T2 | T1Type | T2Type | LoopNameA | LoopNameB | GndName | CatalogNo | CatalogDesc2 | CatalogDesc | Notes
BB1EM658_LOCAL_MODE | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 0 | 0 | 01 | 01 | 00 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM658_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 1 | 0 | 01 | 01 | 01 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM658_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 2 | 0 | 01 | 01 | 02 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM658_ISOLATOR | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 3 | TRUE | 01 | 01 | 03 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM659_LOCAL_MODE | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 0 | 0 | 01 | 02 | 00 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM659_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 1 | 0 | 01 | 02 | 01 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM659_LOCAL_RUN_REV | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 2 | 0 | 01 | 02 | 02 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM659_ISOLATOR | DI | DI | FRQ_REVH | BELT CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 3 | TRUE | 01 | 02 | 03 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM676_LOCAL_MODE | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 0 | 0 | 01 | 03 | 00 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM676_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 1 | 0 | 01 | 03 | 01 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM676_LOCAL_RUN_REV | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 2 | 0 | 01 | 03 | 02 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM676_ISOLATOR | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 3 | TRUE | 01 | 03 | 03 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM672_LOCAL_MODE | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 0 | 0 | 01 | 04 | 00 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM672_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 1 | 0 | 01 | 04 | 01 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM672_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 2 | 0 | 01 | 04 | 02 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM672_ISOLATOR | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 3 | TRUE | 01 | 04 | 03 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM662_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 0 | 0 | 01 | 05 | 00 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM662_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 1 | 0 | 01 | 05 | 01 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM662_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 2 | 0 | 01 | 05 | 02 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM662_ISOLATOR | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 3 | TRUE | 01 | 05 | 03 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM650_LOCAL_MODE | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 0 | 0 | 01 | 06 | 00 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM650_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 1 | 0 | 01 | 06 | 01 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM650_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 2 | 0 | 01 | 06 | 02 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM650_ISOLATOR | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 3 | TRUE | 01 | 06 | 03 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM663_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 0 | 0 | 01 | 07 | 00 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM663_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 1 | 0 | 01 | 07 | 01 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM663_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 2 | 0 | 01 | 07 | 02 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM663_ISOLATOR | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 3 | TRUE | 01 | 07 | 03 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM664_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 0 | 0 | 01 | 08 | 00 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM664_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 1 | 0 | 01 | 08 | 01 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM664_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 2 | 0 | 01 | 08 | 02 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM664_ISOLATOR | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 3 | TRUE | 01 | 08 | 03 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM665_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 0 | 0 | 01 | 09 | 00 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM665_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 1 | 0 | 01 | 09 | 01 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM665_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 2 | 0 | 01 | 09 | 02 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM665_ISOLATOR | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 3 | TRUE | 01 | 09 | 03 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM852_LOCAL_MODE | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 0 | 0 | 01 | 10 | 00 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM852_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 1 | 0 | 01 | 10 | 01 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM852_LOCAL_RUN_REV | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 2 | 0 | 01 | 10 | 02 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM852_ISOLATOR | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 3 | TRUE | 01 | 10 | 03 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 11 | 0 | 0 | 01 | 11 | 00 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 11 | 1 | 0 | 01 | 11 | 01 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 11 | 2 | 0 | 01 | 11 | 02 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 11 | 3 | TRUE | 01 | 11 | 03 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 12 | 0 | 0 | 01 | 12 | 00 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 12 | 1 | 0 | 01 | 12 | 01 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 12 | 2 | 0 | 01 | 12 | 02 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 12 | 3 | TRUE | 01 | 12 | 03 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 0 | 0 | 01 | 13 | 00 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 1 | 0 | 01 | 13 | 01 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 2 | 0 | 01 | 13 | 02 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 3 | TRUE | 01 | 13 | 03 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 0 | 0 | 01 | 14 | 00 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 1 | 0 | 01 | 14 | 01 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 2 | 0 | 01 | 14 | 02 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 3 | TRUE | 01 | 14 | 03 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 0 | 0 | 01 | 15 | 00 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 1 | 0 | 01 | 15 | 01 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 2 | 0 | 01 | 15 | 02 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 3 | TRUE | 01 | 15 | 03 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 0 | 0 | 01 | 16 | 00 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 1 | 0 | 01 | 16 | 01 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 2 | 0 | 01 | 16 | 02 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 3 | TRUE | 01 | 16 | 03 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 0 | 0 | 01 | 17 | 00 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 1 | 0 | 01 | 17 | 01 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 2 | 0 | 01 | 17 | 02 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 3 | TRUE | 01 | 17 | 03 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 0 | 0 | 01 | 18 | 00 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 1 | 0 | 01 | 18 | 01 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 2 | 0 | 01 | 18 | 02 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 3 | TRUE | 01 | 18 | 03 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 0 | 0 | 01 | 19 | 00 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 1 | 0 | 01 | 19 | 01 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 2 | 0 | 01 | 19 | 02 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 3 | TRUE | 01 | 19 | 03 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 0 | 0 | 01 | 20 | 00 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 1 | 0 | 01 | 20 | 01 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 2 | 0 | 01 | 20 | 02 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 3 | TRUE | 01 | 20 | 03 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 0 | 0 | 01 | 21 | 00 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 1 | 0 | 01 | 21 | 01 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 2 | 0 | 01 | 21 | 02 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 3 | TRUE | 01 | 21 | 03 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 0 | 0 | 01 | 22 | 00 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 1 | 0 | 01 | 22 | 01 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 2 | 0 | 01 | 22 | 02 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 3 | TRUE | 01 | 22 | 03 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 0 | 0 | 01 | 23 | 00 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 1 | 0 | 01 | 23 | 01 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 2 | 0 | 01 | 23 | 02 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 3 | TRUE | 01 | 23 | 03 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 0 | 0 | 01 | 24 | 00 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 1 | 0 | 01 | 24 | 01 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 2 | 0 | 01 | 24 | 02 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 3 | TRUE | 01 | 24 | 03 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 0 | 0 | 01 | 25 | 00 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 1 | 0 | 01 | 25 | 01 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 2 | 0 | 01 | 25 | 02 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 3 | TRUE | 01 | 25 | 03 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 0 | 0 | 01 | 26 | 00 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 1 | 0 | 01 | 26 | 01 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 2 | 0 | 01 | 26 | 02 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 3 | TRUE | 01 | 26 | 03 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 0 | 0 | 01 | 27 | 00 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 1 | 0 | 01 | 27 | 01 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 2 | 0 | 01 | 27 | 02 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 3 | TRUE | 01 | 27 | 03 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 0 | 0 | 01 | 28 | 00 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 1 | 0 | 01 | 28 | 01 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 2 | 0 | 01 | 28 | 02 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 3 | TRUE | 01 | 28 | 03 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 0 | 0 | 01 | 29 | 00 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 1 | 0 | 01 | 29 | 01 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 2 | 0 | 01 | 29 | 02 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 3 | TRUE | 01 | 29 | 03 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 0 | 0 | 01 | 30 | 00 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 1 | 0 | 01 | 30 | 01 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 2 | 0 | 01 | 30 | 02 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 3 | TRUE | 01 | 30 | 03 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 0 | 0 | 01 | 31 | 00 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 1 | 0 | 01 | 31 | 01 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 2 | 0 | 01 | 31 | 02 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 3 | TRUE | 01 | 31 | 03 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 0 | 0 | 01 | 32 | 00 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 1 | 0 | 01 | 32 | 01 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 2 | 0 | 01 | 32 | 02 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 3 | TRUE | 01 | 32 | 03 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 0 | 0 | 01 | 33 | 00 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 1 | 0 | 01 | 33 | 01 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 2 | 0 | 01 | 33 | 02 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 3 | TRUE | 01 | 33 | 03 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 0 | 0 | 01 | 34 | 00 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 1 | 0 | 01 | 34 | 01 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 2 | 0 | 01 | 34 | 02 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 3 | TRUE | 01 | 34 | 03 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 0 | 0 | 01 | 35 | 00 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 1 | 0 | 01 | 35 | 01 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 2 | 0 | 01 | 35 | 02 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 3 | TRUE | 01 | 35 | 03 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 0 | 0 | 01 | 36 | 00 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 1 | 0 | 01 | 36 | 01 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 2 | 0 | 01 | 36 | 02 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 3 | TRUE | 01 | 36 | 03 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 0 | 0 | 01 | 37 | 00 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 1 | 0 | 01 | 37 | 01 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 2 | 0 | 01 | 37 | 02 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 3 | TRUE | 01 | 37 | 03 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 0 | 0 | 01 | 38 | 00 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 1 | 0 | 01 | 38 | 01 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 2 | 0 | 01 | 38 | 02 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 3 | TRUE | 01 | 38 | 03 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 0 | 0 | 01 | 39 | 00 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 1 | 0 | 01 | 39 | 01 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 2 | 0 | 01 | 39 | 02 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 3 | TRUE | 01 | 39 | 03 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 0 | 0 | 01 | 40 | 00 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 1 | 0 | 01 | 40 | 01 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 2 | 0 | 01 | 40 | 02 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 3 | TRUE | 01 | 40 | 03 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 0 | 0 | 01 | 41 | 00 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 1 | 0 | 01 | 41 | 01 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 2 | 0 | 01 | 41 | 02 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 3 | TRUE | 01 | 41 | 03 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 0 | 0 | 01 | 42 | 00 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 1 | 0 | 01 | 42 | 01 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 2 | 0 | 01 | 42 | 02 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 3 | TRUE | 01 | 42 | 03 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 0 | 0 | 01 | 43 | 00 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 1 | 0 | 01 | 43 | 01 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 2 | 0 | 01 | 43 | 02 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 3 | TRUE | 01 | 43 | 03 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 0 | 0 | 01 | 44 | 00 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 1 | 0 | 01 | 44 | 01 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 2 | 0 | 01 | 44 | 02 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 3 | TRUE | 01 | 44 | 03 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 0 | 0 | 01 | 45 | 00 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 1 | 0 | 01 | 45 | 01 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 2 | 0 | 01 | 45 | 02 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 3 | TRUE | 01 | 45 | 03 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 0 | 0 | 01 | 46 | 00 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 1 | 0 | 01 | 46 | 01 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 2 | 0 | 01 | 46 | 02 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 3 | TRUE | 01 | 46 | 03 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 0 | 0 | 01 | 47 | 00 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 1 | 0 | 01 | 47 | 01 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 2 | 0 | 01 | 47 | 02 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 3 | TRUE | 01 | 47 | 03 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 0 | 0 | 01 | 48 | 00 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 1 | 0 | 01 | 48 | 01 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 2 | 0 | 01 | 48 | 02 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 3 | TRUE | 01 | 48 | 03 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 0 | 0 | 01 | 49 | 00 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 1 | 0 | 01 | 49 | 01 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 2 | 0 | 01 | 49 | 02 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 3 | TRUE | 01 | 49 | 03 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
|  |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 50 | 0 | #N/A | 01 | 50 | 00 | #N/A | #N/A | RIO_01:50.:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## D_DEVICES
Tags |  |  |  | Description |  |  |  |  | Types
DeviceTag | _Suffix | PLCTag | PLCAddress | _InitialDescription | Desc1 | Desc2 | Desc3 | LongDescription | DeviceCode | DeviceType | IOType | Typical | Notes | DeviceTag | Typical | INITIAL_DESC | TAG1 | DESC1 | DESC2 | DESC3 | TAG2 | LDESC | DeviceCode | Type | D1CATN | D1CATD | D1VNAME1 | D1VNAME2 | D1VCATN | D1VCATD | D1ICATN | D1ICATD | D1KW
BB1IL001 |  | BB1IL001 | <IO NOT ASSIGNED> | Alarm horn and light CO alarm | ALARM HORN AND LIGHT | CO ALARM |  | ALARM HORN AND LIGHT CO ALARM | IL | ALARM | DO | ALM_HORN |  | BB1IL001 | ALM_HORN | Alarm horn and light CO alarm | BB1IL001 | ALARM HORN AND LIGHT | CO ALARM |  | BB1IL001 | ALARM HORN AND LIGHT CO ALARM | IL | ALARM | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IJ002 |  | BB1IJ002 | <IO NOT ASSIGNED> | Scraper Conveyor 1 Alarm horn and lamp | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  | SCRAPER CONVEYOR 1 ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN |  | BB1IJ002 | ALM_HORN | Scraper Conveyor 1 Alarm horn and lamp | BB1IJ002 | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  | BB1IJ002 | SCRAPER CONVEYOR 1 ALARM HORN AND LAMP | IJ | ALARM | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IJ001 |  | BB1IJ001 | <IO NOT ASSIGNED> | Scraper Conveyor 2 Alarm horn and lamp | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  | SCRAPER CONVEYOR 2 ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN |  | BB1IJ001 | ALM_HORN | Scraper Conveyor 2 Alarm horn and lamp | BB1IJ001 | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  | BB1IJ001 | SCRAPER CONVEYOR 2 ALARM HORN AND LAMP | IJ | ALARM | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IJ004 |  | BB1IJ004 | <IO NOT ASSIGNED> | Bottom ash conveyor Alarm horn and lamp | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  | BOTTOM ASH CONVEYOR ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN |  | BB1IJ004 | ALM_HORN | Bottom ash conveyor Alarm horn and lamp | BB1IJ004 | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  | BB1IJ004 | BOTTOM ASH CONVEYOR ALARM HORN AND LAMP | IJ | ALARM | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM405 |  | BB1EM405 | <IO NOT ASSIGNED> | Air intake grill 1 OPEN | AIR INTAKE GRILL 1 | OPEN |  | AIR INTAKE GRILL 1 OPEN | EM | MOTOR | DO | BELIMO_VLV |  | BB1EM405 | BELIMO_VLV | Air intake grill 1 OPEN | BB1EM405 | AIR INTAKE GRILL 1 | OPEN |  | BB1EM405 | AIR INTAKE GRILL 1 OPEN | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS401 |  | BB1GS401 | <IO NOT ASSIGNED> | Air intake grill 1 OPENED LIMIT | AIR INTAKE GRILL 1 | OPENED LIMIT |  | AIR INTAKE GRILL 1 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV |  | BB1GS401 | BELIMO_VLV | Air intake grill 1 OPENED LIMIT | BB1GS401 | AIR INTAKE GRILL 1 | OPENED LIMIT |  | BB1GS401 | AIR INTAKE GRILL 1 OPENED LIMIT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM406 |  | BB1EM406 | <IO NOT ASSIGNED> | Air intake grill 2 OPEN | AIR INTAKE GRILL 2 | OPEN |  | AIR INTAKE GRILL 2 OPEN | EM | MOTOR | DO | BELIMO_VLV |  | BB1EM406 | BELIMO_VLV | Air intake grill 2 OPEN | BB1EM406 | AIR INTAKE GRILL 2 | OPEN |  | BB1EM406 | AIR INTAKE GRILL 2 OPEN | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS412 |  | BB1GS412 | <IO NOT ASSIGNED> | Air intake grill 2 OPENED LIMIT | AIR INTAKE GRILL 2 | OPENED LIMIT |  | AIR INTAKE GRILL 2 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV |  | BB1GS412 | BELIMO_VLV | Air intake grill 2 OPENED LIMIT | BB1GS412 | AIR INTAKE GRILL 2 | OPENED LIMIT |  | BB1GS412 | AIR INTAKE GRILL 2 OPENED LIMIT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM407 |  | BB1EM407 | <IO NOT ASSIGNED> | Air intake grill 3 OPEN | AIR INTAKE GRILL 3 | OPEN |  | AIR INTAKE GRILL 3 OPEN | EM | MOTOR | DO | BELIMO_VLV |  | BB1EM407 | BELIMO_VLV | Air intake grill 3 OPEN | BB1EM407 | AIR INTAKE GRILL 3 | OPEN |  | BB1EM407 | AIR INTAKE GRILL 3 OPEN | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS413 |  | BB1GS413 | <IO NOT ASSIGNED> | Air intake grill 3 OPENED LIMIT | AIR INTAKE GRILL 3 | OPENED LIMIT |  | AIR INTAKE GRILL 3 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV |  | BB1GS413 | BELIMO_VLV | Air intake grill 3 OPENED LIMIT | BB1GS413 | AIR INTAKE GRILL 3 | OPENED LIMIT |  | BB1GS413 | AIR INTAKE GRILL 3 OPENED LIMIT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV410 |  | BB1SV410 | <IO NOT ASSIGNED> | Feed water tank overflow valve | FEED WATER TANK | OVERFLOW VALVE |  | FEED WATER TANK OVERFLOW VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV410 | BIN_VLV | Feed water tank overflow valve | BB1SV410 | FEED WATER TANK | OVERFLOW VALVE |  | BB1SV410 | FEED WATER TANK OVERFLOW VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IV004 |  | BB1IV004 | <IO NOT ASSIGNED> | Boiler bottom blow down on-off valve | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  | BOILER BOTTOM BLOW DOWN ON-OFF VALVE | IV | ISOLATING VALVE | DO | BIN_VLV |  | BB1IV004 | BIN_VLV | Boiler bottom blow down on-off valve | BB1IV004 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  | BB1IV004 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE | IV | ISOLATING VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV001 |  | BB1SV001 | <IO NOT ASSIGNED> | Blow down tank cooling on/off valve | BLOW DOWN TANK COOLING | ON/OFF VALVE |  | BLOW DOWN TANK COOLING ON/OFF VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV001 | BIN_VLV | Blow down tank cooling on/off valve | BB1SV001 | BLOW DOWN TANK COOLING | ON/OFF VALVE |  | BB1SV001 | BLOW DOWN TANK COOLING ON/OFF VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV400 |  | BB1SV400 | <IO NOT ASSIGNED> | Sealing air to rotary feeder solenoid valve | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV400 | BIN_VLV | Sealing air to rotary feeder solenoid valve | BB1SV400 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | BB1SV400 | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV406 |  | BB1SV406 | <IO NOT ASSIGNED> | Sealing air to rotary feeder solenoid valve | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV406 | BIN_VLV | Sealing air to rotary feeder solenoid valve | BB1SV406 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | BB1SV406 | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV950 |  | BB1SV950 | <IO NOT ASSIGNED> | Fuel silo fire water control valve | FUEL SILO FIRE WATER | CONTROL VALVE |  | FUEL SILO FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV950 | BIN_VLV | Fuel silo fire water control valve | BB1SV950 | FUEL SILO FIRE WATER | CONTROL VALVE |  | BB1SV950 | FUEL SILO FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV951 |  | BB1SV951 | <IO NOT ASSIGNED> | Fuel pocket fire water control valve | FUEL POCKET FIRE WATER | CONTROL VALVE |  | FUEL POCKET FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV951 | BIN_VLV | Fuel pocket fire water control valve | BB1SV951 | FUEL POCKET FIRE WATER | CONTROL VALVE |  | BB1SV951 | FUEL POCKET FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV405 |  | BB1CV405 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve | BOTTOM ASH VALVE | SOLENOID VALVE |  | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV |  | BB1CV405 | BIN_VLV | Bottom ash valve solenoid valve | BB1CV405 | BOTTOM ASH VALVE | SOLENOID VALVE |  | BB1CV405 | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV406 |  | BB1CV406 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve | BOTTOM ASH VALVE | SOLENOID VALVE |  | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV |  | BB1CV406 | BIN_VLV | Bottom ash valve solenoid valve | BB1CV406 | BOTTOM ASH VALVE | SOLENOID VALVE |  | BB1CV406 | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV412 |  | BB1CV412 | <IO NOT ASSIGNED> | Bottom ash sieve bypass solenoid valve | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  | BOTTOM ASH SIEVE BYPASS SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV |  | BB1CV412 | BIN_VLV | Bottom ash sieve bypass solenoid valve | BB1CV412 | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  | BB1CV412 | BOTTOM ASH SIEVE BYPASS SOLENOID VALVE | CV | CONTROL VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV414 |  | BB1CV414 | <IO NOT ASSIGNED> | Work air to pneumatic transmitter pneumatic valve | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE | WORK AIR TO PNEUMATIC TRANSMITTER PNEUMATIC VAL VE | CV | CONTROL VALVE | DO | BIN_VLV |  | BB1CV414 | BIN_VLV | Work air to pneumatic transmitter pneumatic valve | BB1CV414 | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE | BB1CV414 | WORK AIR TO PNEUMATIC TRANSMITTER PNEUMATIC VAL VE | CV | CONTROL VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV405 |  | BB1SV405 | <IO NOT ASSIGNED> | Sand filling valve solenoid valve | SAND FILLING VALVE | SOLENOID VALVE |  | SAND FILLING VALVE SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV405 | BIN_VLV | Sand filling valve solenoid valve | BB1SV405 | SAND FILLING VALVE | SOLENOID VALVE |  | BB1SV405 | SAND FILLING VALVE SOLENOID VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV401 |  | BB1SV401 | <IO NOT ASSIGNED> | Bottom ash purging air solenoid valve | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV401 | BIN_VLV | Bottom ash purging air solenoid valve | BB1SV401 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BB1SV401 | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1SV402 |  | BB1SV402 | <IO NOT ASSIGNED> | Bottom ash purging air solenoid valve | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV402 | BIN_VLV | Bottom ash purging air solenoid valve | BB1SV402 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BB1SV402 | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV413 |  | BB1CV413 | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER | CV | CONTROL VALVE | DO | BIN_VLV_2DO |  | BB1CV413 | BIN_VLV_2DO | Control valve of pneumatic transmitter damper | BB1CV413 | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER | BB1CV413 | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER | CV | CONTROL VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV413 | _OPEN | BB1CV413_OPEN | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper OPEN | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER OPEN | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER OPEN | CV | CONTROL VALVE | DO | BIN_VLV_2DO |  | BB1BU500 | BURNER | Burner signals | BB1BU500 | BURNER SIGNALS |  |  | BB1BU500 | BURNER SIGNALS | BU | BURNER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV413 | _CLOSE | BB1CV413_CLOSE | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper CLOSE | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER CLOSE | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER CLOSE | CV | CONTROL VALVE | DO | BIN_VLV_2DO |  | BB1PU800 | CHEMICAL_PUMP | Chemical dosing pump 1 | BB1PU800 | CHEMICAL DOSING PUMP 1 |  |  | BB1PU800 | CHEMICAL DOSING PUMP 1 | PU | PUMP | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1BU500 | _DO_IF1 | BB1BU500_DO_IF1 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 1 | BURNER DIGITAL OUTPUT | INTERFACE 1 |  | BURNER DIGITAL OUTPUT INTERFACE 1 | BU | BURNER | DO | BURNER |  | BB1PU801 | CHEMICAL_PUMP | Chemical dosing pump 2 | BB1PU801 | CHEMICAL DOSING PUMP 2 |  |  | BB1PU801 | CHEMICAL DOSING PUMP 2 | PU | PUMP | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1BU500 | _DO_IF2 | BB1BU500_DO_IF2 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 2 | BURNER DIGITAL OUTPUT | INTERFACE 2 |  | BURNER DIGITAL OUTPUT INTERFACE 2 | BU | BURNER | DO | BURNER |  | BB1EM402 | COMPR | Compressor 1 | BB1EM402 | COMPRESSOR 1 |  |  | BB1EM402 | COMPRESSOR 1 | EM | MOTOR | MOTOR 30kW | MOTOR 30kW, 3 PHASE |  | 30kW, 400VAC |  |  |  |  | 30
BB1BU500 | _DO_IF3 | BB1BU500_DO_IF3 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 3 | BURNER DIGITAL OUTPUT | INTERFACE 3 |  | BURNER DIGITAL OUTPUT INTERFACE 3 | BU | BURNER | DO | BURNER |  | BB1EM403 | COMPR | Compressor 2 | BB1EM403 | COMPRESSOR 2 |  |  | BB1EM403 | COMPRESSOR 2 | EM | MOTOR | MOTOR 30kW | MOTOR 30kW, 3 PHASE |  | 30kW, 400VAC |  |  |  |  | 30
BB1BU500 | _DO_IF4 | BB1BU500_DO_IF4 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 4 | BURNER DIGITAL OUTPUT | INTERFACE 4 |  | BURNER DIGITAL OUTPUT INTERFACE 4 | BU | BURNER | DO | BURNER |  | BB1PT200 | MEAS_ANA | Feed water tank pressure | BB1PT200 | FEED WATER TANK PRESSURE |  |  | BB1PT200 | FEED WATER TANK PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _DO_IF5 | BB1BU500_DO_IF5 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 5 | BURNER DIGITAL OUTPUT | INTERFACE 5 |  | BURNER DIGITAL OUTPUT INTERFACE 5 | BU | BURNER | DO | BURNER |  | BB1LT001 | MEAS_ANA | Feed water tank level 1 | BB1LT001 | FEED WATER TANK LEVEL 1 |  |  | BB1LT001 | FEED WATER TANK LEVEL 1 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _DI_IF1 | BB1BU500_DI_IF1 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 1 | BURNER DIGITAL INPUT | INTERFACE 1 |  | BURNER DIGITAL INPUT INTERFACE 1 | BU | BURNER | DI | BURNER |  | BB1LT002 | MEAS_ANA | Feed water tank level 2 | BB1LT002 | FEED WATER TANK LEVEL 2 |  |  | BB1LT002 | FEED WATER TANK LEVEL 2 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _DI_IF2 | BB1BU500_DI_IF2 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 2 | BURNER DIGITAL INPUT | INTERFACE 2 |  | BURNER DIGITAL INPUT INTERFACE 2 | BU | BURNER | DI | BURNER |  | BB1PT005 | MEAS_ANA | Feed water pressure after valve | BB1PT005 | FEED WATER PRESSURE | AFTER VALVE |  | BB1PT005 | FEED WATER PRESSURE AFTER VALVE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _DI_IF3 | BB1BU500_DI_IF3 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 3 | BURNER DIGITAL INPUT | INTERFACE 3 |  | BURNER DIGITAL INPUT INTERFACE 3 | BU | BURNER | DI | BURNER |  | BB1FT001 | MEAS_ANA | Feed water flow and control | BB1FT001 | FEED WATER FLOW | AND CONTROL |  | BB1FT001 | FEED WATER FLOW AND CONTROL | FT | FLOW TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _DI_IF4 | BB1BU500_DI_IF4 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 4 | BURNER DIGITAL INPUT | INTERFACE 4 |  | BURNER DIGITAL INPUT INTERFACE 4 | BU | BURNER | DI | BURNER |  | BB1TT001 | MEAS_ANA | Feed water temperature | BB1TT001 | FEED WATER TEMPERATURE |  |  | BB1TT001 | FEED WATER TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _DI_IF5 | BB1BU500_DI_IF5 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 5 | BURNER DIGITAL INPUT | INTERFACE 5 |  | BURNER DIGITAL INPUT INTERFACE 5 | BU | BURNER | DI | BURNER |  | BB1TT002 | MEAS_ANA | Feed water pump 2 bearing temperature | BB1TT002 | FEED WATER PUMP 2 | BEARING TEMPERATURE |  | BB1TT002 | FEED WATER PUMP 2 BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _AO_IF1 | BB1BU500_AO_IF1 | <IO NOT ASSIGNED> | BURNER ANALOGUE OUTPUT INTERFACE 1 | BURNER ANALOGUE OUTPUT | INTERFACE 1 |  | BURNER ANALOGUE OUTPUT INTERFACE 1 | BU | BURNER | AO | BURNER |  | BB1PT004 | MEAS_ANA | Feed water pressure before valve | BB1PT004 | FEED WATER PRESSURE | BEFORE VALVE |  | BB1PT004 | FEED WATER PRESSURE BEFORE VALVE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _AO_IF2 | BB1BU500_AO_IF2 | <IO NOT ASSIGNED> | BURNER ANALOGUE OUTPUT INTERFACE 2 | BURNER ANALOGUE OUTPUT | INTERFACE 2 |  | BURNER ANALOGUE OUTPUT INTERFACE 2 | BU | BURNER | AO | BURNER |  | BB1PT002 | MEAS_ANA | Feed water pump 2 pressure side pressure | BB1PT002 | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  | BB1PT002 | FEED WATER PUMP 2 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _AI_IF1 | BB1BU500_AI_IF1 | <IO NOT ASSIGNED> | BURNER ANALOGUE INPUT INTERFACE 1 | BURNER ANALOGUE INPUT | INTERFACE 1 |  | BURNER ANALOGUE INPUT INTERFACE 1 | BU | BURNER | AI | BURNER |  | BB1PT006 | MEAS_ANA | FW suction line strainer pressure diff. | BB1PT006 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | BB1PT006 | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1BU500 | _AI_IF2 | BB1BU500_AI_IF2 | <IO NOT ASSIGNED> | BURNER ANALOGUE INPUT INTERFACE 2 | BURNER ANALOGUE INPUT | INTERFACE 2 |  | BURNER ANALOGUE INPUT INTERFACE 2 | BU | BURNER | AI | BURNER |  | BB1PT007 | MEAS_ANA | FW suction line strainer pressure diff. | BB1PT007 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | BB1PT007 | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PU800 |  | BB1PU800 | <IO NOT ASSIGNED> | Chemical dosing pump 1 | CHEMICAL DOSING PUMP 1 |  |  | CHEMICAL DOSING PUMP 1 | PU | PUMP | DO | CHEMICAL_PUMP |  | BB1TT005 | MEAS_ANA | FW pump 2 motor winding temperature | BB1TT005 | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  | BB1TT005 | FW PUMP 2 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PU801 |  | BB1PU801 | <IO NOT ASSIGNED> | Chemical dosing pump 2 | CHEMICAL DOSING PUMP 2 |  |  | CHEMICAL DOSING PUMP 2 | PU | PUMP | DO | CHEMICAL_PUMP |  | BB1PT001 | MEAS_ANA | Feed water pump 1 pressure side pressure | BB1PT001 | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  | BB1PT001 | FEED WATER PUMP 1 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM402 |  | BB1EM402 | <IO NOT ASSIGNED> | Compressor 1 | COMPRESSOR 1 |  |  | COMPRESSOR 1 | EM | MOTOR | DO | COMPR |  | BB1TT004 | MEAS_ANA | FW pump 1 motor winding temperature | BB1TT004 | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  | BB1TT004 | FW PUMP 1 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM402 | _FAULT_DI | BB1EM402_FAULT_DI | <IO NOT ASSIGNED> | Compressor 1 Fault | COMPRESSOR 1 | FAULT |  | COMPRESSOR 1 FAULT | EM | MOTOR | DO | COMPR |  | BB1TT003 | MEAS_ANA | FW pump 1 motor bearing temperature | BB1TT003 | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  | BB1TT003 | FW PUMP 1 MOTOR BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM402 | _RUNNING_DI | BB1EM402_RUNNING_DI | <IO NOT ASSIGNED> | Compressor 1 Running | COMPRESSOR 1 | RUNNING |  | COMPRESSOR 1 RUNNING | EM | MOTOR | DO | COMPR |  | BB1TT008 | MEAS_ANA | Temperature after economizer | BB1TT008 | TEMPERATURE AFTER | ECONOMIZER |  | BB1TT008 | TEMPERATURE AFTER ECONOMIZER | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM402 | _RESERVE_DI | BB1EM402_RESERVE_DI | <IO NOT ASSIGNED> | Compressor 1 reserve | COMPRESSOR 1 | RESERVE |  | COMPRESSOR 1 RESERVE | EM | MOTOR | DO | COMPR |  | BB1FT200 | MEAS_ANA | Heating steam to feed water tank flow measurement | BB1FT200 | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT | BB1FT200 | HEATING STEAM TO FEED WATER TANK FLOW MEASUREMENT | FT | FLOW TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM402 | _RUN_DO | BB1EM402_RUN_DO | <IO NOT ASSIGNED> | Compressor 1 remote run | COMPRESSOR 1 | REMOTE RUN |  | COMPRESSOR 1 REMOTE RUN | EM | MOTOR | DO | COMPR |  | BB1TT009 | MEAS_ANA | Temperature before economizer | BB1TT009 | TEMPERATURE BEFORE | ECONOMIZER |  | BB1TT009 | TEMPERATURE BEFORE ECONOMIZER | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM402 | _FAULT_ACK_DO | BB1EM402_FAULT_ACK_DO | <IO NOT ASSIGNED> | Compressor 1 Fault Acknowledge | COMPRESSOR 1 | FAULT ACKNOWLEDGE |  | COMPRESSOR 1 FAULT ACKNOWLEDGE | EM | MOTOR | DO | COMPR |  | BB1TT200 | MEAS_ANA | Main steam temperature | BB1TT200 | MAIN STEAM TEMPERATURE |  |  | BB1TT200 | MAIN STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM403 |  | BB1EM403 | <IO NOT ASSIGNED> | Compressor 2 | COMPRESSOR 2 |  |  | COMPRESSOR 2 | EM | MOTOR | DO | COMPR |  | BB1FT202 | MEAS_ANA | Main steam flow | BB1FT202 | MAIN STEAM FLOW |  |  | BB1FT202 | MAIN STEAM FLOW | FT | FLOW TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM403 | _FAULT_DI | BB1EM403_FAULT_DI | <IO NOT ASSIGNED> | Compressor 2 Fault | COMPRESSOR 2 | FAULT |  | COMPRESSOR 2 FAULT | EM | MOTOR | DO | COMPR |  | BB1FT201 | MEAS_ANA | Steam flow to sootblowing and air preheater | BB1FT201 | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  | BB1FT201 | STEAM FLOW TO SOOTBLOWING AND AIR PREHEATER | FT | FLOW TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM403 | _RUNNING_DI | BB1EM403_RUNNING_DI | <IO NOT ASSIGNED> | Compressor 2 Running | COMPRESSOR 2 | RUNNING |  | COMPRESSOR 2 RUNNING | EM | MOTOR | DO | COMPR |  | BB1TT201 | MEAS_ANA | Sootblowing line temperature | BB1TT201 | SOOTBLOWING | LINE TEMPERATURE |  | BB1TT201 | SOOTBLOWING LINE TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1EM403 | _RESERVE_DI | BB1EM403_RESERVE_DI | <IO NOT ASSIGNED> | Compressor 2 reserve | COMPRESSOR 2 | RESERVE |  | COMPRESSOR 2 RESERVE | EM | MOTOR | DO | COMPR |  | <001> | #N/A | Electrical room temperature | <001> | ELECTRICAL ROOM | TEMPERATURE |  | <001> | ELECTRICAL ROOM TEMPERATURE | 1> | #N/A | #N/A | #N/A |  | #N/A |  |  |  |  | #N/A
BB1EM403 | _RUN_DO | BB1EM403_RUN_DO | <IO NOT ASSIGNED> | Compressor 2 remote run | COMPRESSOR 2 | REMOTE RUN |  | COMPRESSOR 2 REMOTE RUN | EM | MOTOR | DO | COMPR |  | <002> | #N/A | PLC-cabinet temperature | <002> | PLC-CABINET | TEMPERATURE |  | <002> | PLC-CABINET TEMPERATURE | 2> | #N/A | #N/A | #N/A |  | #N/A |  |  |  |  | #N/A
BB1EM403 | _FAULT_ACK_DO | BB1EM403_FAULT_ACK_DO | <IO NOT ASSIGNED> | Compressor 2 Fault Acknowledge | COMPRESSOR 2 | FAULT ACKNOWLEDGE |  | COMPRESSOR 2 FAULT ACKNOWLEDGE | EM | MOTOR | DO | COMPR |  | BB1TT006 | MEAS_ANA | Blow down tank temperature and control | BB1TT006 | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  | BB1TT006 | BLOW DOWN TANK TEMPERATURE AND CONTROL | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV200 | _SETPOINT | BB1CV200_SETPOINT | <IO NOT ASSIGNED> | Steam from drum control valve SETPOINT | STEAM FROM DRUM CONTROL | VALVE SETPOINT |  | STEAM FROM DRUM CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1TT202 | MEAS_ANA | Steam outlet temperature from accumulator | BB1TT202 | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  | BB1TT202 | STEAM OUTLET TEMPERATURE FROM ACCUMULATOR | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV200 | _POSITION | BB1CV200_POSITION | <IO NOT ASSIGNED> | Steam from drum control valve POSITION | STEAM FROM DRUM CONTROL | VALVE POSITION |  | STEAM FROM DRUM CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1PT207 | MEAS_ANA | Accumulator pressure | BB1PT207 | ACCUMULATOR PRESSURE |  |  | BB1PT207 | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV001 | _SETPOINT | BB1CV001_SETPOINT | <IO NOT ASSIGNED> | Make-up water control valve SETPOINT | MAKE-UP WATER CONTROL | VALVE SETPOINT |  | MAKE-UP WATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1TT007 | MEAS_ANA | Accumulator temperature | BB1TT007 | ACCUMULATOR TEMPERATURE |  |  | BB1TT007 | ACCUMULATOR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV001 | _POSITION | BB1CV001_POSITION | <IO NOT ASSIGNED> | Make-up water control valve POSITION | MAKE-UP WATER CONTROL | VALVE POSITION |  | MAKE-UP WATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1TT203 | MEAS_ANA | 18bar(g) steam temperature | BB1TT203 | 18BAR(G) STEAM | TEMPERATURE |  | BB1TT203 | 18BAR(G) STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV002 | _SETPOINT | BB1CV002_SETPOINT | <IO NOT ASSIGNED> | Feed water control valve SETPOINT | FEED WATER CONTROL VALVE | SETPOINT |  | FEED WATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1PT204 | MEAS_ANA | Main steam pressure | BB1PT204 | MAIN STEAM PRESSURE |  |  | BB1PT204 | MAIN STEAM PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV002 | _POSITION | BB1CV002_POSITION | <IO NOT ASSIGNED> | Feed water control valve POSITION | FEED WATER CONTROL VALVE | POSITION |  | FEED WATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1LT004 | MEAS_ANA | Steam accumulator level 2 | BB1LT004 | STEAM ACCUMULATOR LEVEL 2 |  |  | BB1LT004 | STEAM ACCUMULATOR LEVEL 2 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM300 | _SETPOINT | BB1DM300_SETPOINT | <IO NOT ASSIGNED> | Tertiary air damper 1 SETPOINT | TERTIARY AIR DAMPER 1 | SETPOINT |  | TERTIARY AIR DAMPER 1 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1PT208 | MEAS_ANA | Accumulator pressure | BB1PT208 | ACCUMULATOR PRESSURE |  |  | BB1PT208 | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM300 | _POSITION | BB1DM300_POSITION | <IO NOT ASSIGNED> | Tertiary air damper 1 POSITION | TERTIARY AIR DAMPER 1 | POSITION |  | TERTIARY AIR DAMPER 1 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1FT203 | MEAS_ANA | Steam to existing header flow measurement | BB1FT203 | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  | BB1FT203 | STEAM TO EXISTING HEADER FLOW MEASUREMENT | FT | FLOW TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM400 | _SETPOINT | BB1DM400_SETPOINT | <IO NOT ASSIGNED> | Primary air damper SETPOINT | PRIMARY AIR DAMPER | SETPOINT |  | PRIMARY AIR DAMPER SETPOINT | DM | DAMPER | AO | CONT_VLV |  | <003> | #N/A | Steam to existing header energy calculator | <003> | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  | <003> | STEAM TO EXISTING HEADER ENERGY CALCULATOR | 3> | #N/A | #N/A | #N/A |  | #N/A |  |  |  |  | #N/A
BB1DM400 | _POSITION | BB1DM400_POSITION | <IO NOT ASSIGNED> | Primary air damper POSITION | PRIMARY AIR DAMPER | POSITION |  | PRIMARY AIR DAMPER POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1LT003 | MEAS_ANA | Steam accumulator level 1 | BB1LT003 | STEAM ACCUMULATOR LEVEL 1 |  |  | BB1LT003 | STEAM ACCUMULATOR LEVEL 1 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM550 | _SETPOINT | BB1DM550_SETPOINT | <IO NOT ASSIGNED> | Recirculation gas damper SETPOINT | RECIRCULATION GAS DAMPER | SETPOINT |  | RECIRCULATION GAS DAMPER SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1QT002 | MEAS_ANA | pH measurement from feed water tank | BB1QT002 | PH MEASUREMENT FROM FEED | WATER TANK |  | BB1QT002 | PH MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM550 | _POSITION | BB1DM550_POSITION | <IO NOT ASSIGNED> | Recirculation gas damper POSITION | RECIRCULATION GAS DAMPER | POSITION |  | RECIRCULATION GAS DAMPER POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1QT006 | MEAS_ANA | Conductivity measurement from main steam | BB1QT006 | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  | BB1QT006 | CONDUCTIVITY MEASUREMENT FROM MAIN STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM301 | _SETPOINT | BB1DM301_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 4 SETPOINT | SECONDARY AIR DAMPER 4 | SETPOINT |  | SECONDARY AIR DAMPER 4 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1QT005 | MEAS_ANA | Conductivity measurement from saturated steam | BB1QT005 | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  | BB1QT005 | CONDUCTIVITY MEASUREMENT FROM SATURATED STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM301 | _POSITION | BB1DM301_POSITION | <IO NOT ASSIGNED> | Secondary air damper 4 POSITION | SECONDARY AIR DAMPER 4 | POSITION |  | SECONDARY AIR DAMPER 4 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1QT003 | MEAS_ANA | Conductivity measurement from condensate | BB1QT003 | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  | BB1QT003 | CONDUCTIVITY MEASUREMENT FROM CONDENSATE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM302 | _SETPOINT | BB1DM302_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 3 SETPOINT | SECONDARY AIR DAMPER 3 | SETPOINT |  | SECONDARY AIR DAMPER 3 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1QT007 | MEAS_ANA | Conductivity measurement from feed water line | BB1QT007 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  | BB1QT007 | CONDUCTIVITY MEASUREMENT FROM FEED WATER LINE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM302 | _POSITION | BB1DM302_POSITION | <IO NOT ASSIGNED> | Secondary air damper 3 POSITION | SECONDARY AIR DAMPER 3 | POSITION |  | SECONDARY AIR DAMPER 3 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1QT001 | MEAS_ANA | Conductivity measurement from feed water tank | BB1QT001 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  | BB1QT001 | CONDUCTIVITY MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM304 | _SETPOINT | BB1DM304_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 1 SETPOINT | SECONDARY AIR DAMPER 1 | SETPOINT |  | SECONDARY AIR DAMPER 1 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1QT004 | MEAS_ANA | Conductivity measurement from boiler water | BB1QT004 | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  | BB1QT004 | CONDUCTIVITY MEASUREMENT FROM BOILER WATER | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM304 | _POSITION | BB1DM304_POSITION | <IO NOT ASSIGNED> | Secondary air damper 1 POSITION | SECONDARY AIR DAMPER 1 | POSITION |  | SECONDARY AIR DAMPER 1 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1PT410 | MEAS_ANA | Secondary air pressure inner front wall | BB1PT410 | SECONDARY AIR PRESSURE | INNER FRONT WALL |  | BB1PT410 | SECONDARY AIR PRESSURE INNER FRONT WALL | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM303 | _SETPOINT | BB1DM303_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 2 SETPOINT | SECONDARY AIR DAMPER 2 | SETPOINT |  | SECONDARY AIR DAMPER 2 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1TT551 | MEAS_ANA | Flue gas temperature 2 | BB1TT551 | FLUE GAS TEMPERATURE 2 |  |  | BB1TT551 | FLUE GAS TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1DM303 | _POSITION | BB1DM303_POSITION | <IO NOT ASSIGNED> | Secondary air damper 2 POSITION | SECONDARY AIR DAMPER 2 | POSITION |  | SECONDARY AIR DAMPER 2 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1TT400 | MEAS_ANA | Primary air temperature before preheater | BB1TT400 | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  | BB1TT400 | PRIMARY AIR TEMPERATURE BEFORE PREHEATER | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV004 | _SETPOINT | BB1CV004_SETPOINT | <IO NOT ASSIGNED> | Primary air preheater control valve SETPOINT | PRIMARY AIR PREHEATER | CONTROL VALVE SETPOINT |  | PRIMARY AIR PREHEATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1PT403 | MEAS_ANA | Secondary air pressure inner back wall | BB1PT403 | SECONDARY AIR PRESSURE | INNER BACK WALL |  | BB1PT403 | SECONDARY AIR PRESSURE INNER BACK WALL | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV004 | _POSITION | BB1CV004_POSITION | <IO NOT ASSIGNED> | Primary air preheater control valve POSITION | PRIMARY AIR PREHEATER | CONTROL VALVE POSITION |  | PRIMARY AIR PREHEATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1PT550 | MEAS_ANA | Flue gas pressure at the outlet of the boiler | BB1PT550 | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  | BB1PT550 | FLUE GAS PRESSURE AT THE OUTLET OF THE BOILER | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV402 | _SETPOINT | BB1CV402_SETPOINT | <IO NOT ASSIGNED> | Fuel chute B carrying air control valve 2 SETPOINT | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | SETPOINT | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1TT012 | MEAS_ANA | Condensate temperature from primary air preheater | BB1TT012 | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R | BB1TT012 | CONDENSATE TEMPERATURE FROM PRIMARY AIR PREHEATE R | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV402 | _POSITION | BB1CV402_POSITION | <IO NOT ASSIGNED> | Fuel chute B carrying air control valve 2 POSITION | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | POSITION | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1TT550 | MEAS_ANA | Flue gas temperature 1 | BB1TT550 | FLUE GAS TEMPERATURE 1 |  |  | BB1TT550 | FLUE GAS TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV403 | _SETPOINT | BB1CV403_SETPOINT | <IO NOT ASSIGNED> | Fuel chute A carrying air control valve 1 SETPOINT | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | SETPOINT | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1TT412 | MEAS_ANA | Boiler temperature after empty draft 2 | BB1TT412 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  | BB1TT412 | BOILER TEMPERATURE AFTER EMPTY DRAFT 2 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1CV403 | _POSITION | BB1CV403_POSITION | <IO NOT ASSIGNED> | Fuel chute A carrying air control valve 1 POSITION | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | POSITION | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1TT411 | MEAS_ANA | Boiler temperature after empty draft 1 | BB1TT411 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  | BB1TT411 | BOILER TEMPERATURE AFTER EMPTY DRAFT 1 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT200 |  | BB1PT200 | <IO NOT ASSIGNED> | Feed water tank pressure | FEED WATER TANK PRESSURE |  |  | FEED WATER TANK PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1QT552 | MEAS_ANA | Fluegas CO measurement | BB1QT552 | FLUEGAS CO MEASUREMENT |  |  | BB1QT552 | FLUEGAS CO MEASUREMENT | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT001 |  | BB1LT001 | <IO NOT ASSIGNED> | Feed water tank level 1 | FEED WATER TANK LEVEL 1 |  |  | FEED WATER TANK LEVEL 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1TT405 | MEAS_ANA | Primary air temperature | BB1TT405 | PRIMARY AIR TEMPERATURE |  |  | BB1TT405 | PRIMARY AIR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT002 |  | BB1LT002 | <IO NOT ASSIGNED> | Feed water tank level 2 | FEED WATER TANK LEVEL 2 |  |  | FEED WATER TANK LEVEL 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1TT415 | MEAS_ANA | Boiler bed temperature middle level | BB1TT415 | BOILER BED TEMPERATURE | MIDDLE LEVEL |  | BB1TT415 | BOILER BED TEMPERATURE MIDDLE LEVEL | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT005 |  | BB1PT005 | <IO NOT ASSIGNED> | Feed water pressure after valve | FEED WATER PRESSURE | AFTER VALVE |  | FEED WATER PRESSURE AFTER VALVE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT416 | MEAS_ANA | Boiler bed temperature lower level | BB1TT416 | BOILER BED TEMPERATURE | LOWER LEVEL |  | BB1TT416 | BOILER BED TEMPERATURE LOWER LEVEL | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1FT001 |  | BB1FT001 | <IO NOT ASSIGNED> | Feed water flow and control | FEED WATER FLOW | AND CONTROL |  | FEED WATER FLOW AND CONTROL | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1TT410 | MEAS_ANA | Boiler 1st draft temperature | BB1TT410 | BOILER 1ST DRAFT | TEMPERATURE |  | BB1TT410 | BOILER 1ST DRAFT TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT001 |  | BB1TT001 | <IO NOT ASSIGNED> | Feed water temperature | FEED WATER TEMPERATURE |  |  | FEED WATER TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT116 | MEAS_ANA | Steam temperature to air preheater | BB1TT116 | STEAM TEMPERATURE TO | AIR PREHEATER |  | BB1TT116 | STEAM TEMPERATURE TO AIR PREHEATER | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT002 |  | BB1TT002 | <IO NOT ASSIGNED> | Feed water pump 2 bearing temperature | FEED WATER PUMP 2 | BEARING TEMPERATURE |  | FEED WATER PUMP 2 BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT308 | MEAS_ANA | Furnace temperature connection | BB1TT308 | FURNACE TEMPERATURE | CONNECTION |  | BB1TT308 | FURNACE TEMPERATURE CONNECTION | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT004 |  | BB1PT004 | <IO NOT ASSIGNED> | Feed water pressure before valve | FEED WATER PRESSURE | BEFORE VALVE |  | FEED WATER PRESSURE BEFORE VALVE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1QT553 | MEAS_ANA | Boiler room gas detector | BB1QT553 | BOILER ROOM GAS DETECTOR |  |  | BB1QT553 | BOILER ROOM GAS DETECTOR | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT002 |  | BB1PT002 | <IO NOT ASSIGNED> | Feed water pump 2 pressure side pressure | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  | FEED WATER PUMP 2 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT408 | MEAS_ANA | Secondary air fan motor bearing temperature 1 | BB1TT408 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | BB1TT408 | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT006 |  | BB1PT006 | <IO NOT ASSIGNED> | FW suction line strainer pressure diff. | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT423 | MEAS_ANA | Secondary air fan motor bearing temperature 2 | BB1TT423 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | BB1TT423 | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT007 |  | BB1PT007 | <IO NOT ASSIGNED> | FW suction line strainer pressure diff. | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT406 | MEAS_ANA | Secondary air fan motor winding temperature 1 | BB1TT406 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | BB1TT406 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT005 |  | BB1TT005 | <IO NOT ASSIGNED> | FW pump 2 motor winding temperature | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  | FW PUMP 2 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT404 | MEAS_ANA | Primary air fan motor bearing temperature 1 | BB1TT404 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | BB1TT404 | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT001 |  | BB1PT001 | <IO NOT ASSIGNED> | Feed water pump 1 pressure side pressure | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  | FEED WATER PUMP 1 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT409 | MEAS_ANA | Primary air fan motor bearing temperature 2 | BB1TT409 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | BB1TT409 | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT004 |  | BB1TT004 | <IO NOT ASSIGNED> | FW pump 1 motor winding temperature | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  | FW PUMP 1 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT402 | MEAS_ANA | Primary air fan motor winding temperature 1 | BB1TT402 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | BB1TT402 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT003 |  | BB1TT003 | <IO NOT ASSIGNED> | FW pump 1 motor bearing temperature | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  | FW PUMP 1 MOTOR BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT403 | MEAS_ANA | Primary air fan motor winding temperature 2 | BB1TT403 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | BB1TT403 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT008 |  | BB1TT008 | <IO NOT ASSIGNED> | Temperature after economizer | TEMPERATURE AFTER | ECONOMIZER |  | TEMPERATURE AFTER ECONOMIZER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT421 | MEAS_ANA | Primary air fan motor winding temperature 3 | BB1TT421 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | BB1TT421 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1FT200 |  | BB1FT200 | <IO NOT ASSIGNED> | Heating steam to feed water tank flow measurement | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT | HEATING STEAM TO FEED WATER TANK FLOW MEASUREMENT | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1TT407 | MEAS_ANA | Secondary air fan motor winding temperature 2 | BB1TT407 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | BB1TT407 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT009 |  | BB1TT009 | <IO NOT ASSIGNED> | Temperature before economizer | TEMPERATURE BEFORE | ECONOMIZER |  | TEMPERATURE BEFORE ECONOMIZER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT422 | MEAS_ANA | Secondary air fan motor winding temperature 3 | BB1TT422 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | BB1TT422 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT200 |  | BB1TT200 | <IO NOT ASSIGNED> | Main steam temperature | MAIN STEAM TEMPERATURE |  |  | MAIN STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT409 | MEAS_ANA | Secondary air pressure outer front wall | BB1PT409 | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  | BB1PT409 | SECONDARY AIR PRESSURE OUTER FRONT WALL | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1FT202 |  | BB1FT202 | <IO NOT ASSIGNED> | Main steam flow | MAIN STEAM FLOW |  |  | MAIN STEAM FLOW | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1PT411 | MEAS_ANA | Secondary air pressure outer back wall | BB1PT411 | SECONDARY AIR PRESSURE | OUTER BACK WALL |  | BB1PT411 | SECONDARY AIR PRESSURE OUTER BACK WALL | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1FT201 |  | BB1FT201 | <IO NOT ASSIGNED> | Steam flow to sootblowing and air preheater | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  | STEAM FLOW TO SOOTBLOWING AND AIR PREHEATER | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1PT407 | MEAS_ANA | Tertiary air pressure right wall | BB1PT407 | TERTIARY AIR PRESSURE | RIGHT WALL |  | BB1PT407 | TERTIARY AIR PRESSURE RIGHT WALL | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT201 |  | BB1TT201 | <IO NOT ASSIGNED> | Sootblowing line temperature | SOOTBLOWING | LINE TEMPERATURE |  | SOOTBLOWING LINE TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT408 | MEAS_ANA | Tertiary air pressure left wall | BB1PT408 | TERTIARY AIR PRESSURE | LEFT WALL |  | BB1PT408 | TERTIARY AIR PRESSURE LEFT WALL | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
<001> |  | <001> | <IO NOT ASSIGNED> | Electrical room temperature | ELECTRICAL ROOM | TEMPERATURE |  | ELECTRICAL ROOM TEMPERATURE | 1> | #N/A | AI | #N/A |  | BB1TT650 | MEAS_ANA | Scraper conveyor 1 temperature measurement | BB1TT650 | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  | BB1TT650 | SCRAPER CONVEYOR 1 TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
<002> |  | <002> | <IO NOT ASSIGNED> | PLC-cabinet temperature | PLC-CABINET | TEMPERATURE |  | PLC-CABINET TEMPERATURE | 2> | #N/A | AI | #N/A |  | BB1LT611 | MEAS_ANA | Unloading station 1 level | BB1LT611 | UNLOADING STATION 1 LEVEL |  |  | BB1LT611 | UNLOADING STATION 1 LEVEL | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT006 |  | BB1TT006 | <IO NOT ASSIGNED> | Blow down tank temperature and control | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  | BLOW DOWN TANK TEMPERATURE AND CONTROL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT612 | MEAS_ANA | Unloading station 3 level | BB1LT612 | UNLOADING STATION 3 LEVEL |  |  | BB1LT612 | UNLOADING STATION 3 LEVEL | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT202 |  | BB1TT202 | <IO NOT ASSIGNED> | Steam outlet temperature from accumulator | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  | STEAM OUTLET TEMPERATURE FROM ACCUMULATOR | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT613 | MEAS_ANA | Unloading station 2 level | BB1LT613 | UNLOADING STATION 2 LEVEL |  |  | BB1LT613 | UNLOADING STATION 2 LEVEL | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT207 |  | BB1PT207 | <IO NOT ASSIGNED> | Accumulator pressure | ACCUMULATOR PRESSURE |  |  | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT650 | MEAS_ANA | Fuel silo level radar 1 | BB1LT650 | FUEL SILO LEVEL RADAR 1 |  |  | BB1LT650 | FUEL SILO LEVEL RADAR 1 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT007 |  | BB1TT007 | <IO NOT ASSIGNED> | Accumulator temperature | ACCUMULATOR TEMPERATURE |  |  | ACCUMULATOR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT651 | MEAS_ANA | Fuel silo level radar 2 | BB1LT651 | FUEL SILO LEVEL RADAR 2 |  |  | BB1LT651 | FUEL SILO LEVEL RADAR 2 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT203 |  | BB1TT203 | <IO NOT ASSIGNED> | 18bar(g) steam temperature | 18BAR(G) STEAM | TEMPERATURE |  | 18BAR(G) STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT652 | MEAS_ANA | Fuel pocket level | BB1LT652 | FUEL POCKET LEVEL |  |  | BB1LT652 | FUEL POCKET LEVEL | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT204 |  | BB1PT204 | <IO NOT ASSIGNED> | Main steam pressure | MAIN STEAM PRESSURE |  |  | MAIN STEAM PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT652 | MEAS_ANA | Fuel silo temperature measurement | BB1TT652 | FUEL SILO TEMPERATURE | MEASUREMENT |  | BB1TT652 | FUEL SILO TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT004 |  | BB1LT004 | <IO NOT ASSIGNED> | Steam accumulator level 2 | STEAM ACCUMULATOR LEVEL 2 |  |  | STEAM ACCUMULATOR LEVEL 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1TT653 | MEAS_ANA | Fuel pocket temperature | BB1TT653 | FUEL POCKET TEMPERATURE |  |  | BB1TT653 | FUEL POCKET TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT208 |  | BB1PT208 | <IO NOT ASSIGNED> | Accumulator pressure | ACCUMULATOR PRESSURE |  |  | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT552 | MEAS_ANA | ESP inlet pressure transmitter | BB1PT552 | ESP INLET PRESSURE | TRANSMITTER |  | BB1PT552 | ESP INLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1FT203 |  | BB1FT203 | <IO NOT ASSIGNED> | Steam to existing header flow measurement | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  | STEAM TO EXISTING HEADER FLOW MEASUREMENT | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1PT553 | MEAS_ANA | ESP outlet pressure transmitter | BB1PT553 | ESP OUTLET PRESSURE | TRANSMITTER |  | BB1PT553 | ESP OUTLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
<003> |  | <003> | <IO NOT ASSIGNED> | Steam to existing header energy calculator | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  | STEAM TO EXISTING HEADER ENERGY CALCULATOR | 3> | #N/A | AI | #N/A |  | BB1QT554 | MEAS_ANA | Opacity after ESP | BB1QT554 | OPACITY AFTER ESP |  |  | BB1QT554 | OPACITY AFTER ESP | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT003 |  | BB1LT003 | <IO NOT ASSIGNED> | Steam accumulator level 1 | STEAM ACCUMULATOR LEVEL 1 |  |  | STEAM ACCUMULATOR LEVEL 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1TT553 | MEAS_ANA | Flue gas fan motor winding temperature 1 | BB1TT553 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  | BB1TT553 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT002 |  | BB1QT002 | <IO NOT ASSIGNED> | pH measurement from feed water tank | PH MEASUREMENT FROM FEED | WATER TANK |  | PH MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT557 | MEAS_ANA | Flue gas fan motor winding temperature 2 | BB1TT557 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  | BB1TT557 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT006 |  | BB1QT006 | <IO NOT ASSIGNED> | Conductivity measurement from main steam | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  | CONDUCTIVITY MEASUREMENT FROM MAIN STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT558 | MEAS_ANA | Flue gas fan motor winding temperature 3 | BB1TT558 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  | BB1TT558 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT005 |  | BB1QT005 | <IO NOT ASSIGNED> | Conductivity measurement from saturated steam | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  | CONDUCTIVITY MEASUREMENT FROM SATURATED STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT554 | MEAS_ANA | Flue gas fan bearing temperature | BB1TT554 | FLUE GAS FAN BEARING | TEMPERATURE |  | BB1TT554 | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT003 |  | BB1QT003 | <IO NOT ASSIGNED> | Conductivity measurement from condensate | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  | CONDUCTIVITY MEASUREMENT FROM CONDENSATE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT555 | MEAS_ANA | Flue gas fan bearing temperature | BB1TT555 | FLUE GAS FAN BEARING | TEMPERATURE |  | BB1TT555 | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT007 |  | BB1QT007 | <IO NOT ASSIGNED> | Conductivity measurement from feed water line | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  | CONDUCTIVITY MEASUREMENT FROM FEED WATER LINE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT556 | MEAS_ANA | Flue gas temperature before stack | BB1TT556 | FLUE GAS TEMPERATURE | BEFORE STACK |  | BB1TT556 | FLUE GAS TEMPERATURE BEFORE STACK | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT001 |  | BB1QT001 | <IO NOT ASSIGNED> | Conductivity measurement from feed water tank | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  | CONDUCTIVITY MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT850 | MEAS_ANA | ESP Ash hopper 1 temperature | BB1TT850 | ESP ASH HOPPER 1 | TEMPERATURE |  | BB1TT850 | ESP ASH HOPPER 1 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT004 |  | BB1QT004 | <IO NOT ASSIGNED> | Conductivity measurement from boiler water | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  | CONDUCTIVITY MEASUREMENT FROM BOILER WATER | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT851 | MEAS_ANA | ESP Ash hopper 2 temperature | BB1TT851 | ESP ASH HOPPER 2 | TEMPERATURE |  | BB1TT851 | ESP ASH HOPPER 2 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT410 |  | BB1PT410 | <IO NOT ASSIGNED> | Secondary air pressure inner front wall | SECONDARY AIR PRESSURE | INNER FRONT WALL |  | SECONDARY AIR PRESSURE INNER FRONT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TS501 | MEAS_ANA | ESP Insulator 1 temperature | BB1TS501 | ESP INSULATOR 1 | TEMPERATURE |  | BB1TS501 | ESP INSULATOR 1 TEMPERATURE | TS | TEMPERATURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT551 |  | BB1TT551 | <IO NOT ASSIGNED> | Flue gas temperature 2 | FLUE GAS TEMPERATURE 2 |  |  | FLUE GAS TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TS508 | MEAS_ANA | ESP Insulator 2 temperature | BB1TS508 | ESP INSULATOR 2 | TEMPERATURE |  | BB1TS508 | ESP INSULATOR 2 TEMPERATURE | TS | TEMPERATURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT400 |  | BB1TT400 | <IO NOT ASSIGNED> | Primary air temperature before preheater | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  | PRIMARY AIR TEMPERATURE BEFORE PREHEATER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT552 | MEAS_ANA | Flue gas temperature before ESP | BB1TT552 | FLUE GAS TEMPERATURE | BEFORE ESP |  | BB1TT552 | FLUE GAS TEMPERATURE BEFORE ESP | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT403 |  | BB1PT403 | <IO NOT ASSIGNED> | Secondary air pressure inner back wall | SECONDARY AIR PRESSURE | INNER BACK WALL |  | SECONDARY AIR PRESSURE INNER BACK WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT800 | MEAS_ANA | Recycled bed material hopper level switch | BB1LT800 | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  | BB1LT800 | RECYCLED BED MATERIAL HOPPER LEVEL SWITCH | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT550 |  | BB1PT550 | <IO NOT ASSIGNED> | Flue gas pressure at the outlet of the boiler | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  | FLUE GAS PRESSURE AT THE OUTLET OF THE BOILER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT802 | MEAS_ANA | Sand silo level measurement | BB1LT802 | SAND SILO LEVEL | MEASUREMENT |  | BB1LT802 | SAND SILO LEVEL MEASUREMENT | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT012 |  | BB1TT012 | <IO NOT ASSIGNED> | Condensate temperature from primary air preheater | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R | CONDENSATE TEMPERATURE FROM PRIMARY AIR PREHEATE R | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT009 | MEAS_ANA | Cooling water pressure before pump | BB1PT009 | COOLING WATER PRESSURE | BEFORE PUMP |  | BB1PT009 | COOLING WATER PRESSURE BEFORE PUMP | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT550 |  | BB1TT550 | <IO NOT ASSIGNED> | Flue gas temperature 1 | FLUE GAS TEMPERATURE 1 |  |  | FLUE GAS TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT031 | MEAS_ANA | Cooling water temperatureafter bottom ash conveyor | BB1TT031 | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  | BB1TT031 | COOLING WATER TEMPERATURE AFTER BOTTOM ASH CONVEYOR | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT412 |  | BB1TT412 | <IO NOT ASSIGNED> | Boiler temperature after empty draft 2 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  | BOILER TEMPERATURE AFTER EMPTY DRAFT 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT478 | MEAS_ANA | Instrument air pressure | BB1PT478 | INSTRUMENT AIR PRESSURE |  |  | BB1PT478 | INSTRUMENT AIR PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT411 |  | BB1TT411 | <IO NOT ASSIGNED> | Boiler temperature after empty draft 1 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  | BOILER TEMPERATURE AFTER EMPTY DRAFT 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT402 | MEAS_ANA | Instrument air pressure after dryer | BB1PT402 | INSTRUMENT AIR PRESSURE | AFTER DRYER |  | BB1PT402 | INSTRUMENT AIR PRESSURE AFTER DRYER | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT552 |  | BB1QT552 | <IO NOT ASSIGNED> | Fluegas CO measurement | FLUEGAS CO MEASUREMENT |  |  | FLUEGAS CO MEASUREMENT | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT430 | MEAS_ANA | Instrument air tank temperature | BB1TT430 | INSTRUMENT AIR TANK | TEMPERATURE |  | BB1TT430 | INSTRUMENT AIR TANK TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT405 |  | BB1TT405 | <IO NOT ASSIGNED> | Primary air temperature | PRIMARY AIR TEMPERATURE |  |  | PRIMARY AIR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT401 | MEAS_ANA | Boiler room upper part temperature | BB1TT401 | BOILER ROOM UPPER PART | TEMPERATURE |  | BB1TT401 | BOILER ROOM UPPER PART TEMPERATURE | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT415 |  | BB1TT415 | <IO NOT ASSIGNED> | Boiler bed temperature middle level | BOILER BED TEMPERATURE | MIDDLE LEVEL |  | BOILER BED TEMPERATURE MIDDLE LEVEL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT101 | MEAS_ANA_SRS | Steam drum level 1 | BB1LT101 | STEAM DRUM LEVEL 1 |  |  | BB1LT101 | STEAM DRUM LEVEL 1 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT416 |  | BB1TT416 | <IO NOT ASSIGNED> | Boiler bed temperature lower level | BOILER BED TEMPERATURE | LOWER LEVEL |  | BOILER BED TEMPERATURE LOWER LEVEL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT203 | MEAS_ANA_SRS | Steam drum pressure 2 | BB1PT203 | STEAM DRUM PRESSURE 2 |  |  | BB1PT203 | STEAM DRUM PRESSURE 2 | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT410 |  | BB1TT410 | <IO NOT ASSIGNED> | Boiler 1st draft temperature | BOILER 1ST DRAFT | TEMPERATURE |  | BOILER 1ST DRAFT TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT102 | MEAS_ANA_SRS | Steam drum level 2 | BB1LT102 | STEAM DRUM LEVEL 2 |  |  | BB1LT102 | STEAM DRUM LEVEL 2 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT116 |  | BB1TT116 | <IO NOT ASSIGNED> | Steam temperature to air preheater | STEAM TEMPERATURE TO | AIR PREHEATER |  | STEAM TEMPERATURE TO AIR PREHEATER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT201 | MEAS_ANA_SRS | Steam drum pressure 1 | BB1PT201 | STEAM DRUM PRESSURE 1 |  |  | BB1PT201 | STEAM DRUM PRESSURE 1 | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT308 |  | BB1TT308 | <IO NOT ASSIGNED> | Furnace temperature connection | FURNACE TEMPERATURE | CONNECTION |  | FURNACE TEMPERATURE CONNECTION | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT103 | MEAS_ANA_SRS | Steam drum level 3 | BB1LT103 | STEAM DRUM LEVEL 3 |  |  | BB1LT103 | STEAM DRUM LEVEL 3 | LT | LEVEL TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT553 |  | BB1QT553 | <IO NOT ASSIGNED> | Boiler room gas detector | BOILER ROOM GAS DETECTOR |  |  | BOILER ROOM GAS DETECTOR | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1PT205 | MEAS_ANA_SRS | Steam outlet pressure from accumulator | BB1PT205 | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  | BB1PT205 | STEAM OUTLET PRESSURE FROM ACCUMULATOR | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT408 |  | BB1TT408 | <IO NOT ASSIGNED> | Secondary air fan motor bearing temperature 1 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT400 | MEAS_ANA_SRS | Primary air pressure | BB1PT400 | PRIMARY AIR PRESSURE |  |  | BB1PT400 | PRIMARY AIR PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT423 |  | BB1TT423 | <IO NOT ASSIGNED> | Secondary air fan motor bearing temperature 2 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT418 | MEAS_ANA_SRS | Bed temperature 4 | BB1TT418 | BED TEMPERATURE 4 |  |  | BB1TT418 | BED TEMPERATURE 4 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT406 |  | BB1TT406 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 1 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT404 | MEAS_ANA_SRS | Boiler upper part pressure 1 | BB1PT404 | BOILER UPPER PART | PRESSURE 1 |  | BB1PT404 | BOILER UPPER PART PRESSURE 1 | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT404 |  | BB1TT404 | <IO NOT ASSIGNED> | Primary air fan motor bearing temperature 1 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1FT400 | MEAS_ANA_SRS | Primary air flow | BB1FT400 | PRIMARY AIR FLOW |  |  | BB1FT400 | PRIMARY AIR FLOW | FT | FLOW TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT409 |  | BB1TT409 | <IO NOT ASSIGNED> | Primary air fan motor bearing temperature 2 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT401 | MEAS_ANA_SRS | Secondary air pressure | BB1PT401 | SECONDARY AIR PRESSURE |  |  | BB1PT401 | SECONDARY AIR PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT402 |  | BB1TT402 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 1 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1FT401 | MEAS_ANA_SRS | Secondary air flow | BB1FT401 | SECONDARY AIR FLOW |  |  | BB1FT401 | SECONDARY AIR FLOW | FT | FLOW TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT403 |  | BB1TT403 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 2 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT417 | MEAS_ANA_SRS | Bed temperature 3 | BB1TT417 | BED TEMPERATURE 3 |  |  | BB1TT417 | BED TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT421 |  | BB1TT421 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 3 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT413 | MEAS_ANA_SRS | Bed temperature 1 | BB1TT413 | BED TEMPERATURE 1 |  |  | BB1TT413 | BED TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT407 |  | BB1TT407 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 2 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT414 | MEAS_ANA_SRS | Bed temperature 2 | BB1TT414 | BED TEMPERATURE 2 |  |  | BB1TT414 | BED TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT422 |  | BB1TT422 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 3 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT405 | MEAS_ANA_SRS | Boiler upper part pressure 2 | BB1PT405 | BOILER UPPER PART | PRESSURE 2 |  | BB1PT405 | BOILER UPPER PART PRESSURE 2 | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT409 |  | BB1PT409 | <IO NOT ASSIGNED> | Secondary air pressure outer front wall | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  | SECONDARY AIR PRESSURE OUTER FRONT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1QT550 | MEAS_ANA_SRS | Fluegas oxygen measurement 1 | BB1QT550 | FLUEGAS OXYGEN | MEASUREMENT 1 |  | BB1QT550 | FLUEGAS OXYGEN MEASUREMENT 1 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT411 |  | BB1PT411 | <IO NOT ASSIGNED> | Secondary air pressure outer back wall | SECONDARY AIR PRESSURE | OUTER BACK WALL |  | SECONDARY AIR PRESSURE OUTER BACK WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1FT550 | MEAS_ANA_SRS | Recirculation gas flow | BB1FT550 | RECIRCULATION GAS FLOW |  |  | BB1FT550 | RECIRCULATION GAS FLOW | FT | FLOW TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT407 |  | BB1PT407 | <IO NOT ASSIGNED> | Tertiary air pressure right wall | TERTIARY AIR PRESSURE | RIGHT WALL |  | TERTIARY AIR PRESSURE RIGHT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1QT551 | MEAS_ANA_SRS | Fluegas oxygen measurement 2 | BB1QT551 | FLUEGAS OXYGEN | MEASUREMENT 2 |  | BB1QT551 | FLUEGAS OXYGEN MEASUREMENT 2 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT408 |  | BB1PT408 | <IO NOT ASSIGNED> | Tertiary air pressure left wall | TERTIARY AIR PRESSURE | LEFT WALL |  | TERTIARY AIR PRESSURE LEFT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT406 | MEAS_ANA_SRS | Boiler upper part pressure | BB1PT406 | BOILER UPPER PART | PRESSURE |  | BB1PT406 | BOILER UPPER PART PRESSURE | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT650 |  | BB1TT650 | <IO NOT ASSIGNED> | Scraper conveyor 1 temperature measurement | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  | SCRAPER CONVEYOR 1 TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LS700 | MEAS_BIN | Chemical tank 1 level switch | BB1LS700 | CHEMICAL TANK 1 | LEVEL SWITCH |  | BB1LS700 | CHEMICAL TANK 1 LEVEL SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT611 |  | BB1LT611 | <IO NOT ASSIGNED> | Unloading station 1 level | UNLOADING STATION 1 LEVEL |  |  | UNLOADING STATION 1 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1LS701 | MEAS_BIN | Chemical tank 2 level switch | BB1LS701 | CHEMICAL TANK 2 | LEVEL SWITCH |  | BB1LS701 | CHEMICAL TANK 2 LEVEL SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT612 |  | BB1LT612 | <IO NOT ASSIGNED> | Unloading station 3 level | UNLOADING STATION 3 LEVEL |  |  | UNLOADING STATION 3 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS004 | MEAS_BIN | Feed water pump suction side shut-off valve limit switch | BB1GS004 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | BB1GS004 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT613 |  | BB1LT613 | <IO NOT ASSIGNED> | Unloading station 2 level | UNLOADING STATION 2 LEVEL |  |  | UNLOADING STATION 2 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS003 | MEAS_BIN | Feed water pump suction side shut-off valve limit switch | BB1GS003 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | BB1GS003 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT650 |  | BB1LT650 | <IO NOT ASSIGNED> | Fuel silo level radar 1 | FUEL SILO LEVEL RADAR 1 |  |  | FUEL SILO LEVEL RADAR 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS001 | MEAS_BIN | Feed water pump suction side shut-off valve limit switch | BB1GS001 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | BB1GS001 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT651 |  | BB1LT651 | <IO NOT ASSIGNED> | Fuel silo level radar 2 | FUEL SILO LEVEL RADAR 2 |  |  | FUEL SILO LEVEL RADAR 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS002 | MEAS_BIN | Feed water pump suction side shut-off valve limit switch | BB1GS002 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | BB1GS002 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT652 |  | BB1LT652 | <IO NOT ASSIGNED> | Fuel pocket level | FUEL POCKET LEVEL |  |  | FUEL POCKET LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS005 | MEAS_BIN | FW tank overflow On-Off valve position | BB1GS005 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | BB1GS005 | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT652 |  | BB1TT652 | <IO NOT ASSIGNED> | Fuel silo temperature measurement | FUEL SILO TEMPERATURE | MEASUREMENT |  | FUEL SILO TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS006 | MEAS_BIN | FW tank overflow On-Off valve position | BB1GS006 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | BB1GS006 | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT653 |  | BB1TT653 | <IO NOT ASSIGNED> | Fuel pocket temperature | FUEL POCKET TEMPERATURE |  |  | FUEL POCKET TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS007 | MEAS_BIN | Feedwater pump 1 on-off valve limit switch open | BB1GS007 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | BB1GS007 | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT552 |  | BB1PT552 | <IO NOT ASSIGNED> | ESP inlet pressure transmitter | ESP INLET PRESSURE | TRANSMITTER |  | ESP INLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS008 | MEAS_BIN | Feedwater pump 1 on-off valve limit switch close | BB1GS008 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | BB1GS008 | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT553 |  | BB1PT553 | <IO NOT ASSIGNED> | ESP outlet pressure transmitter | ESP OUTLET PRESSURE | TRANSMITTER |  | ESP OUTLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS009 | MEAS_BIN | Feed water pump 2 on-off valve limit switch open | BB1GS009 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | BB1GS009 | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT554 |  | BB1QT554 | <IO NOT ASSIGNED> | Opacity after ESP | OPACITY AFTER ESP |  |  | OPACITY AFTER ESP | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1GS010 | MEAS_BIN | Feed water pump 2 on-off valve limit switch close | BB1GS010 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | BB1GS010 | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT553 |  | BB1TT553 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 1 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS011 | MEAS_BIN | Boiler bottom blow down on-off valve limit switch open | BB1GS011 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | BB1GS011 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT557 |  | BB1TT557 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 2 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS012 | MEAS_BIN | Boiler bottom blow down on-off valve limit switch close | BB1GS012 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | BB1GS012 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT558 |  | BB1TT558 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 3 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS221 | MEAS_BIN | Main steam valve by-pass open limit switch | BB1GS221 | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | BB1GS221 | MAIN STEAM VALVE BY-PASS OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT554 |  | BB1TT554 | <IO NOT ASSIGNED> | Flue gas fan bearing temperature | FLUE GAS FAN BEARING | TEMPERATURE |  | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS222 | MEAS_BIN | Main steam valve by-pass close limit switch | BB1GS222 | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | BB1GS222 | MAIN STEAM VALVE BY-PASS CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT555 |  | BB1TT555 | <IO NOT ASSIGNED> | Flue gas fan bearing temperature | FLUE GAS FAN BEARING | TEMPERATURE |  | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS223 | MEAS_BIN | Main steam line valve open limit switch | BB1GS223 | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | BB1GS223 | MAIN STEAM LINE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT556 |  | BB1TT556 | <IO NOT ASSIGNED> | Flue gas temperature before stack | FLUE GAS TEMPERATURE | BEFORE STACK |  | FLUE GAS TEMPERATURE BEFORE STACK | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS224 | MEAS_BIN | Main steam line valve close limit switch | BB1GS224 | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | BB1GS224 | MAIN STEAM LINE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT850 |  | BB1TT850 | <IO NOT ASSIGNED> | ESP Ash hopper 1 temperature | ESP ASH HOPPER 1 | TEMPERATURE |  | ESP ASH HOPPER 1 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS225 | MEAS_BIN | Start-up line ON-OFF valve open limit switch | BB1GS225 | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | BB1GS225 | START-UP LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT851 |  | BB1TT851 | <IO NOT ASSIGNED> | ESP Ash hopper 2 temperature | ESP ASH HOPPER 2 | TEMPERATURE |  | ESP ASH HOPPER 2 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS226 | MEAS_BIN | Start-up line ON-OFF valve close limit switch | BB1GS226 | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | BB1GS226 | START-UP LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TS501 |  | BB1TS501 | <IO NOT ASSIGNED> | ESP Insulator 1 temperature | ESP INSULATOR 1 | TEMPERATURE |  | ESP INSULATOR 1 TEMPERATURE | TS | TEMPERATURE SWITCH | AI | MEAS_ANA |  | BB1GS200 | MEAS_BIN | Sootblower 1 IN limit switch | BB1GS200 | SOOTBLOWER 1 IN | LIMIT SWITCH |  | BB1GS200 | SOOTBLOWER 1 IN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TS508 |  | BB1TS508 | <IO NOT ASSIGNED> | ESP Insulator 2 temperature | ESP INSULATOR 2 | TEMPERATURE |  | ESP INSULATOR 2 TEMPERATURE | TS | TEMPERATURE SWITCH | AI | MEAS_ANA |  | BB1GS201 | MEAS_BIN | Sootblower 1 OUT limit switch | BB1GS201 | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | BB1GS201 | SOOTBLOWER 1 OUT LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT552 |  | BB1TT552 | <IO NOT ASSIGNED> | Flue gas temperature before ESP | FLUE GAS TEMPERATURE | BEFORE ESP |  | FLUE GAS TEMPERATURE BEFORE ESP | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS203 | MEAS_BIN | Sootblower 2 OUT limit switch | BB1GS203 | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | BB1GS203 | SOOTBLOWER 2 OUT LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT800 |  | BB1LT800 | <IO NOT ASSIGNED> | Recycled bed material hopper level switch | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  | RECYCLED BED MATERIAL HOPPER LEVEL SWITCH | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS204 | MEAS_BIN | Sootblower 2 IN limit switch | BB1GS204 | SOOTBLOWER 2 IN | LIMIT SWITCH |  | BB1GS204 | SOOTBLOWER 2 IN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT802 |  | BB1LT802 | <IO NOT ASSIGNED> | Sand silo level measurement | SAND SILO LEVEL | MEASUREMENT |  | SAND SILO LEVEL MEASUREMENT | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS205 | MEAS_BIN | Sootblower 3 OUT limit switch | BB1GS205 | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | BB1GS205 | SOOTBLOWER 3 OUT LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT009 |  | BB1PT009 | <IO NOT ASSIGNED> | Cooling water pressure before pump | COOLING WATER PRESSURE | BEFORE PUMP |  | COOLING WATER PRESSURE BEFORE PUMP | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS206 | MEAS_BIN | Sootblower 3 IN limit switch | BB1GS206 | SOOTBLOWER 3 IN | LIMIT SWITCH |  | BB1GS206 | SOOTBLOWER 3 IN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT031 |  | BB1TT031 | <IO NOT ASSIGNED> | Cooling water temperatureafter bottom ash conveyor | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  | COOLING WATER TEMPERATURE AFTER BOTTOM ASH CONVEYOR | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS207 | MEAS_BIN | Sootblower 5 OUT limit switch | BB1GS207 | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | BB1GS207 | SOOTBLOWER 5 OUT LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT478 |  | BB1PT478 | <IO NOT ASSIGNED> | Instrument air pressure | INSTRUMENT AIR PRESSURE |  |  | INSTRUMENT AIR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS208 | MEAS_BIN | Sootblower 5 IN limit switch | BB1GS208 | SOOTBLOWER 5 IN | LIMIT SWITCH |  | BB1GS208 | SOOTBLOWER 5 IN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT402 |  | BB1PT402 | <IO NOT ASSIGNED> | Instrument air pressure after dryer | INSTRUMENT AIR PRESSURE | AFTER DRYER |  | INSTRUMENT AIR PRESSURE AFTER DRYER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS209 | MEAS_BIN | Sootblower 6 OUT limit switch | BB1GS209 | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | BB1GS209 | SOOTBLOWER 6 OUT LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT430 |  | BB1TT430 | <IO NOT ASSIGNED> | Instrument air tank temperature | INSTRUMENT AIR TANK | TEMPERATURE |  | INSTRUMENT AIR TANK TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS210 | MEAS_BIN | Sootblower 6 IN limit switch | BB1GS210 | SOOTBLOWER 6 IN | LIMIT SWITCH |  | BB1GS210 | SOOTBLOWER 6 IN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT401 |  | BB1TT401 | <IO NOT ASSIGNED> | Boiler room upper part temperature | BOILER ROOM UPPER PART | TEMPERATURE |  | BOILER ROOM UPPER PART TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS211 | MEAS_BIN | Sootblower 7 OUT limit switch | BB1GS211 | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | BB1GS211 | SOOTBLOWER 7 OUT LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT101 |  | BB1LT101 | <IO NOT ASSIGNED> | Steam drum level 1 | STEAM DRUM LEVEL 1 |  |  | STEAM DRUM LEVEL 1 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS212 | MEAS_BIN | Sootblower 7 IN limit switch | BB1GS212 | SOOTBLOWER 7 IN | LIMIT SWITCH |  | BB1GS212 | SOOTBLOWER 7 IN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT203 |  | BB1PT203 | <IO NOT ASSIGNED> | Steam drum pressure 2 | STEAM DRUM PRESSURE 2 |  |  | STEAM DRUM PRESSURE 2 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS213 | MEAS_BIN | Sootblower 8 OUT limit switch | BB1GS213 | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | BB1GS213 | SOOTBLOWER 8 OUT LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT102 |  | BB1LT102 | <IO NOT ASSIGNED> | Steam drum level 2 | STEAM DRUM LEVEL 2 |  |  | STEAM DRUM LEVEL 2 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS214 | MEAS_BIN | Sootblower 8 IN limit switch | BB1GS214 | SOOTBLOWER 8 IN | LIMIT SWITCH |  | BB1GS214 | SOOTBLOWER 8 IN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT201 |  | BB1PT201 | <IO NOT ASSIGNED> | Steam drum pressure 1 | STEAM DRUM PRESSURE 1 |  |  | STEAM DRUM PRESSURE 1 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS227 | MEAS_BIN | Sootblowing line on-off valve open limit switch | BB1GS227 | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | BB1GS227 | SOOTBLOWING LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LT103 |  | BB1LT103 | <IO NOT ASSIGNED> | Steam drum level 3 | STEAM DRUM LEVEL 3 |  |  | STEAM DRUM LEVEL 3 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS228 | MEAS_BIN | Sootblowing line on-off valve close limit switch | BB1GS228 | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | BB1GS228 | SOOTBLOWING LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT205 |  | BB1PT205 | <IO NOT ASSIGNED> | Steam outlet pressure from accumulator | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  | STEAM OUTLET PRESSURE FROM ACCUMULATOR | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS231 | MEAS_BIN | Steam accumulator pressure control valve open limit switch | BB1GS231 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | BB1GS231 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT400 |  | BB1PT400 | <IO NOT ASSIGNED> | Primary air pressure | PRIMARY AIR PRESSURE |  |  | PRIMARY AIR PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS230 | MEAS_BIN | Steam accumulator pressure control valve close limit switch | BB1GS230 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | BB1GS230 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT418 |  | BB1TT418 | <IO NOT ASSIGNED> | Bed temperature 4 | BED TEMPERATURE 4 |  |  | BED TEMPERATURE 4 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS233 | MEAS_BIN | Steam pressure reduction valve open limit switch | BB1GS233 | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | BB1GS233 | STEAM PRESSURE REDUCTION VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT404 |  | BB1PT404 | <IO NOT ASSIGNED> | Boiler upper part pressure 1 | BOILER UPPER PART | PRESSURE 1 |  | BOILER UPPER PART PRESSURE 1 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS232 | MEAS_BIN | Steam pressure reduction valve close limit switch | BB1GS232 | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | BB1GS232 | STEAM PRESSURE REDUCTION VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1FT400 |  | BB1FT400 | <IO NOT ASSIGNED> | Primary air flow | PRIMARY AIR FLOW |  |  | PRIMARY AIR FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS217 | MEAS_BIN | Main steam line accumulator bypass on-offvalve open limit switch | BB1GS217 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | BB1GS217 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT401 |  | BB1PT401 | <IO NOT ASSIGNED> | Secondary air pressure | SECONDARY AIR PRESSURE |  |  | SECONDARY AIR PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS218 | MEAS_BIN | Main steam line accumulator bypass on-offvalve close limit switch | BB1GS218 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | BB1GS218 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1FT401 |  | BB1FT401 | <IO NOT ASSIGNED> | Secondary air flow | SECONDARY AIR FLOW |  |  | SECONDARY AIR FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS219 | MEAS_BIN | Steam accumulator ON-OFF isolating valve open limit switch | BB1GS219 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | BB1GS219 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT417 |  | BB1TT417 | <IO NOT ASSIGNED> | Bed temperature 3 | BED TEMPERATURE 3 |  |  | BED TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS220 | MEAS_BIN | Steam accumulator ON-OFF isolating valve close limit switch | BB1GS220 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | BB1GS220 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT413 |  | BB1TT413 | <IO NOT ASSIGNED> | Bed temperature 1 | BED TEMPERATURE 1 |  |  | BED TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS217 | MEAS_BIN | Steam accumulator by-passvalve open limit switch | BB1GS217 | STEAM ACCUMULATOR BY-PASS | VALVE OPEN LIMIT SWITCH |  | BB1GS217 | STEAM ACCUMULATOR BY-PASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TT414 |  | BB1TT414 | <IO NOT ASSIGNED> | Bed temperature 2 | BED TEMPERATURE 2 |  |  | BED TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS218 | MEAS_BIN | Steam accumulator by-passvalve close limit switch | BB1GS218 | STEAM ACCUMULATOR BY-PASS | VALVE CLOSE LIMIT SWITCH |  | BB1GS218 | STEAM ACCUMULATOR BY-PASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT405 |  | BB1PT405 | <IO NOT ASSIGNED> | Boiler upper part pressure 2 | BOILER UPPER PART | PRESSURE 2 |  | BOILER UPPER PART PRESSURE 2 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS220 | MEAS_BIN | Steam accumulator ON-OFF valve close limit switch | BB1GS220 | STEAM ACCUMULATOR ON-OFF | VALVE CLOSE LIMIT SWITCH |  | BB1GS220 | STEAM ACCUMULATOR ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT550 |  | BB1QT550 | <IO NOT ASSIGNED> | Fluegas oxygen measurement 1 | FLUEGAS OXYGEN | MEASUREMENT 1 |  | FLUEGAS OXYGEN MEASUREMENT 1 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS219 | MEAS_BIN | Steam accumulator ON-OFF valve open limit switch | BB1GS219 | STEAM ACCUMULATOR ON-OFF | VALVE OPEN LIMIT SWITCH |  | BB1GS219 | STEAM ACCUMULATOR ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1FT550 |  | BB1FT550 | <IO NOT ASSIGNED> | Recirculation gas flow | RECIRCULATION GAS FLOW |  |  | RECIRCULATION GAS FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS215 | MEAS_BIN | Primary air preheater on-off valve open limit switch | BB1GS215 | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | BB1GS215 | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1QT551 |  | BB1QT551 | <IO NOT ASSIGNED> | Fluegas oxygen measurement 2 | FLUEGAS OXYGEN | MEASUREMENT 2 |  | FLUEGAS OXYGEN MEASUREMENT 2 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS216 | MEAS_BIN | Primary air preheater on-off valve close limit switch | BB1GS216 | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | BB1GS216 | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT406 |  | BB1PT406 | <IO NOT ASSIGNED> | Boiler upper part pressure | BOILER UPPER PART | PRESSURE |  | BOILER UPPER PART PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS621 | MEAS_BIN | Unloading station 3, block 3, feeder 3, out | BB1GS621 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | BB1GS621 | UNLOADING STATION 3, BLOCK 3, FEEDER 3, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS700 |  | BB1LS700 | <IO NOT ASSIGNED> | Chemical tank 1 level switch | CHEMICAL TANK 1 | LEVEL SWITCH |  | CHEMICAL TANK 1 LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS611 | MEAS_BIN | Unloading station 2, block 2, feeder 2, out | BB1GS611 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | BB1GS611 | UNLOADING STATION 2, BLOCK 2, FEEDER 2, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS701 |  | BB1LS701 | <IO NOT ASSIGNED> | Chemical tank 2 level switch | CHEMICAL TANK 2 | LEVEL SWITCH |  | CHEMICAL TANK 2 LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS606 | MEAS_BIN | Unloading station 1, block 1, feeder 4, in | BB1GS606 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | BB1GS606 | UNLOADING STATION 1, BLOCK 1, FEEDER 4, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS004 |  | BB1GS004 | <IO NOT ASSIGNED> | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS614 | MEAS_BIN | Unloading station 2, block 2, feeder 4, in | BB1GS614 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | BB1GS614 | UNLOADING STATION 2, BLOCK 2, FEEDER 4, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS003 |  | BB1GS003 | <IO NOT ASSIGNED> | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS619 | MEAS_BIN | Unloading station 3, block 3, feeder 2, out | BB1GS619 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | BB1GS619 | UNLOADING STATION 3, BLOCK 3, FEEDER 2, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS001 |  | BB1GS001 | <IO NOT ASSIGNED> | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS651 | MEAS_BIN | Disc screen by-pass damper limit switch to screen | BB1GS651 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | BB1GS651 | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH TO SCREEN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS002 |  | BB1GS002 | <IO NOT ASSIGNED> | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS602 | MEAS_BIN | Hydraulics unit 1, block 3, pressure switch | BB1PS602 | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | BB1PS602 | HYDRAULICS UNIT 1, BLOCK 3, PRESSURE SWITCH | PS | PRESSURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS005 |  | BB1GS005 | <IO NOT ASSIGNED> | FW tank overflow On-Off valve position | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS615 | MEAS_BIN | Unloading station 2, block 2, feeder 4, out | BB1GS615 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | BB1GS615 | UNLOADING STATION 2, BLOCK 2, FEEDER 4, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS006 |  | BB1GS006 | <IO NOT ASSIGNED> | FW tank overflow On-Off valve position | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS623 | MEAS_BIN | Unloading station 3, block 3, feeder 4, out | BB1GS623 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | BB1GS623 | UNLOADING STATION 3, BLOCK 3, FEEDER 4, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS007 |  | BB1GS007 | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve limit switch open | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST651 | MEAS_BIN | Scraper conveyor 2, rotation guard | BB1ST651 | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | BB1ST651 | SCRAPER CONVEYOR 2, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS008 |  | BB1GS008 | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve limit switch close | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS603 | MEAS_BIN | Unloading station 1, block 1, feeder 2, out | BB1GS603 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | BB1GS603 | UNLOADING STATION 1, BLOCK 1, FEEDER 2, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS009 |  | BB1GS009 | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve limit switch open | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS601 | MEAS_BIN | Hydraulics unit 1, block 2, pressure switch | BB1PS601 | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | BB1PS601 | HYDRAULICS UNIT 1, BLOCK 2, PRESSURE SWITCH | PS | PRESSURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS010 |  | BB1GS010 | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve limit switch close | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS650 | MEAS_BIN | Disc screen by-pass damper limit switch by-pass pos. | BB1GS650 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | BB1GS650 | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH BY-PASS POS. | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS011 |  | BB1GS011 | <IO NOT ASSIGNED> | Boiler bottom blow down on-off valve limit switch open | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS622 | MEAS_BIN | Unloading station 3, block 3, feeder 4, in | BB1GS622 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | BB1GS622 | UNLOADING STATION 3, BLOCK 3, FEEDER 4, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS012 |  | BB1GS012 | <IO NOT ASSIGNED> | Boiler bottom blow down on-off valve limit switch close | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS602 | MEAS_BIN | Unloading station 1, block 1, feeder 2, in | BB1GS602 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | BB1GS602 | UNLOADING STATION 1, BLOCK 1, FEEDER 2, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS221 |  | BB1GS221 | <IO NOT ASSIGNED> | Main steam valve by-pass open limit switch | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | MAIN STEAM VALVE BY-PASS OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS655 | MEAS_BIN | Scraper conveyor 2, turning point blockage guard | BB1LS655 | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | BB1LS655 | SCRAPER CONVEYOR 2, TURNING POINT BLOCKAGE GU ARD | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS222 |  | BB1GS222 | <IO NOT ASSIGNED> | Main steam valve by-pass close limit switch | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | MAIN STEAM VALVE BY-PASS CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS607 | MEAS_BIN | Unloading station 1, block 1, feeder 4, out | BB1GS607 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | BB1GS607 | UNLOADING STATION 1, BLOCK 1, FEEDER 4, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS223 |  | BB1GS223 | <IO NOT ASSIGNED> | Main steam line valve open limit switch | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | MAIN STEAM LINE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS605 | MEAS_BIN | Unloading station 1, block 1, feeder 3, out | BB1GS605 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | BB1GS605 | UNLOADING STATION 1, BLOCK 1, FEEDER 3, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS224 |  | BB1GS224 | <IO NOT ASSIGNED> | Main steam line valve close limit switch | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | MAIN STEAM LINE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS652 | MEAS_BIN | Unloading station 2, block 2, blockage guard | BB1LS652 | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | BB1LS652 | UNLOADING STATION 2, BLOCK 2, BLOCKAGE GUARD | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS225 |  | BB1GS225 | <IO NOT ASSIGNED> | Start-up line ON-OFF valve open limit switch | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | START-UP LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS601 | MEAS_BIN | Unloading station 1, block 1, feeder 1, out | BB1GS601 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | BB1GS601 | UNLOADING STATION 1, BLOCK 1, FEEDER 1, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS226 |  | BB1GS226 | <IO NOT ASSIGNED> | Start-up line ON-OFF valve close limit switch | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | START-UP LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS608 | MEAS_BIN | Hydraulics unit 1, low oil level alarm | BB1LS608 | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | BB1LS608 | HYDRAULICS UNIT 1, LOW OIL LEVEL ALARM | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS200 |  | BB1GS200 | <IO NOT ASSIGNED> | Sootblower 1 IN limit switch | SOOTBLOWER 1 IN | LIMIT SWITCH |  | SOOTBLOWER 1 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS656 | MEAS_BIN | Scraper conveyor 2, fuel silo side blockage guard | BB1LS656 | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | BB1LS656 | SCRAPER CONVEYOR 2, FUEL SILO SIDE BLOCKAGE GUARD | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS201 |  | BB1GS201 | <IO NOT ASSIGNED> | Sootblower 1 OUT limit switch | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | SOOTBLOWER 1 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS600 | MEAS_BIN | Hydraulics unit 1, leaking pool limit switch | BB1LS600 | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | BB1LS600 | HYDRAULICS UNIT 1, LEAKING POOL LIMIT SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS203 |  | BB1GS203 | <IO NOT ASSIGNED> | Sootblower 2 OUT limit switch | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | SOOTBLOWER 2 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS609 | MEAS_BIN | Unloading station 2, block 2, feeder 1, out | BB1GS609 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | BB1GS609 | UNLOADING STATION 2, BLOCK 2, FEEDER 1, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS204 |  | BB1GS204 | <IO NOT ASSIGNED> | Sootblower 2 IN limit switch | SOOTBLOWER 2 IN | LIMIT SWITCH |  | SOOTBLOWER 2 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS650 | MEAS_BIN | Scraper conveyor 1 bed height level switch | BB1LS650 | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | BB1LS650 | SCRAPER CONVEYOR 1 BED HEIGHT LEVEL SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS205 |  | BB1GS205 | <IO NOT ASSIGNED> | Sootblower 3 OUT limit switch | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | SOOTBLOWER 3 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS617 | MEAS_BIN | Unloading station 3, block 3, feeder 1, out | BB1GS617 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | BB1GS617 | UNLOADING STATION 3, BLOCK 3, FEEDER 1, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS206 |  | BB1GS206 | <IO NOT ASSIGNED> | Sootblower 3 IN limit switch | SOOTBLOWER 3 IN | LIMIT SWITCH |  | SOOTBLOWER 3 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS651 | MEAS_BIN | Unloading station 3, block 3, blockage guard | BB1LS651 | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | BB1LS651 | UNLOADING STATION 3, BLOCK 3, BLOCKAGE GUARD | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS207 |  | BB1GS207 | <IO NOT ASSIGNED> | Sootblower 5 OUT limit switch | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | SOOTBLOWER 5 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS612 | MEAS_BIN | Unloading station 2, block 2, feeder 3, in | BB1GS612 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | BB1GS612 | UNLOADING STATION 2, BLOCK 2, FEEDER 3, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS208 |  | BB1GS208 | <IO NOT ASSIGNED> | Sootblower 5 IN limit switch | SOOTBLOWER 5 IN | LIMIT SWITCH |  | SOOTBLOWER 5 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS654 | MEAS_BIN | Scraper conveyor 1, blockage guard | BB1LS654 | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | BB1LS654 | SCRAPER CONVEYOR 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS209 |  | BB1GS209 | <IO NOT ASSIGNED> | Sootblower 6 OUT limit switch | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | SOOTBLOWER 6 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS613 | MEAS_BIN | Unloading station 2, block 2, feeder 3, out | BB1GS613 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | BB1GS613 | UNLOADING STATION 2, BLOCK 2, FEEDER 3, OUT | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS210 |  | BB1GS210 | <IO NOT ASSIGNED> | Sootblower 6 IN limit switch | SOOTBLOWER 6 IN | LIMIT SWITCH |  | SOOTBLOWER 6 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS620 | MEAS_BIN | Unloading station 3, block 3, feeder 3, in | BB1GS620 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | BB1GS620 | UNLOADING STATION 3, BLOCK 3, FEEDER 3, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS211 |  | BB1GS211 | <IO NOT ASSIGNED> | Sootblower 7 OUT limit switch | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | SOOTBLOWER 7 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS618 | MEAS_BIN | Unloading station 3, block 3, feeder 2, in | BB1GS618 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | BB1GS618 | UNLOADING STATION 3, BLOCK 3, FEEDER 2, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS212 |  | BB1GS212 | <IO NOT ASSIGNED> | Sootblower 7 IN limit switch | SOOTBLOWER 7 IN | LIMIT SWITCH |  | SOOTBLOWER 7 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS600 | MEAS_BIN | Hydraulics unit 1, block 1, pressure switch | BB1PS600 | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | BB1PS600 | HYDRAULICS UNIT 1, BLOCK 1, PRESSURE SWITCH | PS | PRESSURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS213 |  | BB1GS213 | <IO NOT ASSIGNED> | Sootblower 8 OUT limit switch | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | SOOTBLOWER 8 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS608 | MEAS_BIN | Unloading station 2, block 2, feeder 1, in | BB1GS608 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | BB1GS608 | UNLOADING STATION 2, BLOCK 2, FEEDER 1, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS214 |  | BB1GS214 | <IO NOT ASSIGNED> | Sootblower 8 IN limit switch | SOOTBLOWER 8 IN | LIMIT SWITCH |  | SOOTBLOWER 8 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS604 | MEAS_BIN | Unloading station 1, block 1, feeder 3, in | BB1GS604 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | BB1GS604 | UNLOADING STATION 1, BLOCK 1, FEEDER 3, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS227 |  | BB1GS227 | <IO NOT ASSIGNED> | Sootblowing line on-off valve open limit switch | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | SOOTBLOWING LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS653 | MEAS_BIN | Unloading station 1, block 1, blockage guard | BB1LS653 | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | BB1LS653 | UNLOADING STATION 1, BLOCK 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS228 |  | BB1GS228 | <IO NOT ASSIGNED> | Sootblowing line on-off valve close limit switch | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | SOOTBLOWING LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS616 | MEAS_BIN | Unloading station 3, block 3, feeder 1, in | BB1GS616 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | BB1GS616 | UNLOADING STATION 3, BLOCK 3, FEEDER 1, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS231 |  | BB1GS231 | <IO NOT ASSIGNED> | Steam accumulator pressure control valve open limit switch | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS600 | MEAS_BIN | Unloading station 1, block 1, feeder 1, in | BB1GS600 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | BB1GS600 | UNLOADING STATION 1, BLOCK 1, FEEDER 1, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS230 |  | BB1GS230 | <IO NOT ASSIGNED> | Steam accumulator pressure control valve close limit switch | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST650 | MEAS_BIN | Scraper conveyor 1, rotation guard | BB1ST650 | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | BB1ST650 | SCRAPER CONVEYOR 1, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS233 |  | BB1GS233 | <IO NOT ASSIGNED> | Steam pressure reduction valve open limit switch | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | STEAM PRESSURE REDUCTION VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS610 | MEAS_BIN | Unloading station 2, block 2, feeder 2, in | BB1GS610 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | BB1GS610 | UNLOADING STATION 2, BLOCK 2, FEEDER 2, IN | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS232 |  | BB1GS232 | <IO NOT ASSIGNED> | Steam pressure reduction valve close limit switch | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | STEAM PRESSURE REDUCTION VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST675 | MEAS_BIN | Leveling roller 3 speed switch | BB1ST675 | LEVELING ROLLER 3 | SPEED SWITCH |  | BB1ST675 | LEVELING ROLLER 3 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS217 |  | BB1GS217 | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-offvalve open limit switch | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS608 | MEAS_BIN | High temperature switch hydraulic oil | BB1TS608 | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | BB1TS608 | HIGH TEMPERATURE SWITCH HYDRAULIC OIL | TS | TEMPERATURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS218 |  | BB1GS218 | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-offvalve close limit switch | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST673 | MEAS_BIN | Leveling roller 1 speed switch | BB1ST673 | LEVELING ROLLER 1 | SPEED SWITCH |  | BB1ST673 | LEVELING ROLLER 1 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS219 |  | BB1GS219 | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve open limit switch | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS600 | MEAS_BIN | Hydraulics unit, thermostat for heater | BB1TS600 | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | BB1TS600 | HYDRAULICS UNIT, THERMOSTAT FOR HEATER | TS | TEMPERATURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS220 |  | BB1GS220 | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve close limit switch | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST674 | MEAS_BIN | Leveling roller 2 speed switch | BB1ST674 | LEVELING ROLLER 2 | SPEED SWITCH |  | BB1ST674 | LEVELING ROLLER 2 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS217 |  | BB1GS217 | <IO NOT ASSIGNED> | Steam accumulator by-passvalve open limit switch | STEAM ACCUMULATOR BY-PASS | VALVE OPEN LIMIT SWITCH |  | STEAM ACCUMULATOR BY-PASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS605 | MEAS_BIN | Hydraulic oil return block 3 filter pressure switch | BB1PS605 | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | BB1PS605 | HYDRAULIC OIL RETURN BLOCK 3 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS218 |  | BB1GS218 | <IO NOT ASSIGNED> | Steam accumulator by-passvalve close limit switch | STEAM ACCUMULATOR BY-PASS | VALVE CLOSE LIMIT SWITCH |  | STEAM ACCUMULATOR BY-PASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS603 | MEAS_BIN | Hydraulic oil return block 1 filter pressure switch | BB1PS603 | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | BB1PS603 | HYDRAULIC OIL RETURN BLOCK 1 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS220 |  | BB1GS220 | <IO NOT ASSIGNED> | Steam accumulator ON-OFF valve close limit switch | STEAM ACCUMULATOR ON-OFF | VALVE CLOSE LIMIT SWITCH |  | STEAM ACCUMULATOR ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS604 | MEAS_BIN | Hydraulic oil return block 2 filter pressure switch | BB1PS604 | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | BB1PS604 | HYDRAULIC OIL RETURN BLOCK 2 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS219 |  | BB1GS219 | <IO NOT ASSIGNED> | Steam accumulator ON-OFF valve open limit switch | STEAM ACCUMULATOR ON-OFF | VALVE OPEN LIMIT SWITCH |  | STEAM ACCUMULATOR ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST654 | MEAS_BIN | Belt magnet rotation guard | BB1ST654 | BELT MAGNET | ROTATION GUARD |  | BB1ST654 | BELT MAGNET ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS215 |  | BB1GS215 | <IO NOT ASSIGNED> | Primary air preheater on-off valve open limit switch | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS661 | MEAS_BIN | Belt magnet deviation detector 1 | BB1GS661 | BELT MAGNET | DEVIATION DETECTOR 1 |  | BB1GS661 | BELT MAGNET DEVIATION DETECTOR 1 | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS216 |  | BB1GS216 | <IO NOT ASSIGNED> | Primary air preheater on-off valve close limit switch | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS662 | MEAS_BIN | Belt magnet deviation detector 2 | BB1GS662 | BELT MAGNET | DEVIATION DETECTOR 2 |  | BB1GS662 | BELT MAGNET DEVIATION DETECTOR 2 | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS621 |  | BB1GS621 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 3, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST652 | MEAS_BIN | Belt conveyor rotation guard | BB1ST652 | BELT CONVEYOR | ROTATION GUARD |  | BB1ST652 | BELT CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS611 |  | BB1GS611 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 2, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS659 | MEAS_BIN | Belt conveyor deviation detector 1 | BB1GS659 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | BB1GS659 | BELT CONVEYOR DEVIATION DETECTOR 1 | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS606 |  | BB1GS606 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 4, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS660 | MEAS_BIN | Belt conveyor deviation detector 2 | BB1GS660 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | BB1GS660 | BELT CONVEYOR DEVIATION DETECTOR 2 | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS614 |  | BB1GS614 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 4, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS663 | MEAS_BIN | Belt conveyor oversize detector | BB1GS663 | BELT CONVEYOR | OVERSIZE DETECTOR |  | BB1GS663 | BELT CONVEYOR OVERSIZE DETECTOR | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS619 |  | BB1GS619 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 2, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST656 | MEAS_BIN | Disc screen drive 1 rotation guard | BB1ST656 | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | BB1ST656 | DISC SCREEN DRIVE 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS651 |  | BB1GS651 | <IO NOT ASSIGNED> | Disc screen by-pass damper limit switch to screen | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH TO SCREEN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST657 | MEAS_BIN | Disc screen drive 2 rotation guard | BB1ST657 | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | BB1ST657 | DISC SCREEN DRIVE 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PS602 |  | BB1PS602 | <IO NOT ASSIGNED> | Hydraulics unit 1, block 3, pressure switch | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 3, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1GS652 | MEAS_BIN | Explosion hatch limit switch 1 | BB1GS652 | EXPLOSION HATCH | LIMIT SWITCH 1 |  | BB1GS652 | EXPLOSION HATCH LIMIT SWITCH 1 | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS615 |  | BB1GS615 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 4, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS653 | MEAS_BIN | Explosion hatch limit switch 2 | BB1GS653 | EXPLOSION HATCH | LIMIT SWITCH 2 |  | BB1GS653 | EXPLOSION HATCH LIMIT SWITCH 2 | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS623 |  | BB1GS623 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 4, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS654 | MEAS_BIN | Explosion hatch limit switch 3 | BB1GS654 | EXPLOSION HATCH | LIMIT SWITCH 3 |  | BB1GS654 | EXPLOSION HATCH LIMIT SWITCH 3 | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST651 |  | BB1ST651 | <IO NOT ASSIGNED> | Scraper conveyor 2, rotation guard | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | SCRAPER CONVEYOR 2, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS655 | MEAS_BIN | Explosion hatch limit switch 4 | BB1GS655 | EXPLOSION HATCH | LIMIT SWITCH 4 |  | BB1GS655 | EXPLOSION HATCH LIMIT SWITCH 4 | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS603 |  | BB1GS603 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 2, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS657 | MEAS_BIN | Fuel silo discharge screw blockage switch | BB1LS657 | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | BB1LS657 | FUEL SILO DISCHARGE SCREW BLOCKAGE SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PS601 |  | BB1PS601 | <IO NOT ASSIGNED> | Hydraulics unit 1, block 2, pressure switch | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 2, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1LS658 | MEAS_BIN | Fuel silo cross conveyor blockage switch | BB1LS658 | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | BB1LS658 | FUEL SILO CROSS CONVEYOR BLOCKAGE SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS650 |  | BB1GS650 | <IO NOT ASSIGNED> | Disc screen by-pass damper limit switch by-pass pos. | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH BY-PASS POS. | GS | GATE SWITCH | DI | MEAS_BIN |  | <004> | #N/A | Fuel silo cross conveyor explosion hatch limit switch | <004> | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | <004> | FUEL SILO CROSS CONVEYOR EXPLOSION HATCH LIMIT SWITCH | 4> | #N/A | #N/A | #N/A |  | #N/A |  |  |  |  | #N/A
BB1GS622 |  | BB1GS622 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 4, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS659 | MEAS_BIN | Fuel feeding screw 1 blockage switch | BB1LS659 | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | BB1LS659 | FUEL FEEDING SCREW 1 BLOCKAGE SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS602 |  | BB1GS602 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 2, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS660 | MEAS_BIN | Fuel feeding screw 2 blockage switch | BB1LS660 | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | BB1LS660 | FUEL FEEDING SCREW 2 BLOCKAGE SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS655 |  | BB1LS655 | <IO NOT ASSIGNED> | Scraper conveyor 2, turning point blockage guard | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | SCRAPER CONVEYOR 2, TURNING POINT BLOCKAGE GU ARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1ST649 | MEAS_BIN | Fuel silo cross conveyor rotation guard | BB1ST649 | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | BB1ST649 | FUEL SILO CROSS CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS607 |  | BB1GS607 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 4, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST652 | MEAS_BIN | Rotating fuel spreader rotation guard | BB1ST652 | ROTATING FUEL SPREADER | ROTATION GUARD |  | BB1ST652 | ROTATING FUEL SPREADER ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS605 |  | BB1GS605 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 3, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST653 | MEAS_BIN | Fuel feeding screw 2 rotation guard | BB1ST653 | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | BB1ST653 | FUEL FEEDING SCREW 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS652 |  | BB1LS652 | <IO NOT ASSIGNED> | Unloading station 2, block 2, blockage guard | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | UNLOADING STATION 2, BLOCK 2, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1ST654 | MEAS_BIN | Fuel feeding rotary feeder 1 rotation guard | BB1ST654 | FUEL FEEDING ROTARY | FEEDER 1 ROTATION GUARD |  | BB1ST654 | FUEL FEEDING ROTARY FEEDER 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS601 |  | BB1GS601 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 1, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST655 | MEAS_BIN | Fuel feeding rotary feeder 2 rotation guard | BB1ST655 | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | BB1ST655 | FUEL FEEDING ROTARY FEEDER 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS608 |  | BB1LS608 | <IO NOT ASSIGNED> | Hydraulics unit 1, low oil level alarm | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | HYDRAULICS UNIT 1, LOW OIL LEVEL ALARM | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1ST659 | MEAS_BIN | Fuel feeding screw 1 rotation guard | BB1ST659 | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | BB1ST659 | FUEL FEEDING SCREW 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS656 |  | BB1LS656 | <IO NOT ASSIGNED> | Scraper conveyor 2, fuel silo side blockage guard | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | SCRAPER CONVEYOR 2, FUEL SILO SIDE BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS655 | MEAS_BIN | Slide gate valve open limit switch | BB1GS655 | SLIDE GATE VALVE OPEN | LIMIT SWITCH |  | BB1GS655 | SLIDE GATE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS600 |  | BB1LS600 | <IO NOT ASSIGNED> | Hydraulics unit 1, leaking pool limit switch | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | HYDRAULICS UNIT 1, LEAKING POOL LIMIT SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS656 | MEAS_BIN | Slide gate valve close limit switch | BB1GS656 | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | BB1GS656 | SLIDE GATE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS609 |  | BB1GS609 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 1, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS661 | MEAS_BIN | Lubrication alarm screw discharger | BB1LS661 | LUBRICATION ALARM | SCREW DISCHARGER |  | BB1LS661 | LUBRICATION ALARM SCREW DISCHARGER | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS650 |  | BB1LS650 | <IO NOT ASSIGNED> | Scraper conveyor 1 bed height level switch | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | SCRAPER CONVEYOR 1 BED HEIGHT LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS802 | MEAS_BIN | Bottom ash valve limit switch | BB1GS802 | BOTTOM ASH VALVE | LIMIT SWITCH |  | BB1GS802 | BOTTOM ASH VALVE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS617 |  | BB1GS617 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 1, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS803 | MEAS_BIN | Bottom ash dropping chuteclosing device limit switch | BB1GS803 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BB1GS803 | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS651 |  | BB1LS651 | <IO NOT ASSIGNED> | Unloading station 3, block 3, blockage guard | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | UNLOADING STATION 3, BLOCK 3, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1LS852 | MEAS_BIN | Fly ash container level switch | BB1LS852 | FLY ASH CONTAINER | LEVEL SWITCH |  | BB1LS852 | FLY ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS612 |  | BB1GS612 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 3, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST805 | MEAS_BIN | Heated ESP collection screw rotation guard | BB1ST805 | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  | BB1ST805 | HEATED ESP COLLECTION SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS654 |  | BB1LS654 | <IO NOT ASSIGNED> | Scraper conveyor 1, blockage guard | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | SCRAPER CONVEYOR 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1ST808 | MEAS_BIN | ESP hopper 2 screw rotation guard | BB1ST808 | ESP HOPPER 2 SCREW | ROTATION GUARD |  | BB1ST808 | ESP HOPPER 2 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS613 |  | BB1GS613 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 3, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST809 | MEAS_BIN | ESP hopper 1 screw rotation guard | BB1ST809 | ESP HOPPER 1 SCREW | ROTATION GUARD |  | BB1ST809 | ESP HOPPER 1 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS620 |  | BB1GS620 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 3, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST804 | MEAS_BIN | ESP Rotary valve rotation guard | BB1ST804 | ESP ROTARY VALVE | ROTATION GUARD |  | BB1ST804 | ESP ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS618 |  | BB1GS618 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 2, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS808 | MEAS_BIN | ESP Ash hopper 2 overheat thermostat | BB1TS808 | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  | BB1TS808 | ESP ASH HOPPER 2 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PS600 |  | BB1PS600 | <IO NOT ASSIGNED> | Hydraulics unit 1, block 1, pressure switch | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 1, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1TS809 | MEAS_BIN | ESP Ash hopper 1 overheat thermostat | BB1TS809 | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  | BB1TS809 | ESP ASH HOPPER 1 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS608 |  | BB1GS608 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 1, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS805 | MEAS_BIN | ESP collection screw heating thermostat | BB1TS805 | ESP COLLECTION SCREW | HEATING THERMOSTAT |  | BB1TS805 | ESP COLLECTION SCREW HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS604 |  | BB1GS604 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 3, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS804 | MEAS_BIN | ESP Rotary valve heating thermostat | BB1TS804 | ESP ROTARY VALVE | HEATING THERMOSTAT |  | BB1TS804 | ESP ROTARY VALVE HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS653 |  | BB1LS653 | <IO NOT ASSIGNED> | Unloading station 1, block 1, blockage guard | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | UNLOADING STATION 1, BLOCK 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS855 | MEAS_BIN | Bottom ash valve solenoid valve open limit switch | BB1GS855 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BB1GS855 | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS616 |  | BB1GS616 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 1, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS856 | MEAS_BIN | Bottom ash valve solenoid valve close limit switch | BB1GS856 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BB1GS856 | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS600 |  | BB1GS600 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 1, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS857 | MEAS_BIN | Bottom ash valve solenoid valve open limit switch | BB1GS857 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BB1GS857 | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST650 |  | BB1ST650 | <IO NOT ASSIGNED> | Scraper conveyor 1, rotation guard | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | SCRAPER CONVEYOR 1, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS858 | MEAS_BIN | Bottom ash valve solenoid valve close limit switch | BB1GS858 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BB1GS858 | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS610 |  | BB1GS610 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 2, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS850 | MEAS_BIN | Bottom ash sieve bypass valve close limit switch | BB1GS850 | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | BB1GS850 | BOTTOM ASH SIEVE BYPASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST675 |  | BB1ST675 | <IO NOT ASSIGNED> | Leveling roller 3 speed switch | LEVELING ROLLER 3 | SPEED SWITCH |  | LEVELING ROLLER 3 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS851 | MEAS_BIN | Bottom ash sieve bypass valve open limit switch | BB1GS851 | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | BB1GS851 | BOTTOM ASH SIEVE BYPASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TS608 |  | BB1TS608 | <IO NOT ASSIGNED> | High temperature switch hydraulic oil | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | HIGH TEMPERATURE SWITCH HYDRAULIC OIL | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1FS003 | MEAS_BIN | Bottom ash cooling flow switch | BB1FS003 | BOTTOM ASH COOLING | FLOW SWITCH |  | BB1FS003 | BOTTOM ASH COOLING FLOW SWITCH | FS | FLOW SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST673 |  | BB1ST673 | <IO NOT ASSIGNED> | Leveling roller 1 speed switch | LEVELING ROLLER 1 | SPEED SWITCH |  | LEVELING ROLLER 1 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS801 | MEAS_BIN | Sand filling valve position open limit switch | BB1GS801 | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | BB1GS801 | SAND FILLING VALVE POSITION OPEN LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TS600 |  | BB1TS600 | <IO NOT ASSIGNED> | Hydraulics unit, thermostat for heater | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | HYDRAULICS UNIT, THERMOSTAT FOR HEATER | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1GS800 | MEAS_BIN | Sand filling valve position close limit switch | BB1GS800 | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | BB1GS800 | SAND FILLING VALVE POSITION CLOSE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST674 |  | BB1ST674 | <IO NOT ASSIGNED> | Leveling roller 2 speed switch | LEVELING ROLLER 2 | SPEED SWITCH |  | LEVELING ROLLER 2 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS854 | MEAS_BIN | Bottom ash dropping chute limit switch | BB1GS854 | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | BB1GS854 | BOTTOM ASH DROPPING CHUTE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PS605 |  | BB1PS605 | <IO NOT ASSIGNED> | Hydraulic oil return block 3 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 3 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1GS853 | MEAS_BIN | Bottom ash dropping chute closing device limit switch | BB1GS853 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BB1GS853 | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PS603 |  | BB1PS603 | <IO NOT ASSIGNED> | Hydraulic oil return block 1 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 1 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1GS859 | MEAS_BIN | Bottom ash to container in place | BB1GS859 | BOTTOM ASH TO CONTAINER | IN PLACE |  | BB1GS859 | BOTTOM ASH TO CONTAINER IN PLACE | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PS604 |  | BB1PS604 | <IO NOT ASSIGNED> | Hydraulic oil return block 2 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 2 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1LS850 | MEAS_BIN | Bottom ash container level switch | BB1LS850 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BB1LS850 | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST654 |  | BB1ST654 | <IO NOT ASSIGNED> | Belt magnet rotation guard | BELT MAGNET | ROTATION GUARD |  | BELT MAGNET ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1LS851 | MEAS_BIN | Bottom ash container level switch | BB1LS851 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BB1LS851 | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS661 |  | BB1GS661 | <IO NOT ASSIGNED> | Belt magnet deviation detector 1 | BELT MAGNET | DEVIATION DETECTOR 1 |  | BELT MAGNET DEVIATION DETECTOR 1 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PT800 | MEAS_BIN | Recycled bed material damper pressure switch | BB1PT800 | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  | BB1PT800 | RECYCLED BED MATERIAL DAMPER PRESSURE SWITCH | PT | PRESSURE TRANSMITTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS662 |  | BB1GS662 | <IO NOT ASSIGNED> | Belt magnet deviation detector 2 | BELT MAGNET | DEVIATION DETECTOR 2 |  | BELT MAGNET DEVIATION DETECTOR 2 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST856 | MEAS_BIN | Purified sand screw conveyor rotation guard | BB1ST856 | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | BB1ST856 | PURIFIED SAND SCREW CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST652 |  | BB1ST652 | <IO NOT ASSIGNED> | Belt conveyor rotation guard | BELT CONVEYOR | ROTATION GUARD |  | BELT CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1ST850 | MEAS_BIN | Bottom ash conveyor rotation guard | BB1ST850 | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | BB1ST850 | BOTTOM ASH CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS659 |  | BB1GS659 | <IO NOT ASSIGNED> | Belt conveyor deviation detector 1 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | BELT CONVEYOR DEVIATION DETECTOR 1 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS852 | MEAS_BIN | Bottom ash conveyor blockage detector | BB1GS852 | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | BB1GS852 | BOTTOM ASH CONVEYOR BLOCKAGE DETECTOR | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS660 |  | BB1GS660 | <IO NOT ASSIGNED> | Belt conveyor deviation detector 2 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | BELT CONVEYOR DEVIATION DETECTOR 2 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST852 | MEAS_BIN | 2nd pass fly ash rotary valve rotation guard | BB1ST852 | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | BB1ST852 | 2ND PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS663 |  | BB1GS663 | <IO NOT ASSIGNED> | Belt conveyor oversize detector | BELT CONVEYOR | OVERSIZE DETECTOR |  | BELT CONVEYOR OVERSIZE DETECTOR | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST853 | MEAS_BIN | 3rd pass fly ash rotary valve rotation guard | BB1ST853 | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | BB1ST853 | 3RD PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST656 |  | BB1ST656 | <IO NOT ASSIGNED> | Disc screen drive 1 rotation guard | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | DISC SCREEN DRIVE 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS020 | MEAS_BIN | Emergency shower use switch | BB1GS020 | EMERGENCY SHOWER | USE SWITCH |  | BB1GS020 | EMERGENCY SHOWER USE SWITCH | GS | GATE SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST657 |  | BB1ST657 | <IO NOT ASSIGNED> | Disc screen drive 2 rotation guard | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | DISC SCREEN DRIVE 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1LS103 | MEAS_BIN_SRS | Steam drum level switch 1 | BB1LS103 | STEAM DRUM LEVEL SWITCH 1 |  |  | BB1LS103 | STEAM DRUM LEVEL SWITCH 1 | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS652 |  | BB1GS652 | <IO NOT ASSIGNED> | Explosion hatch limit switch 1 | EXPLOSION HATCH | LIMIT SWITCH 1 |  | EXPLOSION HATCH LIMIT SWITCH 1 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS104 | MEAS_BIN_SRS | Steam drum level switch 2 | BB1LS104 | STEAM DRUM LEVEL SWITCH 2 |  |  | BB1LS104 | STEAM DRUM LEVEL SWITCH 2 | LS | LEVEL SWITCH | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS653 |  | BB1GS653 | <IO NOT ASSIGNED> | Explosion hatch limit switch 2 | EXPLOSION HATCH | LIMIT SWITCH 2 |  | EXPLOSION HATCH LIMIT SWITCH 2 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS101 | MEAS_BIN_SRS | Boiler emergency shutdown switch 1 | BB1HS101 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  | BB1HS101 | BOILER EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS654 |  | BB1GS654 | <IO NOT ASSIGNED> | Explosion hatch limit switch 3 | EXPLOSION HATCH | LIMIT SWITCH 3 |  | EXPLOSION HATCH LIMIT SWITCH 3 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS103 | MEAS_BIN_SRS | Boiler emergency shutdown switch 3 | BB1HS103 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  | BB1HS103 | BOILER EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS655 |  | BB1GS655 | <IO NOT ASSIGNED> | Explosion hatch limit switch 4 | EXPLOSION HATCH | LIMIT SWITCH 4 |  | EXPLOSION HATCH LIMIT SWITCH 4 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS104 | MEAS_BIN_SRS | Boiler emergency shutdown switch 4 | BB1HS104 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  | BB1HS104 | BOILER EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS657 |  | BB1LS657 | <IO NOT ASSIGNED> | Fuel silo discharge screw blockage switch | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | FUEL SILO DISCHARGE SCREW BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1HS102 | MEAS_BIN_SRS | Boiler emergency shutdown switch 2 | BB1HS102 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  | BB1HS102 | BOILER EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS658 |  | BB1LS658 | <IO NOT ASSIGNED> | Fuel silo cross conveyor blockage switch | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | FUEL SILO CROSS CONVEYOR BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1HS105 | MEAS_BIN_SRS | Boiler emergency shutdown switch 5 | BB1HS105 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  | BB1HS105 | BOILER EMERGENCY SHUTDOWN SWITCH 5 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
<004> |  | <004> | <IO NOT ASSIGNED> | Fuel silo cross conveyor explosion hatch limit switch | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | FUEL SILO CROSS CONVEYOR EXPLOSION HATCH LIMIT SWITCH | 4> | #N/A | DI | #N/A |  | BB1HS106 | MEAS_BIN_SRS | Boiler emergency shutdown switch 6 | BB1HS106 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  | BB1HS106 | BOILER EMERGENCY SHUTDOWN SWITCH 6 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS659 |  | BB1LS659 | <IO NOT ASSIGNED> | Fuel feeding screw 1 blockage switch | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | FUEL FEEDING SCREW 1 BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1HS107 | MEAS_BIN_SRS | Boiler emergency shutdown switch 7 | BB1HS107 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  | BB1HS107 | BOILER EMERGENCY SHUTDOWN SWITCH 7 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS660 |  | BB1LS660 | <IO NOT ASSIGNED> | Fuel feeding screw 2 blockage switch | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | FUEL FEEDING SCREW 2 BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1HS108 | MEAS_BIN_SRS | Boiler emergency shutdown switch 8 | BB1HS108 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  | BB1HS108 | BOILER EMERGENCY SHUTDOWN SWITCH 8 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST649 |  | BB1ST649 | <IO NOT ASSIGNED> | Fuel silo cross conveyor rotation guard | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | FUEL SILO CROSS CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS109 | MEAS_BIN_SRS | Boiler emergency shutdown switch 9 | BB1HS109 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  | BB1HS109 | BOILER EMERGENCY SHUTDOWN SWITCH 9 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST652 |  | BB1ST652 | <IO NOT ASSIGNED> | Rotating fuel spreader rotation guard | ROTATING FUEL SPREADER | ROTATION GUARD |  | ROTATING FUEL SPREADER ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS110 | MEAS_BIN_SRS | Boiler emergency shutdown switch 10 | BB1HS110 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  | BB1HS110 | BOILER EMERGENCY SHUTDOWN SWITCH 10 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST653 |  | BB1ST653 | <IO NOT ASSIGNED> | Fuel feeding screw 2 rotation guard | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | FUEL FEEDING SCREW 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS111 | MEAS_BIN_SRS | Boiler emergency shutdown switch 11 | BB1HS111 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  | BB1HS111 | BOILER EMERGENCY SHUTDOWN SWITCH 11 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST654 |  | BB1ST654 | <IO NOT ASSIGNED> | Fuel feeding rotary feeder 1 rotation guard | FUEL FEEDING ROTARY | FEEDER 1 ROTATION GUARD |  | FUEL FEEDING ROTARY FEEDER 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS112 | MEAS_BIN_SRS | Boiler emergency shutdown switch 12 | BB1HS112 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  | BB1HS112 | BOILER EMERGENCY SHUTDOWN SWITCH 12 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST655 |  | BB1ST655 | <IO NOT ASSIGNED> | Fuel feeding rotary feeder 2 rotation guard | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | FUEL FEEDING ROTARY FEEDER 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS601 | MEAS_BIN_SRS | Fuel system emergency shutdown switch 1 | BB1HS601 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  | BB1HS601 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST659 |  | BB1ST659 | <IO NOT ASSIGNED> | Fuel feeding screw 1 rotation guard | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | FUEL FEEDING SCREW 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS602 | MEAS_BIN_SRS | Fuel system emergency shutdown switch 2 | BB1HS602 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  | BB1HS602 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS655 |  | BB1GS655 | <IO NOT ASSIGNED> | Slide gate valve open limit switch | SLIDE GATE VALVE OPEN | LIMIT SWITCH |  | SLIDE GATE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS603 | MEAS_BIN_SRS | Fuel system emergency shutdown switch 3 | BB1HS603 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  | BB1HS603 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS656 |  | BB1GS656 | <IO NOT ASSIGNED> | Slide gate valve close limit switch | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | SLIDE GATE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS604 | MEAS_BIN_SRS | Fuel system emergency shutdown switch 4 | BB1HS604 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  | BB1HS604 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS661 |  | BB1LS661 | <IO NOT ASSIGNED> | Lubrication alarm screw discharger | LUBRICATION ALARM | SCREW DISCHARGER |  | LUBRICATION ALARM SCREW DISCHARGER | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1IV002 | MTR_VLV | Feedwater pump 1 on-off valve | BB1IV002 | FEEDWATER PUMP 1 ON-OFF | VALVE |  | BB1IV002 | FEEDWATER PUMP 1 ON-OFF VALVE | IV | ISOLATING VALVE | MOTOR 0.25kW | MOTOR 0.25kW, 3 PHASE |  | 0.25kW, 400VAC |  |  |  |  | 0.25
BB1GS802 |  | BB1GS802 | <IO NOT ASSIGNED> | Bottom ash valve limit switch | BOTTOM ASH VALVE | LIMIT SWITCH |  | BOTTOM ASH VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1IV003 | MTR_VLV | Feed water pump 2 on-off valve | BB1IV003 | FEED WATER PUMP 2 ON-OFF | VALVE |  | BB1IV003 | FEED WATER PUMP 2 ON-OFF VALVE | IV | ISOLATING VALVE | MOTOR 0.25kW | MOTOR 0.25kW, 3 PHASE |  | 0.25kW, 400VAC |  |  |  |  | 0.25
BB1GS803 |  | BB1GS803 | <IO NOT ASSIGNED> | Bottom ash dropping chuteclosing device limit switch | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1IV202 | MTR_VLV | Main steam valve by-pass valve | BB1IV202 | MAIN STEAM VALVE BY-PASS | VALVE |  | BB1IV202 | MAIN STEAM VALVE BY-PASS VALVE | IV | ISOLATING VALVE | MOTOR 0.12kW | MOTOR 0.12kW, 3 PHASE |  | 0.12kW, 400VAC |  |  |  |  | 0.12
BB1LS852 |  | BB1LS852 | <IO NOT ASSIGNED> | Fly ash container level switch | FLY ASH CONTAINER | LEVEL SWITCH |  | FLY ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1CV201 | MTR_VLV | Start-up valve | BB1CV201 | START-UP VALVE |  |  | BB1CV201 | START-UP VALVE | CV | CONTROL VALVE | MOTOR 0.06kW | MOTOR 0.06kW, 3 PHASE |  | 0.06kW, 400VAC |  |  |  |  | 0.06
BB1ST805 |  | BB1ST805 | <IO NOT ASSIGNED> | Heated ESP collection screw rotation guard | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  | HEATED ESP COLLECTION SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1IV201 | MTR_VLV | Main steam valve | BB1IV201 | MAIN STEAM VALVE |  |  | BB1IV201 | MAIN STEAM VALVE | IV | ISOLATING VALVE | MOTOR 0.45kW | MOTOR 0.45kW, 3 PHASE |  | 0.45kW, 400VAC |  |  |  |  | 0.45
BB1ST808 |  | BB1ST808 | <IO NOT ASSIGNED> | ESP hopper 2 screw rotation guard | ESP HOPPER 2 SCREW | ROTATION GUARD |  | ESP HOPPER 2 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1IV200 | MTR_VLV | Start-up check valve | BB1IV200 | START-UP CHECK VALVE |  |  | BB1IV200 | START-UP CHECK VALVE | IV | ISOLATING VALVE | MOTOR 0.12kW | MOTOR 0.12kW, 3 PHASE |  | 0.12kW, 400VAC |  |  |  |  | 0.12
BB1ST809 |  | BB1ST809 | <IO NOT ASSIGNED> | ESP hopper 1 screw rotation guard | ESP HOPPER 1 SCREW | ROTATION GUARD |  | ESP HOPPER 1 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1IV203 | MTR_VLV | Sootblowing line on-off valve | BB1IV203 | SOOTBLOWING LINE ON-OFF | VALVE |  | BB1IV203 | SOOTBLOWING LINE ON-OFF VALVE | IV | ISOLATING VALVE | MOTOR 0.12kW | MOTOR 0.12kW, 3 PHASE |  | 0.12kW, 400VAC |  |  |  |  | 0.12
BB1ST804 |  | BB1ST804 | <IO NOT ASSIGNED> | ESP Rotary valve rotation guard | ESP ROTARY VALVE | ROTATION GUARD |  | ESP ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1CV003 | MTR_VLV | Continuous blow down valve | BB1CV003 | CONTINUOUS BLOW DOWN | VALVE |  | BB1CV003 | CONTINUOUS BLOW DOWN VALVE | CV | CONTROL VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1TS808 |  | BB1TS808 | <IO NOT ASSIGNED> | ESP Ash hopper 2 overheat thermostat | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  | ESP ASH HOPPER 2 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1CV203 | MTR_VLV | Steam accumulator pressure control valve | BB1CV203 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE |  | BB1CV203 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE | CV | CONTROL VALVE | MOTOR 0.25kW | MOTOR 0.25kW, 3 PHASE |  | 0.25kW, 400VAC |  |  |  |  | 0.25
BB1TS809 |  | BB1TS809 | <IO NOT ASSIGNED> | ESP Ash hopper 1 overheat thermostat | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  | ESP ASH HOPPER 1 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1CV202 | MTR_VLV | Steam pressure reduction valve | BB1CV202 | STEAM PRESSURE REDUCTION | VALVE |  | BB1CV202 | STEAM PRESSURE REDUCTION VALVE | CV | CONTROL VALVE | MOTOR 0.25kW | MOTOR 0.25kW, 3 PHASE |  | 0.25kW, 400VAC |  |  |  |  | 0.25
BB1TS805 |  | BB1TS805 | <IO NOT ASSIGNED> | ESP collection screw heating thermostat | ESP COLLECTION SCREW | HEATING THERMOSTAT |  | ESP COLLECTION SCREW HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1IV204 | MTR_VLV | Main steam line accumulator bypass on-off valve | BB1IV204 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE | BB1IV204 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE | IV | ISOLATING VALVE | MOTOR 0.45kW | MOTOR 0.45kW, 3 PHASE |  | 0.45kW, 400VAC |  |  |  |  | 0.45
BB1TS804 |  | BB1TS804 | <IO NOT ASSIGNED> | ESP Rotary valve heating thermostat | ESP ROTARY VALVE | HEATING THERMOSTAT |  | ESP ROTARY VALVE HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1IV205 | MTR_VLV | Steam accumulator ON-OFF isolating valve | BB1IV205 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE |  | BB1IV205 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE | IV | ISOLATING VALVE | MOTOR 0.45kW | MOTOR 0.45kW, 3 PHASE |  | 0.45kW, 400VAC |  |  |  |  | 0.45
BB1GS855 |  | BB1GS855 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve open limit switch | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1IV206 | MTR_VLV | Primary air preheater on-off valve | BB1IV206 | PRIMARY AIR PREHEATER | ON-OFF VALVE |  | BB1IV206 | PRIMARY AIR PREHEATER ON-OFF VALVE | IV | ISOLATING VALVE | MOTOR 0.12kW | MOTOR 0.12kW, 3 PHASE |  | 0.12kW, 400VAC |  |  |  |  | 0.12
BB1GS856 |  | BB1GS856 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve close limit switch | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1FM001 | OESA_3ph | Bottom ash sieve feed | BB1FM001 | BOTTOM ASH SIEVE FEED |  |  | BB1FM001 | BOTTOM ASH SIEVE FEED | FM | MOTOR | MOTOR 1.4kW | MOTOR 1.4kW, 3 PHASE |  | 1.4kW, 400VAC |  |  |  |  | 1.4
BB1GS857 |  | BB1GS857 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve open limit switch | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1FL650 | MCCB_1ph | Fuel silo dust filter control box feed | BB1FL650 | FUEL SILO DUST FILTER | CONTROL BOX FEED |  | BB1FL650 | FUEL SILO DUST FILTER CONTROL BOX FEED | FL | FILTER | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS858 |  | BB1GS858 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve close limit switch | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1EH662 | MCCB_1ph | Heater for slipring unit | BB1EH662 | HEATER FOR SLIPRING UNIT |  |  | BB1EH662 | HEATER FOR SLIPRING UNIT | EH | HEATER | MOTOR 0.4kW | MOTOR 0.4kW, 3 PHASE |  | 0.4kW, 400VAC |  |  |  |  | 0.4
BB1GS850 |  | BB1GS850 | <IO NOT ASSIGNED> | Bottom ash sieve bypass valve close limit switch | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH SIEVE BYPASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | <005> | #N/A | Sand transmitter 230 Vac feed | <005> | SAND TRANSMITTER | 230 VAC FEED |  | <005> | SAND TRANSMITTER 230 VAC FEED | 5> | #N/A | #N/A | #N/A |  | #N/A |  |  |  |  | #N/A
BB1GS851 |  | BB1GS851 | <IO NOT ASSIGNED> | Bottom ash sieve bypass valve open limit switch | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH SIEVE BYPASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1DR400 | MCCB_1ph | Compressor 1 dryer | BB1DR400 | COMPRESSOR 1 DRYER |  |  | BB1DR400 | COMPRESSOR 1 DRYER | DR | DRYER | MOTOR 4kW | MOTOR 4kW, 3 PHASE |  | 4kW, 400VAC |  |  |  |  | 4
BB1FS003 |  | BB1FS003 | <IO NOT ASSIGNED> | Bottom ash cooling flow switch | BOTTOM ASH COOLING | FLOW SWITCH |  | BOTTOM ASH COOLING FLOW SWITCH | FS | FLOW SWITCH | DI | MEAS_BIN |  | BB1DR401 | MCCB_1ph | Compressor 2 dryer | BB1DR401 | COMPRESSOR 2 DRYER |  |  | BB1DR401 | COMPRESSOR 2 DRYER | DR | DRYER | MOTOR 4kW | MOTOR 4kW, 3 PHASE |  | 4kW, 400VAC |  |  |  |  | 4
BB1GS801 |  | BB1GS801 | <IO NOT ASSIGNED> | Sand filling valve position open limit switch | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | SAND FILLING VALVE POSITION OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1CP002 | #N/A | Smoke Exhaust cabinet | BB1CP002 | SMOKE EXHAUST CABINET |  |  | BB1CP002 | SMOKE EXHAUST CABINET | CP | CONTROL PANEL? | #N/A | #N/A |  | #N/A |  |  |  |  | #N/A
BB1GS800 |  | BB1GS800 | <IO NOT ASSIGNED> | Sand filling valve position close limit switch | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | SAND FILLING VALVE POSITION CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1FG300 | ESP_DI_DO | ESP hardwired signals to/from Boiler PLC | BB1FG300 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC |  | BB1FG300 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC | FG | ESP | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS854 |  | BB1GS854 | <IO NOT ASSIGNED> | Bottom ash dropping chute limit switch | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | BOTTOM ASH DROPPING CHUTE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SI400 | FAN_SRS_DO | Primary air fan safety interlock | BB1SI400 | PRIMARY AIR FAN | SAFETY INTERLOCK |  | BB1SI400 | PRIMARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS853 |  | BB1GS853 | <IO NOT ASSIGNED> | Bottom ash dropping chute closing device limit switch | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SI401 | FAN_SRS_DO | Secondary air fan safety interlock | BB1SI401 | SECONDARY AIR FAN | SAFETY INTERLOCK |  | BB1SI401 | SECONDARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS859 |  | BB1GS859 | <IO NOT ASSIGNED> | Bottom ash to container in place | BOTTOM ASH TO CONTAINER | IN PLACE |  | BOTTOM ASH TO CONTAINER IN PLACE | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SI603 | FAN_SRS_DO | Fuel reception hydraulic unit 1, pump 1 safety interlock | BB1SI603 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK | BB1SI603 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS850 |  | BB1LS850 | <IO NOT ASSIGNED> | Bottom ash container level switch | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1SI604 | FAN_SRS_DO | Fuel reception hydraulic unit 1, pump 2 safety interlock | BB1SI604 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK | BB1SI604 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS851 |  | BB1LS851 | <IO NOT ASSIGNED> | Bottom ash container level switch | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1SI605 | FAN_SRS_DO | Fuel reception hydraulic unit 1, pump 3 safety interlock | BB1SI605 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK | BB1SI605 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1PT800 |  | BB1PT800 | <IO NOT ASSIGNED> | Recycled bed material damper pressure switch | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  | RECYCLED BED MATERIAL DAMPER PRESSURE SWITCH | PT | PRESSURE TRANSMITTER | DI | MEAS_BIN |  | BB1SI658 | FAN_SRS_DO | Scraper Conveyor 1 safety interlock | BB1SI658 | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  | BB1SI658 | SCRAPER CONVEYOR 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST856 |  | BB1ST856 | <IO NOT ASSIGNED> | Purified sand screw conveyor rotation guard | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | PURIFIED SAND SCREW CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1SI659 | FAN_SRS_DO | Belt Conveyor safety interlock | BB1SI659 | BELT CONVEYOR | SAFETY INTERLOCK |  | BB1SI659 | BELT CONVEYOR SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST850 |  | BB1ST850 | <IO NOT ASSIGNED> | Bottom ash conveyor rotation guard | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | BOTTOM ASH CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1SI675 | FAN_SRS_DO | Disc screen drive 1 safety interlock | BB1SI675 | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  | BB1SI675 | DISC SCREEN DRIVE 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS852 |  | BB1GS852 | <IO NOT ASSIGNED> | Bottom ash conveyor blockage detector | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | BOTTOM ASH CONVEYOR BLOCKAGE DETECTOR | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SI676 | FAN_SRS_DO | Disc screen drive 2 safety interlock | BB1SI676 | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  | BB1SI676 | DISC SCREEN DRIVE 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST852 |  | BB1ST852 | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve rotation guard | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 2ND PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1SI672 | FAN_SRS_DO | Scraper Conveyor 2 safety interlock | BB1SI672 | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  | BB1SI672 | SCRAPER CONVEYOR 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1ST853 |  | BB1ST853 | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve rotation guard | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 3RD PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1SI550 | FAN_SRS_DO | Flue gas fan safety interlock | BB1SI550 | FLUE GAS FAN | SAFETY INTERLOCK |  | BB1SI550 | FLUE GAS FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1GS020 |  | BB1GS020 | <IO NOT ASSIGNED> | Emergency shower use switch | EMERGENCY SHOWER | USE SWITCH |  | EMERGENCY SHOWER USE SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SV601 | PUSH_FEED | Control Valve push feeders unloading station 1 | BB1SV601 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | BB1SV601 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS103 |  | BB1LS103 | <IO NOT ASSIGNED> | Steam drum level switch 1 | STEAM DRUM LEVEL SWITCH 1 |  |  | STEAM DRUM LEVEL SWITCH 1 | LS | LEVEL SWITCH |  | MEAS_BIN_SRS |  | BB1SV603 | PUSH_FEED | Control Valve push feeders unloading station 3 | BB1SV603 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | BB1SV603 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1LS104 |  | BB1LS104 | <IO NOT ASSIGNED> | Steam drum level switch 2 | STEAM DRUM LEVEL SWITCH 2 |  |  | STEAM DRUM LEVEL SWITCH 2 | LS | LEVEL SWITCH |  | MEAS_BIN_SRS |  | BB1SV602 | PUSH_FEED | Control Valve push feeders unloading station 2 | BB1SV602 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | BB1SV602 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 | SV | SOLENOID VALVE | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1HS101 |  | BB1HS101 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 1 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  | BOILER EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM001 | FRQ_DIR | Feed water pump 1 | BB1EM001 | FEED WATER PUMP 1 |  |  | BB1EM001 | FEED WATER PUMP 1 | EM | MOTOR | MOTOR 75kW | MOTOR 75kW, 3 PHASE |  | 75kW, 400VAC |  |  |  |  | 75
BB1HS103 |  | BB1HS103 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 3 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  | BOILER EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM002 | FRQ_DIR | Feed water pump 2 | BB1EM002 | FEED WATER PUMP 2 |  |  | BB1EM002 | FEED WATER PUMP 2 | EM | MOTOR | MOTOR 75kW | MOTOR 75kW, 3 PHASE |  | 75kW, 400VAC |  |  |  |  | 75
BB1HS104 |  | BB1HS104 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 4 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  | BOILER EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM400 | FRQ_DIR | Primary air fan | BB1EM400 | PRIMARY AIR FAN |  |  | BB1EM400 | PRIMARY AIR FAN | EM | MOTOR | MOTOR 132kW | MOTOR 132kW, 3 PHASE |  | 132kW, 400VAC |  |  |  |  | 132
BB1HS102 |  | BB1HS102 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 2 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  | BOILER EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM401 | FRQ_DIR | Secondary air fan | BB1EM401 | SECONDARY AIR FAN |  |  | BB1EM401 | SECONDARY AIR FAN | EM | MOTOR | MOTOR 45kW | MOTOR 45kW, 3 PHASE |  | 45kW, 400VAC |  |  |  |  | 45
BB1HS105 |  | BB1HS105 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 5 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  | BOILER EMERGENCY SHUTDOWN SWITCH 5 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM550 | FRQ_DIR | Flue gas fan | BB1EM550 | FLUE GAS FAN |  |  | BB1EM550 | FLUE GAS FAN | EM | MOTOR | MOTOR 75kW | MOTOR 75kW, 3 PHASE |  | 75kW, 400VAC |  |  |  |  | 75
BB1HS106 |  | BB1HS106 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 6 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  | BOILER EMERGENCY SHUTDOWN SWITCH 6 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM603 | FRQ_DIRH | Fuel reception hydraulic unit 1, pump 1 | BB1EM603 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  | BB1EM603 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 | EM | MOTOR | MOTOR 37kW | MOTOR 37kW, 3 PHASE |  | 37kW, 400VAC |  |  |  |  | 37
BB1HS107 |  | BB1HS107 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 7 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  | BOILER EMERGENCY SHUTDOWN SWITCH 7 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM604 | FRQ_DIRH | Fuel reception hydraulic unit 1, pump 2 | BB1EM604 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  | BB1EM604 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 | EM | MOTOR | MOTOR 37kW | MOTOR 37kW, 3 PHASE |  | 37kW, 400VAC |  |  |  |  | 37
BB1HS108 |  | BB1HS108 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 8 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  | BOILER EMERGENCY SHUTDOWN SWITCH 8 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM605 | FRQ_DIRH | Fuel reception hydraulic unit 1, pump 3 | BB1EM605 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  | BB1EM605 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 | EM | MOTOR | MOTOR 37kW | MOTOR 37kW, 3 PHASE |  | 37kW, 400VAC |  |  |  |  | 37
BB1HS109 |  | BB1HS109 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 9 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  | BOILER EMERGENCY SHUTDOWN SWITCH 9 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM658 | FRQ_REVH | SCRAPER CONVEYOR 1 | BB1EM658 | SCRAPER CONVEYOR 1 |  |  | BB1EM658 | SCRAPER CONVEYOR 1 | EM | MOTOR | MOTOR 15kW | MOTOR 15kW, 3 PHASE |  | 15kW, 400VAC | 20F11GC030AA0NNNNN | PowerFlex 753 Series VSD, 15kW, 400VAC | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 15
BB1HS110 |  | BB1HS110 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 10 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  | BOILER EMERGENCY SHUTDOWN SWITCH 10 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM659 | FRQ_REVH | BELT CONVEYOR | BB1EM659 | BELT CONVEYOR |  |  | BB1EM659 | BELT CONVEYOR | EM | MOTOR | MOTOR 4kW | MOTOR 4kW, 3 PHASE |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 4
BB1HS111 |  | BB1HS111 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 11 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  | BOILER EMERGENCY SHUTDOWN SWITCH 11 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM675 | DOL_REVH_BUS | DISC SCREEN DRIVE 1 | BB1EM675 | DISC SCREEN DRIVE 1 |  |  | BB1EM675 | DISC SCREEN DRIVE 1 | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1HS112 |  | BB1HS112 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 12 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  | BOILER EMERGENCY SHUTDOWN SWITCH 12 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM676 | FRQ_REVH | DISC SCREEN DRIVE 2 | BB1EM676 | DISC SCREEN DRIVE 2 |  |  | BB1EM676 | DISC SCREEN DRIVE 2 | EM | MOTOR | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE |  | 7.5kW, 400VAC | 20F11GC015AA0NNNNN | PowerFlex 753 Series VSD, 7.5kW, 400VAC | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 7.5
BB1HS601 |  | BB1HS601 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 1 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM672 | FRQ_REVH | SCRAPER CONVEYOR 2 | BB1EM672 | SCRAPER CONVEYOR 2 |  |  | BB1EM672 | SCRAPER CONVEYOR 2 | EM | MOTOR | MOTOR 18.5kW | MOTOR 18.5kW, 3 PHASE |  | 18.5kW, 400VAC | 20F11GC037AA0NNNNN | PowerFlex 753 Series VSD, 18.5kW, 400VAC | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 18.5
BB1HS602 |  | BB1HS602 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 2 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM662 | FRQ_REVH | FUEL SILO SCREW DISCHARGE | BB1EM662 | FUEL SILO SCREW DISCHARGE |  |  | BB1EM662 | FUEL SILO SCREW DISCHARGE | EM | MOTOR | MOTOR 22kW | MOTOR 22kW, 3 PHASE |  | 22kW, 400VAC | 20F11GC043AA0NNNNN | PowerFlex 753 Series VSD, 22kW, 400VAC | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | 22
BB1HS603 |  | BB1HS603 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 3 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM650 | FRQ_REVH | SLEWING MOTOR FOR SCREW | BB1EM650 | SLEWING MOTOR FOR SCREW |  |  | BB1EM650 | SLEWING MOTOR FOR SCREW | EM | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 2.2
BB1HS604 |  | BB1HS604 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 4 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM663 | FRQ_REVH | FUEL SILO CROSS CONVEYOR | BB1EM663 | FUEL SILO CROSS CONVEYOR |  |  | BB1EM663 | FUEL SILO CROSS CONVEYOR | EM | MOTOR | MOTOR 4kW | MOTOR 4kW, 3 PHASE |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 4
BB1IV002 | _OPEN | BB1IV002_OPEN | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve OPEN | FEEDWATER PUMP 1 ON-OFF | VALVE OPEN |  | FEEDWATER PUMP 1 ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM664 | FRQ_REVH | FUEL FEEDING SCREW 1 | BB1EM664 | FUEL FEEDING SCREW 1 |  |  | BB1EM664 | FUEL FEEDING SCREW 1 | EM | MOTOR | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE |  | 5.5kW, 400VAC | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 5.5
BB1IV002 | _CLOSE | BB1IV002_CLOSE | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve CLOSE | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSE |  | FEEDWATER PUMP 1 ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM665 | FRQ_REVH | FUEL FEEDING SCREW 2 | BB1EM665 | FUEL FEEDING SCREW 2 |  |  | BB1EM665 | FUEL FEEDING SCREW 2 | EM | MOTOR | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE |  | 5.5kW, 400VAC | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 5.5
BB1IV002 | _OPENED | BB1IV002_OPENED | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve OPENED | FEEDWATER PUMP 1 ON-OFF | VALVE OPENED |  | FEEDWATER PUMP 1 ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM852 | FRQ_REVH | BOTTOM ASH CONVEYOR | BB1EM852 | BOTTOM ASH CONVEYOR |  |  | BB1EM852 | BOTTOM ASH CONVEYOR | EM | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | 2.2
BB1IV002 | _CLOSED | BB1IV002_CLOSED | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve CLOSED | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSED |  | FEEDWATER PUMP 1 ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM660 | DOL_DIR | Cooling fan for slewing motor | BB1EM660 | COOLING FAN FOR | SLEWING MOTOR |  | BB1EM660 | COOLING FAN FOR SLEWING MOTOR | EM | MOTOR | MOTOR 0.09kW | MOTOR 0.09kW, 3 PHASE |  | 0.09kW, 400VAC |  |  |  |  | 0.09
BB1IV002 | _FAULT | BB1IV002_FAULT | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve FAULT | FEEDWATER PUMP 1 ON-OFF | VALVE FAULT |  | FEEDWATER PUMP 1 ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM654 | DOL_DIR | Lubrication unit | BB1EM654 | LUBRICATION UNIT |  |  | BB1EM654 | LUBRICATION UNIT | EM | MOTOR | MOTOR 0.2kW | MOTOR 0.2kW, 3 PHASE |  | 0.2kW, 400VAC |  |  |  |  | 0.2
BB1IV002 | _POSITION | BB1IV002_POSITION | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve POSITION | FEEDWATER PUMP 1 ON-OFF | VALVE POSITION |  | FEEDWATER PUMP 1 ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM653 | DOL_DIR | Cooling fan fuel feeding screw 1 | BB1EM653 | COOLING FAN FUEL | FEEDING SCREW 1 |  | BB1EM653 | COOLING FAN FUEL FEEDING SCREW 1 | EM | MOTOR | MOTOR 0.15kW | MOTOR 0.15kW, 3 PHASE |  | 0.15kW, 400VAC |  |  |  |  | 0.15
BB1IV003 | _OPEN | BB1IV003_OPEN | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve OPEN | FEED WATER PUMP 2 ON-OFF | VALVE OPEN |  | FEED WATER PUMP 2 ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM655 | DOL_DIR | Cooling fan fuel feeding screw 2 | BB1EM655 | COOLING FAN FUEL | FEEDING SCREW 2 |  | BB1EM655 | COOLING FAN FUEL FEEDING SCREW 2 | EM | MOTOR | MOTOR 0.15kW | MOTOR 0.15kW, 3 PHASE |  | 0.15kW, 400VAC |  |  |  |  | 0.15
BB1IV003 | _CLOSE | BB1IV003_CLOSE | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve CLOSE | FEED WATER PUMP 2 ON-OFF | VALVE CLOSE |  | FEED WATER PUMP 2 ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM606 | DOL_DIR_BUS | Dust extraction fan | BB1EM606 | DUST EXTRACTION FAN |  |  | BB1EM606 | DUST EXTRACTION FAN | EM | MOTOR | MOTOR 30kW | MOTOR 30kW, 3 PHASE |  | 30kW, 400VAC |  |  |  |  | 30
BB1IV003 | _OPENED | BB1IV003_OPENED | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve OPENED | FEED WATER PUMP 2 ON-OFF | VALVE OPENED |  | FEED WATER PUMP 2 ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EH600 | DOL_DIR_BUS | Electric heater hydraulic unit | BB1EH600 | ELECTRIC HEATER | HYDRAULIC UNIT |  | BB1EH600 | ELECTRIC HEATER HYDRAULIC UNIT | EH | HEATER | MOTOR 1.5kW | MOTOR 1.5kW, 3 PHASE |  | 1.5kW, 400VAC |  |  |  |  | 1.5
BB1IV003 | _CLOSED | BB1IV003_CLOSED | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve CLOSED | FEED WATER PUMP 2 ON-OFF | VALVE CLOSED |  | FEED WATER PUMP 2 ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM651 | DOL_DIR_BUS | Fuel silo dust filter fan | BB1EM651 | FUEL SILO DUST FILTER FAN |  |  | BB1EM651 | FUEL SILO DUST FILTER FAN | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IV003 | _FAULT | BB1IV003_FAULT | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve FAULT | FEED WATER PUMP 2 ON-OFF | VALVE FAULT |  | FEED WATER PUMP 2 ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM008 | DOL_DIR_BUS | Conveyor cooling pump | BB1EM008 | CONVEYOR COOLING PUMP |  |  | BB1EM008 | CONVEYOR COOLING PUMP | EM | MOTOR | MOTOR 1.1kW | MOTOR 1.1kW, 3 PHASE |  | 1.1kW, 400VAC |  |  |  |  | 1.1
BB1IV003 | _POSITION | BB1IV003_POSITION | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve POSITION | FEED WATER PUMP 2 ON-OFF | VALVE POSITION |  | FEED WATER PUMP 2 ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM009 | DOL_DIR_BUS | Bottom ash conveyor heat exchanger fan | BB1EM009 | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN |  | BB1EM009 | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN | EM | MOTOR | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE |  | 7.5kW, 400VAC |  |  |  |  | 7.5
BB1IV202 | _OPEN | BB1IV202_OPEN | <IO NOT ASSIGNED> | Main steam valve by-pass valve OPEN | MAIN STEAM VALVE BY-PASS | VALVE OPEN |  | MAIN STEAM VALVE BY-PASS VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM408 | DOL_DIR_BUS | Boiler house heater 1 | BB1EM408 | BOILER HOUSE HEATER 1 |  |  | BB1EM408 | BOILER HOUSE HEATER 1 | EM | MOTOR | MOTOR 15kW | MOTOR 15kW, 3 PHASE |  | 15kW, 400VAC |  |  |  |  | 15
BB1IV202 | _CLOSE | BB1IV202_CLOSE | <IO NOT ASSIGNED> | Main steam valve by-pass valve CLOSE | MAIN STEAM VALVE BY-PASS | VALVE CLOSE |  | MAIN STEAM VALVE BY-PASS VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM409 | DOL_DIR_BUS | Boiler house heater 2 | BB1EM409 | BOILER HOUSE HEATER 2 |  |  | BB1EM409 | BOILER HOUSE HEATER 2 | EM | MOTOR | MOTOR 15kW | MOTOR 15kW, 3 PHASE |  | 15kW, 400VAC |  |  |  |  | 15
BB1IV202 | _OPENED | BB1IV202_OPENED | <IO NOT ASSIGNED> | Main steam valve by-pass valve OPENED | MAIN STEAM VALVE BY-PASS | VALVE OPENED |  | MAIN STEAM VALVE BY-PASS VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM703 | DOL_DIRH | Chemical filling pump 1 | BB1EM703 | CHEMICAL FILLING PUMP 1 |  |  | BB1EM703 | CHEMICAL FILLING PUMP 1 | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IV202 | _CLOSED | BB1IV202_CLOSED | <IO NOT ASSIGNED> | Main steam valve by-pass valve CLOSED | MAIN STEAM VALVE BY-PASS | VALVE CLOSED |  | MAIN STEAM VALVE BY-PASS VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM704 | DOL_DIRH | Chemical filling pump 2 | BB1EM704 | CHEMICAL FILLING PUMP 2 |  |  | BB1EM704 | CHEMICAL FILLING PUMP 2 | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IV202 | _FAULT | BB1IV202_FAULT | <IO NOT ASSIGNED> | Main steam valve by-pass valve FAULT | MAIN STEAM VALVE BY-PASS | VALVE FAULT |  | MAIN STEAM VALVE BY-PASS VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM670 | DOL_DIRH_BUS | Belt magnet | BB1EM670 | BELT MAGNET |  |  | BB1EM670 | BELT MAGNET | EM | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE |  | 2.2kW, 400VAC |  |  |  |  | 2.2
BB1IV202 | _POSITION | BB1IV202_POSITION | <IO NOT ASSIGNED> | Main steam valve by-pass valve POSITION | MAIN STEAM VALVE BY-PASS | VALVE POSITION |  | MAIN STEAM VALVE BY-PASS VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM652 | DOL_DIRH_BUS | Rotating fuel spreader | BB1EM652 | ROTATING FUEL SPREADER |  |  | BB1EM652 | ROTATING FUEL SPREADER | EM | MOTOR | MOTOR 0.75kW | MOTOR 0.75kW, 3 PHASE |  | 0.75kW, 400VAC |  |  |  |  | 0.75
BB1CV201 | _OPEN | BB1CV201_OPEN | <IO NOT ASSIGNED> | Start-up valve OPEN | START-UP VALVE OPEN |  |  | START-UP VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV |  | BB1BL200 | DOL_REV_BUS | Sootblower 1 | BB1BL200 | SOOTBLOWER 1 |  |  | BB1BL200 | SOOTBLOWER 1 | BL | BLOWER | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1CV201 | _CLOSE | BB1CV201_CLOSE | <IO NOT ASSIGNED> | Start-up valve CLOSE | START-UP VALVE CLOSE |  |  | START-UP VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV |  | BB1BL201 | DOL_REV_BUS | Sootblower 2 | BB1BL201 | SOOTBLOWER 2 |  |  | BB1BL201 | SOOTBLOWER 2 | BL | BLOWER | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1CV201 | _OPENED | BB1CV201_OPENED | <IO NOT ASSIGNED> | Start-up valve OPENED | START-UP VALVE OPENED |  |  | START-UP VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV |  | BB1BL202 | DOL_REV_BUS | Sootblower 3 | BB1BL202 | SOOTBLOWER 3 |  |  | BB1BL202 | SOOTBLOWER 3 | BL | BLOWER | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1CV201 | _CLOSED | BB1CV201_CLOSED | <IO NOT ASSIGNED> | Start-up valve CLOSED | START-UP VALVE CLOSED |  |  | START-UP VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV |  | BB1BL203 | DOL_REV_BUS | Sootblower 4 | BB1BL203 | SOOTBLOWER 4 |  |  | BB1BL203 | SOOTBLOWER 4 | BL | BLOWER | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1CV201 | _FAULT | BB1CV201_FAULT | <IO NOT ASSIGNED> | Start-up valve FAULT | START-UP VALVE FAULT |  |  | START-UP VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV |  | BB1BL204 | DOL_REV_BUS | Sootblower 5 | BB1BL204 | SOOTBLOWER 5 |  |  | BB1BL204 | SOOTBLOWER 5 | BL | BLOWER | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1CV201 | _POSITION | BB1CV201_POSITION | <IO NOT ASSIGNED> | Start-up valve POSITION | START-UP VALVE POSITION |  |  | START-UP VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV |  | BB1BL205 | DOL_REV_BUS | Sootblower 6 | BB1BL205 | SOOTBLOWER 6 |  |  | BB1BL205 | SOOTBLOWER 6 | BL | BLOWER | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1IV201 | _OPEN | BB1IV201_OPEN | <IO NOT ASSIGNED> | Main steam valve OPEN | MAIN STEAM VALVE OPEN |  |  | MAIN STEAM VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1BL206 | DOL_REV_BUS | Sootblower 7 | BB1BL206 | SOOTBLOWER 7 |  |  | BB1BL206 | SOOTBLOWER 7 | BL | BLOWER | MOTOR 0.37kW | MOTOR 0.37kW, 3 PHASE |  | 0.37kW, 400VAC |  |  |  |  | 0.37
BB1IV201 | _CLOSE | BB1IV201_CLOSE | <IO NOT ASSIGNED> | Main steam valve CLOSE | MAIN STEAM VALVE CLOSE |  |  | MAIN STEAM VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM815 | DOL_REV_BUS | Fly ash container screw | BB1EM815 | FLY ASH CONTAINER SCREW |  |  | BB1EM815 | FLY ASH CONTAINER SCREW | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IV201 | _OPENED | BB1IV201_OPENED | <IO NOT ASSIGNED> | Main steam valve OPENED | MAIN STEAM VALVE OPENED |  |  | MAIN STEAM VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM855 | DOL_REV_BUS | Ash container screw | BB1EM855 | ASH CONTAINER SCREW |  |  | BB1EM855 | ASH CONTAINER SCREW | EM | MOTOR | MOTOR 1.5kW | MOTOR 1.5kW, 3 PHASE |  | 1.5kW, 400VAC |  |  |  |  | 1.5
BB1IV201 | _CLOSED | BB1IV201_CLOSED | <IO NOT ASSIGNED> | Main steam valve CLOSED | MAIN STEAM VALVE CLOSED |  |  | MAIN STEAM VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM401 | FRQ_DIR | Exhaust fan 1 | BB1EM401 | EXHAUST FAN 1 |  |  | BB1EM401 | EXHAUST FAN 1 | EM | MOTOR | MOTOR 45kW | MOTOR 45kW, 3 PHASE |  | 45kW, 400VAC |  |  |  |  | 45
BB1IV201 | _FAULT | BB1IV201_FAULT | <IO NOT ASSIGNED> | Main steam valve FAULT | MAIN STEAM VALVE FAULT |  |  | MAIN STEAM VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM402 | COMPR | Exhaust fan 2 | BB1EM402 | EXHAUST FAN 2 |  |  | BB1EM402 | EXHAUST FAN 2 | EM | MOTOR | MOTOR 30kW | MOTOR 30kW, 3 PHASE |  | 30kW, 400VAC |  |  |  |  | 30
BB1IV201 | _POSITION | BB1IV201_POSITION | <IO NOT ASSIGNED> | Main steam valve POSITION | MAIN STEAM VALVE POSITION |  |  | MAIN STEAM VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM403 | COMPR | Exhaust fan 3 | BB1EM403 | EXHAUST FAN 3 |  |  | BB1EM403 | EXHAUST FAN 3 | EM | MOTOR | MOTOR 30kW | MOTOR 30kW, 3 PHASE |  | 30kW, 400VAC |  |  |  |  | 30
BB1IV200 | _OPEN | BB1IV200_OPEN | <IO NOT ASSIGNED> | Start-up check valve OPEN | START-UP CHECK VALVE | OPEN |  | START-UP CHECK VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  |  | #N/A | [8 empty] | 0 | #N/A | #N/A |  | #N/A |  |  |  |  | #N/A
BB1IV200 | _CLOSE | BB1IV200_CLOSE | <IO NOT ASSIGNED> | Start-up check valve CLOSE | START-UP CHECK VALVE | CLOSE |  | START-UP CHECK VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM673 | DOL_REVH_BUS | Levelling roller 1 | BB1EM673 | LEVELLING ROLLER 1 |  |  | BB1EM673 | LEVELLING ROLLER 1 | EM | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE |  | 2.2kW, 400VAC |  |  |  |  | 2.2
BB1IV200 | _OPENED | BB1IV200_OPENED | <IO NOT ASSIGNED> | Start-up check valve OPENED | START-UP CHECK VALVE | OPENED |  | START-UP CHECK VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM674 | DOL_REVH_BUS | Levelling roller 2 | BB1EM674 | LEVELLING ROLLER 2 |  |  | BB1EM674 | LEVELLING ROLLER 2 | EM | MOTOR | MOTOR 3kW | MOTOR 3kW, 3 PHASE |  | 3kW, 400VAC |  |  |  |  | 3
BB1IV200 | _CLOSED | BB1IV200_CLOSED | <IO NOT ASSIGNED> | Start-up check valve CLOSED | START-UP CHECK VALVE | CLOSED |  | START-UP CHECK VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM601 | DOL_REVH_BUS | Dust extraction rotary feeder | BB1EM601 | DUST EXTRACTION | ROTARY FEEDER |  | BB1EM601 | DUST EXTRACTION ROTARY FEEDER | EM | MOTOR | MOTOR 0.75kW | MOTOR 0.75kW, 3 PHASE |  | 0.75kW, 400VAC |  |  |  |  | 0.75
BB1IV200 | _FAULT | BB1IV200_FAULT | <IO NOT ASSIGNED> | Start-up check valve FAULT | START-UP CHECK VALVE | FAULT |  | START-UP CHECK VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1IV650 | DOL_REVH_BUS | Slide gate valve | BB1IV650 | SLIDE GATE VALVE |  |  | BB1IV650 | SLIDE GATE VALVE | IV | ISOLATING VALVE | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE |  | 2.2kW, 400VAC |  |  |  |  | 2.2
BB1IV200 | _POSITION | BB1IV200_POSITION | <IO NOT ASSIGNED> | Start-up check valve POSITION | START-UP CHECK VALVE | POSITION |  | START-UP CHECK VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM657 | DOL_REVH_BUS | Fuel feeding rotary valve 1 | BB1EM657 | FUEL FEEDING | ROTARY VALVE 1 |  | BB1EM657 | FUEL FEEDING ROTARY VALVE 1 | EM | MOTOR | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE |  | 7.5kW, 400VAC |  |  |  |  | 7.5
BB1IV203 | _OPEN | BB1IV203_OPEN | <IO NOT ASSIGNED> | Sootblowing line on-off valve OPEN | SOOTBLOWING LINE ON-OFF | VALVE OPEN |  | SOOTBLOWING LINE ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM656 | DOL_REVH_BUS | Fuel feeding rotary valve 2 | BB1EM656 | FUEL FEEDING | ROTARY VALVE 2 |  | BB1EM656 | FUEL FEEDING ROTARY VALVE 2 | EM | MOTOR | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE |  | 7.5kW, 400VAC |  |  |  |  | 7.5
BB1IV203 | _CLOSE | BB1IV203_CLOSE | <IO NOT ASSIGNED> | Sootblowing line on-off valve CLOSE | SOOTBLOWING LINE ON-OFF | VALVE CLOSE |  | SOOTBLOWING LINE ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM856 | DOL_REVH_BUS | Purified sand screw conveyor | BB1EM856 | PURIFIED SAND | SCREW CONVEYOR |  | BB1EM856 | PURIFIED SAND SCREW CONVEYOR | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IV203 | _OPENED | BB1IV203_OPENED | <IO NOT ASSIGNED> | Sootblowing line on-off valve OPENED | SOOTBLOWING LINE ON-OFF | VALVE OPENED |  | SOOTBLOWING LINE ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM850 | DOL_REVH_BUS | 2nd pass fly ash rotary valve | BB1EM850 | 2ND PASS FLY ASH | ROTARY VALVE |  | BB1EM850 | 2ND PASS FLY ASH ROTARY VALVE | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IV203 | _CLOSED | BB1IV203_CLOSED | <IO NOT ASSIGNED> | Sootblowing line on-off valve CLOSED | SOOTBLOWING LINE ON-OFF | VALVE CLOSED |  | SOOTBLOWING LINE ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM851 | DOL_REVH_BUS | 3rd pass fly ash rotary valve | BB1EM851 | 3RD PASS FLY ASH | ROTARY VALVE |  | BB1EM851 | 3RD PASS FLY ASH ROTARY VALVE | EM | MOTOR | MOTOR 0kW | MOTOR 0kW, 3 PHASE |  | 0kW, 400VAC |  |  |  |  | 0
BB1IV203 | _FAULT | BB1IV203_FAULT | <IO NOT ASSIGNED> | Sootblowing line on-off valve FAULT | SOOTBLOWING LINE ON-OFF | VALVE FAULT |  | SOOTBLOWING LINE ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV203 | _POSITION | BB1IV203_POSITION | <IO NOT ASSIGNED> | Sootblowing line on-off valve POSITION | SOOTBLOWING LINE ON-OFF | VALVE POSITION |  | SOOTBLOWING LINE ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1CV003 | _OPEN | BB1CV003_OPEN | <IO NOT ASSIGNED> | Continuous blow down valve OPEN | CONTINUOUS BLOW DOWN | VALVE OPEN |  | CONTINUOUS BLOW DOWN VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV003 | _CLOSE | BB1CV003_CLOSE | <IO NOT ASSIGNED> | Continuous blow down valve CLOSE | CONTINUOUS BLOW DOWN | VALVE CLOSE |  | CONTINUOUS BLOW DOWN VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV003 | _OPENED | BB1CV003_OPENED | <IO NOT ASSIGNED> | Continuous blow down valve OPENED | CONTINUOUS BLOW DOWN | VALVE OPENED |  | CONTINUOUS BLOW DOWN VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _CLOSED | BB1CV003_CLOSED | <IO NOT ASSIGNED> | Continuous blow down valve CLOSED | CONTINUOUS BLOW DOWN | VALVE CLOSED |  | CONTINUOUS BLOW DOWN VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _FAULT | BB1CV003_FAULT | <IO NOT ASSIGNED> | Continuous blow down valve FAULT | CONTINUOUS BLOW DOWN | VALVE FAULT |  | CONTINUOUS BLOW DOWN VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _POSITION | BB1CV003_POSITION | <IO NOT ASSIGNED> | Continuous blow down valve POSITION | CONTINUOUS BLOW DOWN | VALVE POSITION |  | CONTINUOUS BLOW DOWN VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1CV203 | _OPEN | BB1CV203_OPEN | <IO NOT ASSIGNED> | Steam accumulator pressure control valve OPEN | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV203 | _CLOSE | BB1CV203_CLOSE | <IO NOT ASSIGNED> | Steam accumulator pressure control valve CLOSE | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV203 | _OPENED | BB1CV203_OPENED | <IO NOT ASSIGNED> | Steam accumulator pressure control valve OPENED | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPENED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _CLOSED | BB1CV203_CLOSED | <IO NOT ASSIGNED> | Steam accumulator pressure control valve CLOSED | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _FAULT | BB1CV203_FAULT | <IO NOT ASSIGNED> | Steam accumulator pressure control valve FAULT | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | FAULT | STEAM ACCUMULATOR PRESSURE CONTROL VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _POSITION | BB1CV203_POSITION | <IO NOT ASSIGNED> | Steam accumulator pressure control valve POSITION | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | POSITION | STEAM ACCUMULATOR PRESSURE CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1CV202 | _OPEN | BB1CV202_OPEN | <IO NOT ASSIGNED> | Steam pressure reduction valve OPEN | STEAM PRESSURE REDUCTION | VALVE OPEN |  | STEAM PRESSURE REDUCTION VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV202 | _CLOSE | BB1CV202_CLOSE | <IO NOT ASSIGNED> | Steam pressure reduction valve CLOSE | STEAM PRESSURE REDUCTION | VALVE CLOSE |  | STEAM PRESSURE REDUCTION VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV202 | _OPENED | BB1CV202_OPENED | <IO NOT ASSIGNED> | Steam pressure reduction valve OPENED | STEAM PRESSURE REDUCTION | VALVE OPENED |  | STEAM PRESSURE REDUCTION VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _CLOSED | BB1CV202_CLOSED | <IO NOT ASSIGNED> | Steam pressure reduction valve CLOSED | STEAM PRESSURE REDUCTION | VALVE CLOSED |  | STEAM PRESSURE REDUCTION VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _FAULT | BB1CV202_FAULT | <IO NOT ASSIGNED> | Steam pressure reduction valve FAULT | STEAM PRESSURE REDUCTION | VALVE FAULT |  | STEAM PRESSURE REDUCTION VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _POSITION | BB1CV202_POSITION | <IO NOT ASSIGNED> | Steam pressure reduction valve POSITION | STEAM PRESSURE REDUCTION | VALVE POSITION |  | STEAM PRESSURE REDUCTION VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1IV204 | _OPEN | BB1IV204_OPEN | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve OPEN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV204 | _CLOSE | BB1IV204_CLOSE | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve CLOSE | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV204 | _OPENED | BB1IV204_OPENED | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve OPENED | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPENED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _CLOSED | BB1IV204_CLOSED | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve CLOSED | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _FAULT | BB1IV204_FAULT | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve FAULT | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE FAULT | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _POSITION | BB1IV204_POSITION | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve POSITION | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE POSITION | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV205 | _OPEN | BB1IV205_OPEN | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve OPEN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV205 | _CLOSE | BB1IV205_CLOSE | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve CLOSE | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV205 | _OPENED | BB1IV205_OPENED | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve OPENED | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPENED |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _CLOSED | BB1IV205_CLOSED | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve CLOSED | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSED |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _FAULT | BB1IV205_FAULT | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve FAULT | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE FAULT |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _POSITION | BB1IV205_POSITION | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve POSITION | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE POSITION |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV206 | _OPEN | BB1IV206_OPEN | <IO NOT ASSIGNED> | Primary air preheater on-off valve OPEN | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN |  | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV206 | _CLOSE | BB1IV206_CLOSE | <IO NOT ASSIGNED> | Primary air preheater on-off valve CLOSE | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE |  | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV206 | _OPENED | BB1IV206_OPENED | <IO NOT ASSIGNED> | Primary air preheater on-off valve OPENED | PRIMARY AIR PREHEATER | ON-OFF VALVE OPENED |  | PRIMARY AIR PREHEATER ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _CLOSED | BB1IV206_CLOSED | <IO NOT ASSIGNED> | Primary air preheater on-off valve CLOSED | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSED |  | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _FAULT | BB1IV206_FAULT | <IO NOT ASSIGNED> | Primary air preheater on-off valve FAULT | PRIMARY AIR PREHEATER | ON-OFF VALVE FAULT |  | PRIMARY AIR PREHEATER ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _POSITION | BB1IV206_POSITION | <IO NOT ASSIGNED> | Primary air preheater on-off valve POSITION | PRIMARY AIR PREHEATER | ON-OFF VALVE POSITION |  | PRIMARY AIR PREHEATER ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1FM001 | _ESTOP | BB1FM001_ESTOP | <IO NOT ASSIGNED> | Bottom ash sieve feed ESTOP | BOTTOM ASH SIEVE FEED | ESTOP |  | BOTTOM ASH SIEVE FEED ESTOP | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _RUNNING | BB1FM001_RUNNING | <IO NOT ASSIGNED> | Bottom ash sieve feed RUNNING | BOTTOM ASH SIEVE FEED | RUNNING |  | BOTTOM ASH SIEVE FEED RUNNING | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _MAN_AUTO | BB1FM001_MAN_AUTO | <IO NOT ASSIGNED> | Bottom ash sieve feed MAN/AUTO | BOTTOM ASH SIEVE FEED | MAN/AUTO |  | BOTTOM ASH SIEVE FEED MAN/AUTO | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _FAULT | BB1FM001_FAULT | <IO NOT ASSIGNED> | Bottom ash sieve feed THERMAL FAULT | BOTTOM ASH SIEVE FEED | THERMAL FAULT |  | BOTTOM ASH SIEVE FEED THERMAL FAULT | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _VOLTAGE_OK | BB1FM001_VOLTAGE_OK | <IO NOT ASSIGNED> | Bottom ash sieve feed VOLTAGE OK | BOTTOM ASH SIEVE FEED | VOLTAGE OK |  | BOTTOM ASH SIEVE FEED VOLTAGE OK | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _START_STOP | BB1FM001_START_STOP | <IO NOT ASSIGNED> | Bottom ash sieve feed START/STOP | BOTTOM ASH SIEVE FEED | START/STOP |  | BOTTOM ASH SIEVE FEED START/STOP | FM | MOTOR | DO | OESA_3ph
<005> |  | <005> | <IO NOT ASSIGNED> | Sand transmitter 230 Vac feed | SAND TRANSMITTER | 230 VAC FEED |  | SAND TRANSMITTER 230 VAC FEED | 5> | #N/A |  | #N/A
BB1FG300 | _ESP_COLLECTIVE_ALARM | BB1FG300_ESP_COLLECTIVE_ALARM | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_ALARM | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_COLLECTIVE_WARNING | BB1FG300_ESP_COLLECTIVE_WARNING | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_WARNING | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_IN_STANDBY | BB1FG300_ESP_IN_STANDBY | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_IN_STANDBY | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_IN_STANDBY | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_STANDBY | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_IN_OPERATION | BB1FG300_ESP_IN_OPERATION | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_IN_OPERATION | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_IN_OPERATION | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_OPERATION | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI1 | BB1FG300_ESP_SPARE_DI1 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI1 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI2 | BB1FG300_ESP_SPARE_DI2 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI2 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI3 | BB1FG300_ESP_SPARE_DI3 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI3 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI4 | BB1FG300_ESP_SPARE_DI4 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI4 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_EXT_RELEASE_FILTER | BB1FG300_ESP_EXT_RELEASE_FILTER | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_EXT_RELEASE_FILTER | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO1 | BB1FG300_ESP_SPARE_DO1 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO1 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO2 | BB1FG300_ESP_SPARE_DO2 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO2 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO3 | BB1FG300_ESP_SPARE_DO3 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO3 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO4 | BB1FG300_ESP_SPARE_DO4 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO4 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO5 | BB1FG300_ESP_SPARE_DO5 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO5 | FG | ESP | DO | ESP_DI_DO
BB1SI400 |  | BB1SI400 | <IO NOT ASSIGNED> | Primary air fan safety interlock | PRIMARY AIR FAN | SAFETY INTERLOCK |  | PRIMARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI401 |  | BB1SI401 | <IO NOT ASSIGNED> | Secondary air fan safety interlock | SECONDARY AIR FAN | SAFETY INTERLOCK |  | SECONDARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI603 |  | BB1SI603 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI604 |  | BB1SI604 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI605 |  | BB1SI605 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI658 |  | BB1SI658 | <IO NOT ASSIGNED> | Scraper Conveyor 1 safety interlock | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  | SCRAPER CONVEYOR 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI659 |  | BB1SI659 | <IO NOT ASSIGNED> | Belt Conveyor safety interlock | BELT CONVEYOR | SAFETY INTERLOCK |  | BELT CONVEYOR SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI675 |  | BB1SI675 | <IO NOT ASSIGNED> | Disc screen drive 1 safety interlock | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  | DISC SCREEN DRIVE 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI676 |  | BB1SI676 | <IO NOT ASSIGNED> | Disc screen drive 2 safety interlock | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  | DISC SCREEN DRIVE 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI672 |  | BB1SI672 | <IO NOT ASSIGNED> | Scraper Conveyor 2 safety interlock | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  | SCRAPER CONVEYOR 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI550 |  | BB1SI550 | <IO NOT ASSIGNED> | Flue gas fan safety interlock | FLUE GAS FAN | SAFETY INTERLOCK |  | FLUE GAS FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SV601 | _OUT | BB1SV601_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 1 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV601 | _IN | BB1SV601_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 1 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV603 | _OUT | BB1SV603_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 3 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV603 | _IN | BB1SV603_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 3 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV602 | _OUT | BB1SV602_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 2 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV602 | _IN | BB1SV602_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 2 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1EM603 | _LOCAL_MODE | BB1EM603_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM603 | _LOCAL_RUN | BB1EM603_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM603 | _ISOLATOR | BB1EM603_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _LOCAL_MODE | BB1EM604_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _LOCAL_RUN | BB1EM604_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _ISOLATOR | BB1EM604_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _LOCAL_MODE | BB1EM605_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _LOCAL_RUN | BB1EM605_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _ISOLATOR | BB1EM605_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM658 | _LOCAL_MODE | BB1EM658_LOCAL_MODE | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | SCRAPER CONVEYOR 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _LOCAL_RUN_FWD | BB1EM658_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _LOCAL_RUN_REV | BB1EM658_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_RUN_REV | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  | SCRAPER CONVEYOR 1 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _ISOLATOR | BB1EM658_ISOLATOR | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 ISOLATOR | SCRAPER CONVEYOR 1 | ISOLATOR |  | SCRAPER CONVEYOR 1 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_MODE | BB1EM659_LOCAL_MODE | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_MODE | BELT CONVEYOR | LOCAL_MODE |  | BELT CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_RUN_FWD | BB1EM659_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_RUN_FWD | BELT CONVEYOR | LOCAL_RUN_FWD |  | BELT CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_RUN_REV | BB1EM659_LOCAL_RUN_REV | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_RUN_REV | BELT CONVEYOR | LOCAL_RUN_REV |  | BELT CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _ISOLATOR | BB1EM659_ISOLATOR | <IO NOT ASSIGNED> | BELT CONVEYOR ISOLATOR | BELT CONVEYOR | ISOLATOR |  | BELT CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM675 | _LOCAL_MODE | BB1EM675_LOCAL_MODE | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_MODE | DISC SCREEN DRIVE 1 | LOCAL_MODE |  | DISC SCREEN DRIVE 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _LOCAL_RUN_FWD | BB1EM675_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD | DISC SCREEN DRIVE 1 | LOCAL_RUN_FWD |  | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _LOCAL_RUN_REV | BB1EM675_LOCAL_RUN_REV | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_RUN_REV | DISC SCREEN DRIVE 1 | LOCAL_RUN_REV |  | DISC SCREEN DRIVE 1 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _ISOLATOR | BB1EM675_ISOLATOR | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 ISOLATOR | DISC SCREEN DRIVE 1 | ISOLATOR |  | DISC SCREEN DRIVE 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM676 | _LOCAL_MODE | BB1EM676_LOCAL_MODE | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_MODE | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | DISC SCREEN DRIVE 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _LOCAL_RUN_FWD | BB1EM676_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _LOCAL_RUN_REV | BB1EM676_LOCAL_RUN_REV | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_RUN_REV | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | DISC SCREEN DRIVE 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _ISOLATOR | BB1EM676_ISOLATOR | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 ISOLATOR | DISC SCREEN DRIVE 2 | ISOLATOR |  | DISC SCREEN DRIVE 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_MODE | BB1EM672_LOCAL_MODE | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_MODE | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | SCRAPER CONVEYOR 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_RUN_FWD | BB1EM672_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_RUN_REV | BB1EM672_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_RUN_REV | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | SCRAPER CONVEYOR 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _ISOLATOR | BB1EM672_ISOLATOR | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 ISOLATOR | SCRAPER CONVEYOR 2 | ISOLATOR |  | SCRAPER CONVEYOR 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_MODE | BB1EM662_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_MODE | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | FUEL SILO SCREW DISCHARGE LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_RUN_FWD | BB1EM662_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | FUEL SILO SCREW DISCHARGE LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_RUN_REV | BB1EM662_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | FUEL SILO SCREW DISCHARGE LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _ISOLATOR | BB1EM662_ISOLATOR | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGEISOLATOR | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | FUEL SILO SCREW DISCHARGE ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_MODE | BB1EM650_LOCAL_MODE | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_MODE | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | SLEWING MOTOR FOR SCREW LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_RUN_FWD | BB1EM650_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_RUN_REV | BB1EM650_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _ISOLATOR | BB1EM650_ISOLATOR | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW ISOLATOR | SLEWING MOTOR FOR SCREW | ISOLATOR |  | SLEWING MOTOR FOR SCREW ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_MODE | BB1EM663_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_MODE | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | FUEL SILO CROSS CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_RUN_FWD | BB1EM663_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_RUN_REV | BB1EM663_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _ISOLATOR | BB1EM663_ISOLATOR | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR ISOLATOR | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | FUEL SILO CROSS CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_MODE | BB1EM664_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_MODE | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | FUEL FEEDING SCREW 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_RUN_FWD | BB1EM664_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_RUN_REV | BB1EM664_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_RUN_REV | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | FUEL FEEDING SCREW 1 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _ISOLATOR | BB1EM664_ISOLATOR | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 ISOLATOR | FUEL FEEDING SCREW 1 | ISOLATOR |  | FUEL FEEDING SCREW 1 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_MODE | BB1EM665_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_MODE | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | FUEL FEEDING SCREW 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_RUN_FWD | BB1EM665_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_RUN_REV | BB1EM665_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_RUN_REV | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | FUEL FEEDING SCREW 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _ISOLATOR | BB1EM665_ISOLATOR | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 ISOLATOR | FUEL FEEDING SCREW 2 | ISOLATOR |  | FUEL FEEDING SCREW 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_MODE | BB1EM852_LOCAL_MODE | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_MODE | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | BOTTOM ASH CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_RUN_FWD | BB1EM852_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_RUN_REV | BB1EM852_LOCAL_RUN_REV | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_RUN_REV | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | BOTTOM ASH CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _ISOLATOR | BB1EM852_ISOLATOR | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR ISOLATOR | BOTTOM ASH CONVEYOR | ISOLATOR |  | BOTTOM ASH CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM660 | _RUNNING | BB1EM660_RUNNING | <IO NOT ASSIGNED> | Cooling fan for slewing motor RUNNING | COOLING FAN FOR | SLEWING MOTOR RUNNING |  | COOLING FAN FOR SLEWING MOTOR RUNNING | EM | MOTOR | DI | DOL_DIR
BB1EM660 | _FAULT | BB1EM660_FAULT | <IO NOT ASSIGNED> | Cooling fan for slewing motor FAULT | COOLING FAN FOR | SLEWING MOTOR FAULT |  | COOLING FAN FOR SLEWING MOTOR FAULT | EM | MOTOR | DI | DOL_DIR
BB1EM660 | _RUN | BB1EM660_RUN | <IO NOT ASSIGNED> | Cooling fan for slewing motor RUN | COOLING FAN FOR | SLEWING MOTOR RUN |  | COOLING FAN FOR SLEWING MOTOR RUN | EM | MOTOR | DO | DOL_DIR
BB1EM660 | _ISOLATOR | BB1EM660_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan for slewing motor ISOLATOR | COOLING FAN FOR | SLEWING MOTOR ISOLATOR |  | COOLING FAN FOR SLEWING MOTOR ISOLATOR | EM | MOTOR | DI | DOL_DIR
BB1EM654 | _RUNNING | BB1EM654_RUNNING | <IO NOT ASSIGNED> | Lubrication unit RUNNING | LUBRICATION UNIT RUNNING |  |  | LUBRICATION UNIT RUNNING | EM | MOTOR | DI | DOL_DIR
BB1EM654 | _FAULT | BB1EM654_FAULT | <IO NOT ASSIGNED> | Lubrication unit FAULT | LUBRICATION UNIT FAULT |  |  | LUBRICATION UNIT FAULT | EM | MOTOR | DI | DOL_DIR
BB1EM654 | _RUN | BB1EM654_RUN | <IO NOT ASSIGNED> | Lubrication unit RUN | LUBRICATION UNIT RUN |  |  | LUBRICATION UNIT RUN | EM | MOTOR | DO | DOL_DIR
BB1EM654 | _ISOLATOR | BB1EM654_ISOLATOR | <IO NOT ASSIGNED> | Lubrication unit ISOLATOR | LUBRICATION UNIT ISOLATOR |  |  | LUBRICATION UNIT ISOLATOR | EM | MOTOR | DI | DOL_DIR
BB1EM653 | _RUNNING | BB1EM653_RUNNING | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 RUNNING | COOLING FAN FUEL | FEEDING SCREW 1 RUNNING |  | COOLING FAN FUEL FEEDING SCREW 1 RUNNING | EM | MOTOR | DI | DOL_DIR
BB1EM653 | _FAULT | BB1EM653_FAULT | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 FAULT | COOLING FAN FUEL | FEEDING SCREW 1 FAULT |  | COOLING FAN FUEL FEEDING SCREW 1 FAULT | EM | MOTOR | DI | DOL_DIR
BB1EM653 | _RUN | BB1EM653_RUN | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 RUN | COOLING FAN FUEL | FEEDING SCREW 1 RUN |  | COOLING FAN FUEL FEEDING SCREW 1 RUN | EM | MOTOR | DO | DOL_DIR
BB1EM653 | _ISOLATOR | BB1EM653_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 ISOLATOR | COOLING FAN FUEL | FEEDING SCREW 1 ISOLATOR |  | COOLING FAN FUEL FEEDING SCREW 1 ISOLATOR | EM | MOTOR | DI | DOL_DIR
BB1EM655 | _RUNNING | BB1EM655_RUNNING | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 RUNNING | COOLING FAN FUEL | FEEDING SCREW 2 RUNNING |  | COOLING FAN FUEL FEEDING SCREW 2 RUNNING | EM | MOTOR | DI | DOL_DIR
BB1EM655 | _FAULT | BB1EM655_FAULT | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 FAULT | COOLING FAN FUEL | FEEDING SCREW 2 FAULT |  | COOLING FAN FUEL FEEDING SCREW 2 FAULT | EM | MOTOR | DI | DOL_DIR
BB1EM655 | _RUN | BB1EM655_RUN | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 RUN | COOLING FAN FUEL | FEEDING SCREW 2 RUN |  | COOLING FAN FUEL FEEDING SCREW 2 RUN | EM | MOTOR | DO | DOL_DIR
BB1EM655 | _ISOLATOR | BB1EM655_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 ISOLATOR | COOLING FAN FUEL | FEEDING SCREW 2 ISOLATOR |  | COOLING FAN FUEL FEEDING SCREW 2 ISOLATOR | EM | MOTOR | DI | DOL_DIR
BB1EM606 | _ISOLATOR | BB1EM606_ISOLATOR | <IO NOT ASSIGNED> | Dust extraction fan ISOLATOR | DUST EXTRACTION FAN | ISOLATOR |  | DUST EXTRACTION FAN ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EH600 | _ISOLATOR | BB1EH600_ISOLATOR | <IO NOT ASSIGNED> | Electric heater hydraulic unit ISOLATOR | ELECTRIC HEATER | HYDRAULIC UNIT ISOLATOR |  | ELECTRIC HEATER HYDRAULIC UNIT ISOLATOR | EH | HEATER | DI | DOL_DIR_BUS
BB1EM651 | _ISOLATOR | BB1EM651_ISOLATOR | <IO NOT ASSIGNED> | Fuel silo dust filter fanISOLATOR | FUEL SILO DUST FILTER FAN | ISOLATOR |  | FUEL SILO DUST FILTER FAN ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM008 | _ISOLATOR | BB1EM008_ISOLATOR | <IO NOT ASSIGNED> | Conveyor cooling pump ISOLATOR | CONVEYOR COOLING PUMP | ISOLATOR |  | CONVEYOR COOLING PUMP ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM009 | _ISOLATOR | BB1EM009_ISOLATOR | <IO NOT ASSIGNED> | Bottom ash conveyor heat exchanger fan ISOLATOR | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN ISOLAT | OR | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN ISOLAT OR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM408 | _ISOLATOR | BB1EM408_ISOLATOR | <IO NOT ASSIGNED> | Boiler house heater 1 ISOLATOR | BOILER HOUSE HEATER 1 | ISOLATOR |  | BOILER HOUSE HEATER 1 ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM409 | _ISOLATOR | BB1EM409_ISOLATOR | <IO NOT ASSIGNED> | Boiler house heater 2 ISOLATOR | BOILER HOUSE HEATER 2 | ISOLATOR |  | BOILER HOUSE HEATER 2 ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM703 | _RUNNING | BB1EM703_RUNNING | <IO NOT ASSIGNED> | Chemical filling pump 1 RUNNING | CHEMICAL FILLING PUMP 1 | RUNNING |  | CHEMICAL FILLING PUMP 1 RUNNING | EM | MOTOR | DI | DOL_DIRH
BB1EM703 | _FAULT | BB1EM703_FAULT | <IO NOT ASSIGNED> | Chemical filling pump 1 FAULT | CHEMICAL FILLING PUMP 1 | FAULT |  | CHEMICAL FILLING PUMP 1 FAULT | EM | MOTOR | DI | DOL_DIRH
BB1EM703 | _RUN | BB1EM703_RUN | <IO NOT ASSIGNED> | Chemical filling pump 1 RUN | CHEMICAL FILLING PUMP 1 | RUN |  | CHEMICAL FILLING PUMP 1 RUN | EM | MOTOR | DO | DOL_DIRH
BB1EM703 | _LOCAL_MODE | BB1EM703_LOCAL_MODE | <IO NOT ASSIGNED> | Chemical filling pump 1 LOCAL_MODE | CHEMICAL FILLING PUMP 1 | LOCAL_MODE |  | CHEMICAL FILLING PUMP 1 LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH
BB1EM703 | _LOCAL_RUN | BB1EM703_LOCAL_RUN | <IO NOT ASSIGNED> | Chemical filling pump 1 LOCAL_RUN | CHEMICAL FILLING PUMP 1 | LOCAL_RUN |  | CHEMICAL FILLING PUMP 1 LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH
BB1EM703 | _ISOLATOR | BB1EM703_ISOLATOR | <IO NOT ASSIGNED> | Chemical filling pump 1 ISOLATOR | CHEMICAL FILLING PUMP 1 | ISOLATOR |  | CHEMICAL FILLING PUMP 1 ISOLATOR | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _RUNNING | BB1EM704_RUNNING | <IO NOT ASSIGNED> | Chemical filling pump 2 RUNNING | CHEMICAL FILLING PUMP 2 | RUNNING |  | CHEMICAL FILLING PUMP 2 RUNNING | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _FAULT | BB1EM704_FAULT | <IO NOT ASSIGNED> | Chemical filling pump 2 FAULT | CHEMICAL FILLING PUMP 2 | FAULT |  | CHEMICAL FILLING PUMP 2 FAULT | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _RUN | BB1EM704_RUN | <IO NOT ASSIGNED> | Chemical filling pump 2 RUN | CHEMICAL FILLING PUMP 2 | RUN |  | CHEMICAL FILLING PUMP 2 RUN | EM | MOTOR | DO | DOL_DIRH
BB1EM704 | _LOCAL_MODE | BB1EM704_LOCAL_MODE | <IO NOT ASSIGNED> | Chemical filling pump 2 LOCAL_MODE | CHEMICAL FILLING PUMP 2 | LOCAL_MODE |  | CHEMICAL FILLING PUMP 2 LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _LOCAL_RUN | BB1EM704_LOCAL_RUN | <IO NOT ASSIGNED> | Chemical filling pump 2 LOCAL_RUN | CHEMICAL FILLING PUMP 2 | LOCAL_RUN |  | CHEMICAL FILLING PUMP 2 LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH
BB1EM704 | _ISOLATOR | BB1EM704_ISOLATOR | <IO NOT ASSIGNED> | Chemical filling pump 2 ISOLATOR | CHEMICAL FILLING PUMP 2 | ISOLATOR |  | CHEMICAL FILLING PUMP 2 ISOLATOR | EM | MOTOR | DI | DOL_DIRH
BB1EM670 | _LOCAL_MODE | BB1EM670_LOCAL_MODE | <IO NOT ASSIGNED> | Belt magnet LOCAL_MODE | BELT MAGNET LOCAL_MODE |  |  | BELT MAGNET LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM670 | _LOCAL_RUN | BB1EM670_LOCAL_RUN | <IO NOT ASSIGNED> | Belt magnet LOCAL_RUN | BELT MAGNET LOCAL_RUN |  |  | BELT MAGNET LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM670 | _ISOLATOR | BB1EM670_ISOLATOR | <IO NOT ASSIGNED> | Belt magnet ISOLATOR | BELT MAGNET ISOLATOR |  |  | BELT MAGNET ISOLATOR | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _LOCAL_MODE | BB1EM652_LOCAL_MODE | <IO NOT ASSIGNED> | Rotating fuel spreader LOCAL_MODE | ROTATING FUEL SPREADER | LOCAL_MODE |  | ROTATING FUEL SPREADER LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _LOCAL_RUN | BB1EM652_LOCAL_RUN | <IO NOT ASSIGNED> | Rotating fuel spreader LOCAL_RUN | ROTATING FUEL SPREADER | LOCAL_RUN |  | ROTATING FUEL SPREADER LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _ISOLATOR | BB1EM652_ISOLATOR | <IO NOT ASSIGNED> | Rotating fuel spreader ISOLATOR | ROTATING FUEL SPREADER | ISOLATOR |  | ROTATING FUEL SPREADER ISOLATOR | EM | MOTOR | DI | DOL_DIRH_BUS
BB1BL200 | _ISOLATOR | BB1BL200_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 1 ISOLATOR | SOOTBLOWER 1 ISOLATOR |  |  | SOOTBLOWER 1 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL201 | _ISOLATOR | BB1BL201_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 2 ISOLATOR | SOOTBLOWER 2 ISOLATOR |  |  | SOOTBLOWER 2 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL202 | _ISOLATOR | BB1BL202_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 3 ISOLATOR | SOOTBLOWER 3 ISOLATOR |  |  | SOOTBLOWER 3 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL203 | _ISOLATOR | BB1BL203_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 4 ISOLATOR | SOOTBLOWER 4 ISOLATOR |  |  | SOOTBLOWER 4 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL204 | _ISOLATOR | BB1BL204_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 5 ISOLATOR | SOOTBLOWER 5 ISOLATOR |  |  | SOOTBLOWER 5 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL205 | _ISOLATOR | BB1BL205_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 6 ISOLATOR | SOOTBLOWER 6 ISOLATOR |  |  | SOOTBLOWER 6 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL206 | _ISOLATOR | BB1BL206_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 7 ISOLATOR | SOOTBLOWER 7 ISOLATOR |  |  | SOOTBLOWER 7 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1EM815 | _ISOLATOR | BB1EM815_ISOLATOR | <IO NOT ASSIGNED> | Fly ash container screw ISOLATOR | FLY ASH CONTAINER SCREW I | SOLATOR |  | FLY ASH CONTAINER SCREW I SOLATOR | EM | MOTOR | DI | DOL_REV_BUS
BB1EM855 | _ISOLATOR | BB1EM855_ISOLATOR | <IO NOT ASSIGNED> | Ash container screw ISOLATOR | ASH CONTAINER SCREW ISOLA | TOR |  | ASH CONTAINER SCREW ISOLA TOR | EM | MOTOR | DI | DOL_REV_BUS
BB1EM401 | _ISOLATOR | BB1EM401_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 1 ISOLATOR | EXHAUST FAN 1 ISOLATOR |  |  | EXHAUST FAN 1 ISOLATOR | EM | MOTOR | DI | FRQ_DIR
BB1EM402 |  | BB1EM402 | <IO NOT ASSIGNED> | Exhaust fan 2 | EXHAUST FAN 2 |  |  | EXHAUST FAN 2 | EM | MOTOR | DO | COMPR
BB1EM402 | _ISOLATOR | BB1EM402_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 2 ISOLATOR | EXHAUST FAN 2 ISOLATOR |  |  | EXHAUST FAN 2 ISOLATOR | EM | MOTOR | DO | COMPR
BB1EM403 |  | BB1EM403 | <IO NOT ASSIGNED> | Exhaust fan 3 | EXHAUST FAN 3 |  |  | EXHAUST FAN 3 | EM | MOTOR | DO | COMPR
BB1EM403 | _ISOLATOR | BB1EM403_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 3 ISOLATOR | EXHAUST FAN 3 ISOLATOR |  |  | EXHAUST FAN 3 ISOLATOR | EM | MOTOR | DO | COMPR
BB1EM673 | _LOCAL_MODE | BB1EM673_LOCAL_MODE | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_MODE | LEVELLING ROLLER 1 | LOCAL_MODE |  | LEVELLING ROLLER 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _LOCAL_RUN_FWD | BB1EM673_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_RUN_FWD | LEVELLING ROLLER 1 | LOCAL_RUN_FWD |  | LEVELLING ROLLER 1 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _LOCAL_RUN_REV | BB1EM673_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_RUN_REV | LEVELLING ROLLER 1 | LOCAL_RUN_REV |  | LEVELLING ROLLER 1 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _ISOLATOR | BB1EM673_ISOLATOR | <IO NOT ASSIGNED> | Levelling roller 1 ISOLATOR | LEVELLING ROLLER 1 | ISOLATOR |  | LEVELLING ROLLER 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_MODE | BB1EM674_LOCAL_MODE | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_MODE | LEVELLING ROLLER 2 | LOCAL_MODE |  | LEVELLING ROLLER 2 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_RUN_FWD | BB1EM674_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_RUN_FWD | LEVELLING ROLLER 2 | LOCAL_RUN_FWD |  | LEVELLING ROLLER 2 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_RUN_REV | BB1EM674_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_RUN_REV | LEVELLING ROLLER 2 | LOCAL_RUN_REV |  | LEVELLING ROLLER 2 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _ISOLATOR | BB1EM674_ISOLATOR | <IO NOT ASSIGNED> | Levelling roller 2 ISOLATOR | LEVELLING ROLLER 2 | ISOLATOR |  | LEVELLING ROLLER 2 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_MODE | BB1EM601_LOCAL_MODE | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_MODE | DUST EXTRACTION | ROTARY FEEDER LOCAL_MODE |  | DUST EXTRACTION ROTARY FEEDER LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_RUN_FWD | BB1EM601_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_RUN_FWD | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_F | WD | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_F WD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_RUN_REV | BB1EM601_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_RUN_REV | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_R | EV | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_R EV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _ISOLATOR | BB1EM601_ISOLATOR | <IO NOT ASSIGNED> | Dust extraction rotary feeder ISOLATOR | DUST EXTRACTION | ROTARY FEEDER ISOLATOR |  | DUST EXTRACTION ROTARY FEEDER ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_MODE | BB1IV650_LOCAL_MODE | <IO NOT ASSIGNED> | Slide gate valve LOCAL_MODE | SLIDE GATE VALVE | LOCAL_MODE |  | SLIDE GATE VALVE LOCAL_MODE | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_RUN_FWD | BB1IV650_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Slide gate valve LOCAL_RUN_FWD | SLIDE GATE VALVE | LOCAL_RUN_FWD |  | SLIDE GATE VALVE LOCAL_RUN_FWD | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_RUN_REV | BB1IV650_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Slide gate valve LOCAL_RUN_REV | SLIDE GATE VALVE | LOCAL_RUN_REV |  | SLIDE GATE VALVE LOCAL_RUN_REV | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _ISOLATOR | BB1IV650_ISOLATOR | <IO NOT ASSIGNED> | Slide gate valve ISOLATOR | SLIDE GATE VALVE | ISOLATOR |  | SLIDE GATE VALVE ISOLATOR | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_MODE | BB1EM657_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 1 LOCAL_MODE |  | FUEL FEEDING ROTARY VALVE 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_RUN_FWD | BB1EM657_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | FWD | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_RUN_REV | BB1EM657_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_RUN_REV | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | REV | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _ISOLATOR | BB1EM657_ISOLATOR | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 ISOLATOR | FUEL FEEDING | ROTARY VALVE 1 ISOLATOR |  | FUEL FEEDING ROTARY VALVE 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_MODE | BB1EM656_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 2 LOCAL_MODE |  | FUEL FEEDING ROTARY VALVE 2 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_RUN_FWD | BB1EM656_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | FWD | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_RUN_REV | BB1EM656_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_RUN_REV | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | REV | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _ISOLATOR | BB1EM656_ISOLATOR | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 ISOLATOR | FUEL FEEDING | ROTARY VALVE 2 ISOLATOR |  | FUEL FEEDING ROTARY VALVE 2 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_MODE | BB1EM856_LOCAL_MODE | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_MODE | PURIFIED SAND | SCREW CONVEYOR LOCAL_MODE |  | PURIFIED SAND SCREW CONVEYOR LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_RUN_FWD | BB1EM856_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_RUN_FWD | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | FWD | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_RUN_REV | BB1EM856_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_RUN_REV | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | REV | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _ISOLATOR | BB1EM856_ISOLATOR | <IO NOT ASSIGNED> | Purified sand screw conveyor ISOLATOR | PURIFIED SAND | SCREW CONVEYOR ISOLATOR |  | PURIFIED SAND SCREW CONVEYOR ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_MODE | BB1EM850_LOCAL_MODE | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_MODE | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  | 2ND PASS FLY ASH ROTARY VALVE LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_RUN_FWD | BB1EM850_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_RUN_ FWD | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_RUN_REV | BB1EM850_LOCAL_RUN_REV | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_RUN_ REV | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | REV | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _ISOLATOR | BB1EM850_ISOLATOR | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve ISOLATOR | 2ND PASS FLY ASH | ROTARY VALVE ISOLATOR |  | 2ND PASS FLY ASH ROTARY VALVE ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_MODE | BB1EM851_LOCAL_MODE | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_MODE | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  | 3RD PASS FLY ASH ROTARY VALVE LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_RUN_FWD | BB1EM851_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_RUN_ FWD | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_RUN_REV | BB1EM851_LOCAL_RUN_REV | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_RUN_ REV | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | REV | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _ISOLATOR | BB1EM851_ISOLATOR | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve ISOLATOR | 3RD PASS FLY ASH | ROTARY VALVE ISOLATOR |  | 3RD PASS FLY ASH ROTARY VALVE ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
|  | <BB1TX001> | <IO NOT ASSIGNED> | BIOMASS BOILER SITE TRANSFORMER | BIOMASS BOILER | SITE TRANSFORMER |  | BIOMASS BOILER SITE TRANSFORMER |  | 0 |  | #N/A
|  | <BB1SA001> | <IO NOT ASSIGNED> | SUREGE ARRESTOR | SUREGE ARRESTOR |  |  | SUREGE ARRESTOR |  | 0 |  | #N/A

## C_CABLE
Cables
_Tag | _Typical | CableName1 | Cable1CatN | Cable1CatD | CableName2 | Cable2CatN | Cable2CatD | CableName3 | Cable3CatN | Cable3CatD | CableName4 | Cable4CatN | Cable4CatD
BB1EM658 | FRQ_REVH | BB1EM658/01 |  |  | BB1EM658/02 |  |  | BB1EM658/03
BB1EM659 | FRQ_REVH | BB1EM659/01 |  |  | BB1EM659/02 |  |  | BB1EM659/03
BB1EM676 | FRQ_REVH | BB1EM676/01 |  |  | BB1EM676/02 |  |  | BB1EM676/03
BB1EM672 | FRQ_REVH | BB1EM672/01 |  |  | BB1EM672/02 |  |  | BB1EM672/03
BB1EM662 | FRQ_REVH | BB1EM662/01 |  |  | BB1EM662/02 |  |  | BB1EM662/03
BB1EM650 | FRQ_REVH | BB1EM650/01 |  |  | BB1EM650/02 |  |  | BB1EM650/03
BB1EM663 | FRQ_REVH | BB1EM663/01 |  |  | BB1EM663/02 |  |  | BB1EM663/03
BB1EM664 | FRQ_REVH | BB1EM664/01 |  |  | BB1EM664/02 |  |  | BB1EM664/03
BB1EM665 | FRQ_REVH | BB1EM665/01 |  |  | BB1EM665/02 |  |  | BB1EM665/03
BB1EM852 | FRQ_REVH | BB1EM852/01 |  |  | BB1EM852/02 |  |  | BB1EM852/03
BB1EM658 | FRQ_REVH | BB1EM658/01 |  |  | BB1EM658/02 |  |  | BB1EM658/03
BB1EM659 | FRQ_REVH | BB1EM659/01 |  |  | BB1EM659/02 |  |  | BB1EM659/03
BB1EM676 | FRQ_REVH | BB1EM676/01 |  |  | BB1EM676/02 |  |  | BB1EM676/03
BB1EM672 | FRQ_REVH | BB1EM672/01 |  |  | BB1EM672/02 |  |  | BB1EM672/03
BB1EM662 | FRQ_REVH | BB1EM662/01 |  |  | BB1EM662/02 |  |  | BB1EM662/03
BB1EM650 | FRQ_REVH | BB1EM650/01 |  |  | BB1EM650/02 |  |  | BB1EM650/03
BB1EM663 | FRQ_REVH | BB1EM663/01 |  |  | BB1EM663/02 |  |  | BB1EM663/03
BB1EM664 | FRQ_REVH | BB1EM664/01 |  |  | BB1EM664/02 |  |  | BB1EM664/03
BB1EM665 | FRQ_REVH | BB1EM665/01 |  |  | BB1EM665/02 |  |  | BB1EM665/03
BB1EM852 | FRQ_REVH | BB1EM852/01 |  |  | BB1EM852/02 |  |  | BB1EM852/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 | X-3C+E | XXXmm^2 - 3C+E | 0/02 | X-3C+E-V | XXXmm^2 - 3C+E - VSD | 0/03 | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
0 | #N/A | 0/01 |  |  | 0/02 |  |  | 0/03
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!
#VALUE! | #VALUE! |  |  |  | #VALUE! |  |  | #VALUE!

## _LookupTables
Code | Type
IL | ALARM |  | Channel | IOTerminal | Type | CatN | CatD2 | CatD | ChannelIndex | LoopNameA | LoopTerminalA | LoopNameB | LoopTerminalB | GndName | GndTerminal | MaxIndex | T1 | T2 | T3 | T1Type | T2Type | T3Type
IJ | ALARM |  | 0 | 0 | DI | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D | 0 | V+ | 1 | [5 empty] | V+ | 0 |  | 24VDC | DI
EM | MOTOR |  | 1 | 2 | DI | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D | 1 | V+ | 3 | [5 empty] | V+ | 1 |  | 24VDC | DI
GS | GATE SWITCH |  | 2 | 4 | DI | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D | 2 | V+ | 5 | [5 empty] | V+ | 2 |  | 24VDC | DI
SV | SOLENOID VALVE |  | 3 | 6 | DI | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D | 3 | V+ | 7 |  |  |  |  | TRUE | V+ | 3 |  | 24VDC | DI
IV | ISOLATING VALVE |  | 0 | 0 | DO | 1734-OB4E*M1 | Digital Output 1 (00,06) | 1734-OB4E | 0 | V- | 4 | [5 empty] | 0 | V- |  | DO | 0VDC
CV | CONTROL VALVE |  | 1 | 1 | DO | 1734-OB4E*M2 | Digital Output 2 (01,07) | 1734-OB4E | 1 | V- | 5 | [5 empty] | 1 | V- |  | DO | 0VDC
BU | BURNER |  | 2 | 2 | DO | 1734-OB4E*M3 | Digital Output 3 (02,04) | 1734-OB4E | 2 | V- | 6 | [5 empty] | 2 | V- |  | DO | 0VDC
PU | PUMP |  | 3 | 3 | DO | 1734-OB4E*M4 | Digital Output 4 (03,05) | 1734-OB4E | 3 | V- | 7 |  |  |  |  | TRUE | 3 | V- |  | DO | 0VDC
DM | DAMPER |  | 0 | 0 | AI | 1734-IE8C#MOP-8AI*M1 | Analog Input 1 (0.24,I0,0.SHD) | 1734-IE8C | 0 | [7 empty] | 0 |  |  | AI
PT | PRESSURE TRANSMITTER |  | 1 | 1 | AI | 1734-IE8C#MOP-8AI*M2 | Analog Input 2 (1.24,I1,1.SHD) | 1734-IE8C | 1 | [7 empty] | 1 |  |  | AI
LT | LEVEL TRANSMITTER |  | 2 | 2 | AI | 1734-IE8C#MOP-8AI*M3 | Analog Input 3 (2.24,I2,2.SHD) | 1734-IE8C | 2 | [7 empty] | 2 |  |  | AI
FT | FLOW TRANSMITTER |  | 3 | 3 | AI | 1734-IE8C#MOP-8AI*M4 | Analog Input 4 (3.24,I3,3.SHD) | 1734-IE8C | 3 | [7 empty] | 3 |  |  | AI
TT | TEMPERATURE TRANSMITTER |  | 4 | 4 | AI | 1734-IE8C#MOP-8AI*M5 | Analog Input 5 (4.24,I4,4.SHD) | 1734-IE8C | 4 | [7 empty] | 4 |  |  | AI
QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | 5 | 5 | AI | 1734-IE8C#MOP-8AI*M6 | Analog Input 6 (5.24,I5,5.SHD) | 1734-IE8C | 5 | [7 empty] | 5 |  |  | AI
TS | TEMPERATURE SWITCH |  | 6 | 6 | AI | 1734-IE8C#MOP-8AI*M7 | Analog Input 7 (6.24,I6,6.0) | 1734-IE8C | 6 | [7 empty] | 6 |  |  | AI
LS | LEVEL SWITCH |  | 7 | 7 | AI | 1734-IE8C#MOP-8AI*M8 | Analog Input 8 (7.24,I7,7.SHD) | 1734-IE8C | 7 | [6 empty] | TRUE | 7 |  |  | AI
PS | PRESSURE SWITCH |  | 0 | 0 | AO | 1734-OE2C*M1 | Analog Output 1 (00,04,02) | 1734-OE2C | 0 | V- | 4 | V+ | 6 | SH | 2 |  | 0 | V- | V+ | AO | 0VDC | 24VDC
ST | SPEED SWITCH/ROTATION GUARD |  | 1 | 1 | AO | 1734-OE2C*M2 | Analog Output 2 (01,05,03) | 1734-OE2C | 1 | V- | 5 | V+ | 7 | SH | 3 | TRUE | 1 | V- | V+ | AO | 0VDC | 24VDC
FS | FLOW SWITCH
HS | EMERGENCY STOP
FM | MOTOR
FL | FILTER
EH | HEATER
DR | DRYER
CP | CONTROL PANEL?
FG | ESP
SI | SAFETY INTERLOCK
BL | BLOWER
Type | CatD | ShortCat
DI | 1734-IB4D | IB4D
DO | 1734-OB4E | OB4E
AI | 1734-IE8C | IE8C
AO | 1734-OE2C | OE2C

## prototype V6 spec
Object Name
objPrefix | objIndex | Column1 | objDesc |  | prefix | index | seperator | attribute | suffix | delimiter | result
P | 0 |  | numbered PLC IO block placeholder |  | P | 1 | _ | NAME |  |  | P1_NAME
D | 0 |  | numbered Device block placeholder |  | D | 1
C | 0 |  | numbered Cable block placeholder |  | C | 1
X | 0 |  | numbered PANEL block place holder |  | X | 1 |  | XIO | TI | _
VS | 0 |  | numbered VSD block placeholder |  | VS | 1
SS | 0 |  | numbered Soft Starter block placeholder |  | SS | 1
IS | 0 |  | numbered ISOLATOR block placeholder |  | IS | 1
Q | 0 |  | numbered PROTECTION block placeholder |  | Q | 1
W |  |  | WIRE
M | 0 |  | numbered MOTOR block placeholder |  | M | 1
Object Attribute |  |  |  | len
Column1 | Column2 | Column3 | Column4 | 4
NAME |  | NAME |  | 4
SLOT |  | SLOT |  | 4 | DRAWING
CHAN |  | CHAN |  | 3 | PROTOTYPE
TAG |  | TAG |  | 5 | X1_PNL
DESC2 |  | DESC2 |  | 5 | X1_PDESC
DESC3 |  | DESC3 |  | 5 | X1_24DC
DESC4 |  | DESC4 |  | 3 | X1_0DC
TAG |  | TAG | 0 | 3 | X1_24ACL
PNL |  | PNL |  | 3 | X1_24ACN
MFG |  | MFG |  | 4 | X1_230ACL1
CATN |  | CATN |  | 4 | X1_230ACN
CATD |  | CATD |  | 3 | X1_XIO
XIO |  | XIO | 0 | 6 | X1_XIO_TI
XIO | TI | XIO_TI |  | 6 | X1_XIO_FI
XIO | FI | XIO_FI |  | 6 | X1_XIO_KI
XIO | KI | XIO_KI |  | 3 | X1_XDB
XDB |  | XDB |  | 6 | X1_XDB_TI
XDB | TI | XDB_TI |  | 6 | X1_XDB_FI
XDB | FI | XDB_FI |  | 6 | X1_XDB_KI
XDB | KI | XDB_KI |  | 6 | X2_PNL
XDB | QI | XDB_QI |  | 5 | X2_PDESC
24VDC |  | 24VDC |  | 4 | X2_24DC
0VDC |  | 0VDC |  | 5 | X2_0DC
24VAC |  | 24VAC |  | 7 | X2_24ACL
24VAC | N | 24VAC_N |  | 7 | X2_24ACN
230V | L1 | 230V_L1 |  | 7 | X2_230ACL1
230V | L2 | 230V_L2 |  | 7 | X2_230ACN
230V | L3 | 230V_L3 |  | 6 | X2_XIO
230V | N | 230V_N |  | #REF! | X2_XIO_TI
TYPE |  | TYPE |  | 4 | X2_XIO_FI
|  |  |  | 0 | X2_XIO_KI
|  |  |  | 0 | X2_XDB
DWG | PREFIX | DWG_PREFIX |  | 10 | X2_XDB_TI
DWG | NUMBER | DWG_NUMBER |  | 10 | X2_XDB_FI
DRAWING |  | DRAWING |  | 7 | X2_XDB_KI
PROTOTYPE |  | PROTOTYPE |  | 9 | P1_NAME
CABLE | TYPE | CABLE_TYPE |  | 10 | P1_RACK
CABLE | DESC | CABLE_DESC |  | 10 | P1_SLOT
|  | 0 |  | 1 | P1_CHAN
|  | 0 |  | 1 | P1_MFG
SET_TO |  | SET_TO |  | 6 | P1_CATN
KW |  | KW |  | 2 | P1_CATD
AMPS |  | AMPS |  | 4 | P1_TAG
VOLTS |  | VOLTS |  | 5 | P1_DESC2
|  |  |  | 0 | P1_DESC3
P1_DESC4
Generic Power Cable Spec |  |  |  |  | P1_T1
VoltageRating | insulation | Cores | Size | Column1 | P1_T2
300/500 | PVC | 1 | 1.5 | Neutral-Screen | P2_NAME
0.6/1kV | XPLE | 36 |  | VSD | P2_RACK
|  |  |  | SWA | P2_SLOT
|  |  |  | FLEX | P2_CHAN
P2_MFG
P2_CATN
P2_CATD
P2_TAG
PVC | P |  |  |  | P2_DESC2
XPLE | X |  |  |  | P2_DESC3
Neutral Screen | NS |  |  |  | P2_DESC4
Steel-Wire-Armour | S |  |  |  | P2_T1
Flex | F |  |  |  | D1_TAG
Marine | M |  |  |  | D1_DESC2
D1_DESC3
Seperator: | - |  |  |  | D1_DESC4
D1_VDESC
VoltageRating | Examples | Description | NOTES |  | D1_TYPE
0 | 120V RMS | Instrumentation/Comms cables. Use for Extra Low Voltage Only |  |  | D1_T1
1 | 300/500 0.6/1kV | Suitible for general 230/400V applications |  |  | D1_T2
2 | >1kV | MV,HV Cables |  |  | D2_TAG
D2_DESC2
Insulation | Examples | Description | NOTES |  | D2_DESC3
P | TPS, R75 | General purpose cable. 75deg max |  |  | D2_DESC4
X | XPLE, R90 | Suitible for general 230/400V applications |  |  | D2_VDESC
X+ |  | Hi temp cable suitible for eg. 120, 150 degrees |  |  | D2_TYPE
D2_T1
D2_T2
Cores | Examples | Description | NOTES |  | C1_MFG
[n]C |  | Number of cores |  |  | C1_CATN
[n]PR |  | Number of Pairs |  |  | C1_CATD
+E |  | plus earth |  |  | C1_TAG
C1_COR1
Properties | Examples | Description | NOTES |  | C1_COR2
V |  | VSD Cable | Can include any number of entries. Can be ommited if not applicible |  | C2_MFG
N |  | Neutral-Screen |  |  | C2_CATN
A |  | Steel-Wire Armour |  |  | C2_CATD
F |  | Flexible |  |  | C2_TAG
M |  | Marine Rated |  |  | C2_COR1
T |  | Twisted-Pair? |  |  | C2_COR2
S |  | Shielded?
Examples
| 0P-3PR-S-1.5 | Instrumentation PVC 3 Pair shielded cable, 1.5mm^2
| 2X-3C+E-VF-35 | Power XPLE 3C+E Flexible VSD cable, 35mm

## MSIO
[10 empty] | MSIO-list | [26 empty] | Date |  | Name |  |  |  | Remarks | [23 empty] | New data with green | Changes with yellow |  | Revision
Revision 3
| Basic information | [8 empty] | Motor | [8 empty] | Supply | [7 empty] | I/O | [9 empty] | Scale |  |  | PLC I/O ( Process) |  |  |  | SIS I/O (Safety) |  |  |  | Bus I/O - Register |  |  |  | Alarm threshold |  |  |  | Instrument |  |  |  | Device |  |  | Supplier | Documentation |  |  | Location |  | Revision
Adresses
Row index | Area | Process | Device | Equipment | TAG | Description | Description 2. language | Short Description (n char) | Column1 | Power (kW) | Current (A) | Speed (rpm) | Voltage (V) | Cos φ | Thermistor | ATEX | Column2 | Column3 | Electrical center | Cubicle | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Signal suffix | W | Signal TAG | Column10 | Column11 | Rack | Slot | Chan. | Addr. | Term. | Min | Max | Unit | DI | DO | AI | AO | SDI | SDO | SAI | SAO | BDI | BDO | BAI | BAO | LL | L | H | HH | Transmitter type | Type of signal | Switch state | Voltage | Manufacturer | Model | Connection | Name | P&ID | Typical | Hook-up | Electrical room | Cabinet | Remarks | Issue
0 |  | BB1 | EM | 001 | BB1EM001 | Feed water pump 1 |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Sulzer/ABB | 4001 | FRQ_DIR |  |  |  | Tag changed | 3
1 | [27 empty] | Running | BB1PU001 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
2 | [27 empty] | MCC Fault | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
3 | [27 empty] | Safety switch | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
4 | [27 empty] | VFD Alarm | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
5 | [27 empty] | Run command | BB1PU001 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
6 | [27 empty] | Current | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
7 | [27 empty] | Speed reference | BB1PU001 | [21 empty] | X | [13 empty] | FRQ_DIR
8 | [27 empty] | Actual speed | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
9 | [27 empty] | Torque | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
10 | [27 empty] | RPM | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
11 |  | BB1 | EM | 002 | BB1EM002 | Feed water pump 2 |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Sulzer/ABB | 4001 | FRQ_DIR |  |  |  | Tag changed | 3
12 | [27 empty] | Running | BB1PU002 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
13 | [27 empty] | MCC Fault | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
14 | [27 empty] | Safety switch | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
15 | [27 empty] | VFD Alarm | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
16 | [27 empty] | Run command | BB1PU002 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
17 | [27 empty] | Current | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
18 | [27 empty] | Speed reference | BB1PU002 | [21 empty] | X | [13 empty] | FRQ_DIR
19 | [27 empty] | Actual speed | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
20 | [27 empty] | Torque | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
21 | [27 empty] | RPM | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
873 |  | BB1 | EM | 703 | BB1EM703 | Chemical filling pump 1 |  | Best guess < 1kW |  |  |  |  | 240 | [26 empty] | 4 | 1 | [22 empty] | 4001 | DOL_DIRH |  |  |  | Pump added | 3
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local run command | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local mode switch | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
873 |  | BB1 | EM | 704 | BB1EM704 | Chemical filling pump 2 |  | Best guess < 1kW |  |  |  |  | 240 | [26 empty] | 4 | 1 | [22 empty] | 4001 | DOL_DIRH |  |  |  | Pump added | 3
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local run command | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local mode switch | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
22 |  | BB1 | PU | 800 | BB1PU800 | Chemical dosing pump 1 |  |  |  | 0.37 |  |  | 230 | [29 empty] | 1 | [20 empty] | 4001 | CHEMICAL_PUMP |  | Field IO |  | Motor details | 1
23 | [27 empty] | Control signal | BB1PU800 | [13 empty] | X | [21 empty] | CHEMICAL_PUMP |  | Field IO
28 |  | BB1 | LS | 700 | BB1LS700 | Chemical tank 1 level switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | LS001 | Field IO |  | Instrument added | 1
29 | [27 empty] | Binary State | BB1LT001 | [10 empty] | X | [24 empty] | MEAS_BIN |  | Field IO
24 |  | BB1 | PU | 801 | BB1PU801 | Chemical dosing pump 2 |  |  |  | 0.37 |  |  | 230 | [29 empty] | 1 | [20 empty] | 4001 | CHEMICAL_PUMP |  | Field IO |  | Motor details | 1
25 | [27 empty] | Control signal | BB1PU801 | [13 empty] | X | [21 empty] | CHEMICAL_PUMP |  | Field IO
28 |  | BB1 | LS | 701 | BB1LS701 | Chemical tank 2 level switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | LS001 | Field IO |  | Instrument added | 1
29 | [27 empty] | Binary State | BB1LT001 | [10 empty] | X | [24 empty] | MEAS_BIN |  | Field IO
26 |  | BB1 | PT | 200 | BB1PT200 | Feed water tank pressure | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [13 empty] | Pressure |  |  |  | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
27 | [27 empty] | Measurement | BB1PT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
28 |  | BB1 | LT | 001 | BB1LT001 | Feed water tank level 1 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | LT001 | Field IO
29 | [27 empty] | Measurement | BB1LT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
30 |  | BB1 | LT | 002 | BB1LT002 | Feed water tank level 2 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | LT001 | Field IO
31 | [27 empty] | Measurement | BB1LT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
32 |  | BB1 | PT | 005 | BB1PT005 | Feed water pressure after valve | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
33 | [27 empty] | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
34 |  | BB1 | FT | 001 | BB1FT001 | Feed water flow and control | [35 empty] | 1 | [21 empty] | 4001 | MEAS_ANA | FT002 | Field IO
35 | [27 empty] | Measurement | BB1FT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
36 |  | BB1 | CV | 200 | BB1CV200 | Steam from drum control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
37 | [27 empty] | Setpoint position | BB1CV200 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
38 | [27 empty] | Position feedback | BB1CV200 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
39 |  | BB1 | TT | 001 | BB1TT001 | Feed water temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4001 | MEAS_ANA | TT001 | Field IO
40 | [27 empty] | Measurement | BB1TT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
41 |  | BB1 | IV | 002 | BB1IV002 | Feedwater pump 1 on-off valve |  |  |  | 0.25 | 1.9 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA10.2-22 + RWG |  | Konwell/Auma | 4001 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
43 |  | BB1 | TT | 002 | BB1TT002 | Feed water pump 2 bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
44 | [27 empty] | Measurement | BB1TT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
45 |  | BB1 | GS | 004 | BB1GS004 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
46 | [27 empty] | Binary state | BB1GS004 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
47 |  | BB1 | PT | 004 | BB1PT004 | Feed water pressure before valve | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
48 | [27 empty] | Measurement | BB1PT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
49 |  | BB1 | GS | 003 | BB1GS003 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
50 | [27 empty] | Binary state | BB1GS003 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
51 |  | BB1 | IV | 003 | BB1IV003 | Feed water pump 2 on-off valve |  |  |  | 0.25 | 1.9 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA10.2-22 + RWG |  | Konwell/Auma | 4001 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
53 |  | BB1 | PT | 002 | BB1PT002 | Feed water pump 2 pressure side pressure | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
54 | [27 empty] | Measurement | BB1PT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
55 |  | BB1 | CV | 001 | BB1CV001 | Make-up water control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
56 | [27 empty] | Setpoint position | BB1CV001 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
57 | [27 empty] | Position feedback | BB1CV001 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
58 |  | BB1 | PT | 006 | BB1PT006 | FW suction line strainer pressure diff. | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67LGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | PT004 | Field IO
59 | [27 empty] | Measurement | BB1PT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
60 |  | BB1 | GS | 001 | BB1GS001 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
61 | [27 empty] | Binary state | BB1GS001 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
62 |  | BB1 | PT | 007 | BB1PT007 | FW suction line strainer pressure diff. | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67LGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | PT004 | Field IO
63 | [27 empty] | Measurement | BB1PT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
64 |  | BB1 | TT | 005 | BB1TT005 | FW pump 2 motor winding temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
65 | [27 empty] | Measurement | BB1TT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
66 |  | BB1 | PT | 001 | BB1PT001 | Feed water pump 1 pressure side pressure | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
67 | [27 empty] | Measurement | BB1PT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
68 |  | BB1 | GS | 002 | BB1GS002 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
69 | [27 empty] | Binary state | BB1GS002 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
70 |  | BB1 | CV | 002 | BB1CV002 | Feed water control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
71 | [27 empty] | Setpoint position | BB1CV002 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
72 | [27 empty] | Position feedback | BB1CV002 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
73 |  | BB1 | TT | 004 | BB1TT004 | FW pump 1 motor winding temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
74 | [27 empty] | Measurement | BB1TT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
75 |  | BB1 | TT | 003 | BB1TT003 | FW pump 1 motor bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA |  | Field IO
76 | [27 empty] | Measurement | BB1TT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
77 |  | BB1 | SV | 410 | BB1SV410 | Feed water tank overflow valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4001 | BIN_VLV | AA005 | Field IO |  | tag changed | 1
78 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1IV001 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | 24 VDC feed added | 1
79 |  | BB1 | GS | 005 | BB1GS005 | FW tank overflow On-Off valve position | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
80 | [27 empty] | Binary state | BB1GS005 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
81 |  | BB1 | GS | 006 | BB1GS006 | FW tank overflow On-Off valve position | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
82 | [27 empty] | Binary state | BB1GS006 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
83 |  | BB1 | GS | 007 | BB1GS007 | Feedwater pump 1 on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
84 | [27 empty] | Binary state | BB1GS007 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
85 |  | BB1 | GS | 008 | BB1GS008 | Feedwater pump 1 on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
86 | [27 empty] | Binary state | BB1GS008 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
87 |  | BB1 | GS | 009 | BB1GS009 | Feed water pump 2 on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
88 | [27 empty] | Binary state | BB1GS009 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
89 |  | BB1 | GS | 010 | BB1GS010 | Feed water pump 2 on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
90 | [27 empty] | Binary state | BB1GS010 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
91 |  | BB1 | LT | 101 | BB1LT101 | Steam drum level 1 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
92 | [27 empty] | Measurement SRS | BB1LS100 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
91 |  | BB1 | LS | 103 | BB1LS103 | Steam drum level switch 1 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | LS003 | SRS |  | Instrument added | 2
92 | [27 empty] | Binary state SRS | BB1LS100 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Instrument added | 2
91 |  | BB1 | LS | 104 | BB1LS104 | Steam drum level switch 2 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | LS003 | SRS |  | Instrument added | 2
92 | [27 empty] | Binary state SRS | BB1LS100 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Instrument added | 2
93 |  | BB1 | IV | 004 | BB1IV004 | Boiler bottom blow down on-off valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4002 | BIN_VLV | AA005 | Field IO
94 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1IV004 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | 24 VDC feed added | 1
83 |  | BB1 | GS | 011 | BB1GS011 | Boiler bottom blow down on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 1
84 | [27 empty] | Binary state | BB1GS007 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
85 |  | BB1 | GS | 012 | BB1GS012 | Boiler bottom blow down on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 1
86 | [27 empty] | Binary state | BB1GS008 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
95 |  | BB1 | PT | 203 | BB1PT203 | Steam drum pressure 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4002 | MEAS_ANA_SRS | PT001.1 | SRS
96 | [27 empty] | Measurement SRS | BB1PT203 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
97 |  | BB1 | TT | 008 | BB1TT008 | Temperature after economizer | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4002 | MEAS_ANA | TT001 | Field IO
98 | [27 empty] | Measurement | BB1TT008 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
99 |  | BB1 | LT | 102 | BB1LT102 | Steam drum level 2 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
100 | [27 empty] | Measurement SRS | BB1LS101 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
101 |  | BB1 | PT | 201 | BB1PT201 | Steam drum pressure 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4002 | MEAS_ANA_SRS | PT001.1 | SRS
102 | [27 empty] | Measurement SRS | BB1PT201 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
103 |  | BB1 | LT | 103 | BB1LT103 | Steam drum level 3 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
104 | [27 empty] | Measurement SRS | BB1LS102 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
105 |  | BB1 | FT | 200 | BB1FT200 | Heating steam to feed water tank flow measurement | [30 empty] | 0 | 5 | t/h |  |  | 1 | [21 empty] | 4002 | MEAS_ANA | FT001 | Field IO
106 | [27 empty] | Measurement | BB1FT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
107 |  | BB1 | HS | 101 | BB1HS101 | Boiler emergency shutdown switch 1 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
108 | [27 empty] | Binary state SRS | BB1HS101 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
109 |  | BB1 | HS | 103 | BB1HS103 | Boiler emergency shutdown switch 3 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
111 |  | BB1 | TT | 009 | BB1TT009 | Temperature before economizer | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4002 | MEAS_ANA | TT001 | Field IO
112 | [27 empty] | Measurement | BB1TT009 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
113 |  | BB1 | HS | 104 | BB1HS104 | Boiler emergency shutdown switch 4 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
114 | [27 empty] | Binary state SRS | BB1HS104 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
115 |  | BB1 | HS | 102 | BB1HS102 | Boiler emergency shutdown switch 2 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
116 | [27 empty] | Binary state SRS | BB1HS102 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
117 |  | BB1 | HS | 105 | BB1HS105 | Boiler emergency shutdown switch 5 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
118 | [27 empty] | Binary state SRS | BB1HS105 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
119 |  | BB1 | HS | 106 | BB1HS106 | Boiler emergency shutdown switch 6 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
120 | [27 empty] | Binary state SRS | BB1HS106 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
121 |  | BB1 | HS | 107 | BB1HS107 | Boiler emergency shutdown switch 7 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
122 | [27 empty] | Binary state SRS | BB1HS107 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
123 |  | BB1 | HS | 108 | BB1HS108 | Boiler emergency shutdown switch 8 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
124 | [27 empty] | Binary state SRS | BB1HS108 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
125 |  | BB1 | HS | 109 | BB1HS109 | Boiler emergency shutdown switch 9 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
126 | [27 empty] | Binary state SRS | BB1HS109 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
127 |  | BB1 | HS | 110 | BB1HS110 | Boiler emergency shutdown switch 10 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
128 | [27 empty] | Binary state SRS | BB1HS110 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
129 |  | BB1 | HS | 111 | BB1HS111 | Boiler emergency shutdown switch 11 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
130 | [27 empty] | Binary state SRS | BB1HS111 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
131 |  | BB1 | HS | 112 | BB1HS112 | Boiler emergency shutdown switch 12 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
132 | [27 empty] | Binary state SRS | BB1HS112 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
133 |  | BB1 | TT | 200 | BB1TT200 | Main steam temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4003 | MEAS_ANA | TT001 | Field IO
134 | [27 empty] | Measurement | BB1TT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
135 |  | BB1 | FT | 202 | BB1FT202 | Main steam flow | [30 empty] | 0 | 30 | t/h |  |  | 1 | [21 empty] | 4003 | MEAS_ANA | FT001 | Field IO
136 | [27 empty] | Measurement | BB1FT202 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
137 |  | BB1 | IV | 202 | BB1IV202 | Main steam valve by-pass valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
138 | [27 empty] | Open direction command | BB1IV202 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
139 | [27 empty] | Close direction command | BB1IV202 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
140 | [27 empty] | Torque limit open direction | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
141 | [27 empty] | Torque limit close direction | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
142 | [27 empty] | Actuator fault | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
143 | [27 empty] | Position | BB1IV202 | [12 empty] | X | [22 empty] | MTR_VLV
144 |  | BB1 | CV | 201 | BB1CV201 | Start-up valve |  |  |  | 0.06 | 0.6 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SAR10.2 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
145 | [27 empty] | Open direction command | BB1CV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
146 | [27 empty] | Close direction command | BB1CV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
147 | [27 empty] | Torque limit open direction | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
148 | [27 empty] | Torque limit close direction | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
149 | [27 empty] | Actuator fault | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
150 | [27 empty] | Position | BB1CV201 | [12 empty] | X | [22 empty] | MTR_VLV
151 |  | BB1 | IV | 201 | BB1IV201 | Main steam valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA14.2-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
152 | [27 empty] | Open direction command | BB1IV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
153 | [27 empty] | Close direction command | BB1IV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
154 | [27 empty] | Torque limit open direction | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
155 | [27 empty] | Torque limit close direction | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
156 | [27 empty] | Actuator fault | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
157 | [27 empty] | Position | BB1IV201 | [12 empty] | X | [22 empty] | MTR_VLV
158 |  | BB1 | FT | 201 | BB1FT201 | Steam flow to sootblowing and air preheater | [30 empty] | 0 | 8 | t/h |  |  | 1 | [21 empty] | 4003 | MEAS_ANA | FT001 | Field IO
159 | [27 empty] | Measurement | BB1FT201 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
160 |  | BB1 | IV | 200 | BB1IV200 | Start-up check valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
167 |  | BB1 | GS | 221 | BB1GS221 | Main steam valve by-pass open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
168 | [27 empty] | Binary state | BB1GS221 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
169 |  | BB1 | GS | 222 | BB1GS222 | Main steam valve by-pass close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
170 | [27 empty] | Binary state | BB1GS222 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
171 |  | BB1 | GS | 223 | BB1GS223 | Main steam line valve open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
172 | [27 empty] | Binary state | BB1GS223 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
173 |  | BB1 | GS | 224 | BB1GS224 | Main steam line valve close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
174 | [27 empty] | Binary state | BB1GS224 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
175 |  | BB1 | GS | 225 | BB1GS225 | Start-up line ON-OFF valve open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
176 | [27 empty] | Binary state | BB1GS225 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
177 |  | BB1 | GS | 226 | BB1GS226 | Start-up line ON-OFF valve close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
178 | [27 empty] | Binary state | BB1GS226 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
179 |  | BB1 | GS | 200 | BB1GS200 | Sootblower 1 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
180 | [27 empty] | Binary state | BB1GS200 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
181 |  | BB1 | GS | 201 | BB1GS201 | Sootblower 1 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
182 | [27 empty] | Binary state | BB1GS201 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
183 |  | BB1 | GS | 203 | BB1GS203 | Sootblower 2 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
184 | [27 empty] | Binary state | BB1GS203 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
185 |  | BB1 | GS | 204 | BB1GS204 | Sootblower 2 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
186 | [27 empty] | Binary state | BB1GS204 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
187 |  | BB1 | GS | 205 | BB1GS205 | Sootblower 3 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
188 | [27 empty] | Binary state | BB1GS205 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
189 |  | BB1 | GS | 206 | BB1GS206 | Sootblower 3 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
190 | [27 empty] | Binary state | BB1GS206 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
191 |  | BB1 | GS | 207 | BB1GS207 | Sootblower 5 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
192 | [27 empty] | Binary state | BB1GS207 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
193 |  | BB1 | GS | 208 | BB1GS208 | Sootblower 5 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
194 | [27 empty] | Binary state | BB1GS208 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
195 |  | BB1 | GS | 209 | BB1GS209 | Sootblower 6 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
196 | [27 empty] | Binary state | BB1GS209 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
197 |  | BB1 | GS | 210 | BB1GS210 | Sootblower 6 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
198 | [27 empty] | Binary state | BB1GS210 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
199 |  | BB1 | GS | 211 | BB1GS211 | Sootblower 7 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
200 | [27 empty] | Binary state | BB1GS211 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
201 |  | BB1 | GS | 212 | BB1GS212 | Sootblower 7 IN limit switch | [6 empty] | 24 | [26 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
202 | [27 empty] | Binary state | BB1GS212 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
203 |  | BB1 | GS | 213 | BB1GS213 | Sootblower 8 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
204 | [27 empty] | Binary state | BB1GS213 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
205 |  | BB1 | GS | 214 | BB1GS214 | Sootblower 8 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
206 | [27 empty] | Binary state | BB1GS214 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
207 |  | BB1 | IV | 203 | BB1IV203 | Sootblowing line on-off valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4004 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
209 |  | BB1 | TT | 201 | BB1TT201 | Sootblowing line temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [21 empty] | 4004 | MEAS_ANA | TT001 | Field IO
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
209 |  | BB1 | TT |  |  | Electrical room temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [22 empty] | MEAS_ANA | TT007 |  |  | Instrument added | 3
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA
209 |  | BB1 | TT |  |  | PLC-cabinet temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [22 empty] | MEAS_ANA | TT007 |  |  | Instrument added | 3
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA
211 |  | BB1 | GS | 227 | BB1GS227 | Sootblowing line on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | MCC
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 228 | BB1GS228 | Sootblowing line on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | MCC
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
215 |  | BB1 | BL | 200 | BB1BL200 | Sootblower 1 |  |  |  | 0.37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
221 |  | BB1 | BL | 201 | BB1BL201 | Sootblower 2 |  |  |  | 0.37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
227 |  | BB1 | BL | 202 | BB1BL202 | Sootblower 3 |  |  |  | 0.37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
233 |  | BB1 | BL | 203 | BB1BL203 | Sootblower 4 |  |  |  | 0.37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
239 |  | BB1 | BL | 204 | BB1BL204 | Sootblower 5 |  |  |  | 0.37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
245 |  | BB1 | BL | 205 | BB1BL205 | Sootblower 6 |  |  |  | 0.37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
251 |  | BB1 | BL | 206 | BB1BL206 | Sootblower 7 |  |  |  | 0.37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
257 |  | BB1 | TT | 006 | BB1TT006 | Blow down tank temperature and control | [30 empty] | 0 | 100 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4005 | MEAS_ANA | TT001 | Field IO
258 | [27 empty] | Measurement | BB1TT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
259 |  | BB1 | CV | 003 | BB1CV003 | Continuous blow down valve |  |  |  |  | 2 |  | 240 | [26 empty] | 3 | 2 | 1 | [17 empty] | Gestra | BAE 46-1-ANSI + EF10-1 + 1000 ohm |  | Konwell/Gestra | 4005 | MTR_VLV | AA001 |  |  | Model added | 1
260 | [27 empty] | Open direction command | BB1CV003 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
261 | [27 empty] | Close direction command | BB1CV003 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
262 | [27 empty] | Torque limit open direction | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
263 | [27 empty] | Torque limit close direction | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
264 | [27 empty] | Actuator fault | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
265 | [7 empty] | needs R/I converter 0...10 Kohm=4..20 mA | [19 empty] | Position | BB1CV003 | [12 empty] | X | [22 empty] | MTR_VLV
266 |  | BB1 | SV | 001 | BB1SV001 | Blow down tank cooling on/off valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4005 | BIN_VLV | AA005 | Field IO
267 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1SV001 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
268 |  | BB1 | PT | 205 | BB1PT205 | Steam outlet pressure from accumulator | [30 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA_SRS | PT001.1 | SRS |  | Moved to SRS | 2
269 | [27 empty] | Measurement SRS | BB1PT205 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS |  | Moved to SRS | 2
270 |  | BB1 | TT | 202 | BB1TT202 | Steam outlet temperature from accumulator | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
271 | [27 empty] | Measurement | BB1TT202 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
272 |  | BB1 | PT | 207 | BB1PT207 | Accumulator pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
273 | [27 empty] | Measurement | BB1PT207 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
274 |  | BB1 | CV | 203 | BB1CV203 | Steam accumulator pressure control valve |  |  |  | 0.25 | 1.8 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SAR14.2 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
211 |  | BB1 | GS | 231 | BB1GS231 | Steam accumulator pressure control valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | Field IO |  | Signal added | 1
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
213 |  | BB1 | GS | 230 | BB1GS230 | Steam accumulator pressure control valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | Field IO |  | Signal added | 1
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
277 |  | BB1 | TT | 007 | BB1TT007 | Accumulator temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
278 | [27 empty] | Measurement | BB1TT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
279 |  | BB1 | TT | 203 | BB1TT203 | 18bar(g) steam temperature |  | Transmitter wired to energy calculator | [28 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
280 | [27 empty] | Measurement | BB1TT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
281 |  | BB1 | CV | 202 | BB1CV202 | Steam pressure reduction valve |  |  |  | 0.25 | 1.8 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SAR14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 233 | BB1GS233 | Steam pressure reduction valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 232 | BB1GS232 | Steam pressure reduction valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
284 |  | BB1 | PT | 204 | BB1PT204 | Main steam pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
285 | [27 empty] | Measurement | BB1PT204 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
286 |  | BB1 | LT | 004 | BB1LT004 | Steam accumulator level 2 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4006 | MEAS_ANA | LT001 | Field IO
287 | [27 empty] | Measurement | BB1LT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
288 |  | BB1 | IV | 204 | BB1IV204 | Main steam line accumulator bypass on-off valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 217 | BB1GS217 | Main steam line accumulator bypass on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 218 | BB1GS218 | Main steam line accumulator bypass on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
290 |  | BB1 | PT | 208 | BB1PT208 | Accumulator pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
291 | [27 empty] | Measurement | BB1PT208 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
292 |  | BB1 | FT | 203 | BB1FT203 | Steam to existing header flow measurement | [30 empty] | 0 | 25 | t/h |  |  | 1 | [21 empty] | 4006 | MEAS_ANA | FT001 | Field IO
293 | [27 empty] | Measurement | BB1FT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
292 |  | BB1 | QT |  |  | Steam to existing header energy calculator | [6 empty] | 240 | [28 empty] | 1 | [17 empty] | E+H | RMS621-21BBA1221 |  |  | 4006 | MEAS_ANA |  | Field IO |  | Instrument added | 3
293 | [27 empty] | Measurement | BB1FT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
294 |  | BB1 | LT | 003 | BB1LT003 | Steam accumulator level 1 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4006 | MEAS_ANA | LT001 | Field IO
295 | [27 empty] | Measurement | BB1LT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
296 |  | BB1 | IV | 205 | BB1IV205 | Steam accumualtor ON-OFF isolating valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 219 | BB1GS219 | Steam accumualtor ON-OFF isolating valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 220 | BB1GS220 | Steam accumualtor ON-OFF isolating valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
298 |  | BB1 | GS | 217 | BB1GS217 | Steam accumulator by-pass valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
299 | [27 empty] | Binary state | BB1GS217 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
300 |  | BB1 | GS | 218 | BB1GS218 | Steam accumulator by-pass valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
301 | [27 empty] | Binary state | BB1GS218 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
302 |  | BB1 | GS | 220 | BB1GS220 | Steam accumulator ON-OFF valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
303 | [27 empty] | Binary state | BB1GS220 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
304 |  | BB1 | GS | 219 | BB1GS219 | Steam accumulator ON-OFF valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
305 | [27 empty] | Binary state | BB1GS219 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
306 |  | BB1 | QT | 002 | BB1QT002 | pH measurement from feed water tank | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
307 | [27 empty] | Measurement | BB1QT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
308 |  | BB1 | QT | 006 | BB1QT006 | Conductivity measurement from main steam | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
309 | [27 empty] | Measurement | BB1QT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
310 |  | BB1 | QT | 005 | BB1QT005 | Conductivity measurement from saturated steam | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
311 | [27 empty] | Measurement | BB1QT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
312 |  | BB1 | QT | 003 | BB1QT003 | Conductivity measurement from condensate | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
313 | [27 empty] | Measurement | BB1QT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
314 |  | BB1 | QT | 007 | BB1QT007 | Conductivity measurement from feed water line | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
315 | [27 empty] | Measurement | BB1QT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
316 |  | BB1 | QT | 001 | BB1QT001 | Conductivity measurement from feed water tank | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
317 | [27 empty] | Measurement | BB1QT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
318 |  | BB1 | QT | 004 | BB1QT004 | Conductivity measurement from boiler water | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
319 | [27 empty] | Measurement | BB1QT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
320 |  | BB1 | PT | 400 | BB1PT400 | Primary air pressure |  | SIL2 classified transmitter | [28 empty] | 0 | 16 | kPa | [6 empty] | 1 | [13 empty] | E+H | PMC51-AA22IA1EGJGCJA+LAZ1 | G1/2 |  | 4008 | MEAS_ANA_SRS | PT002 | SRS
321 | [27 empty] | Measurement SRS | BB1PT400 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
322 |  | BB1 | TT | 418 | BB1TT418 | Bed temperature 4 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
323 | [27 empty] | Measurement SRS | BB1TT418 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
324 |  | BB1 | PT | 404 | BB1PT404 | Boiler upper part pressure 1 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
325 | [27 empty] | Measurement SRS | BB1PT404 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
326 |  | BB1 | FT | 400 | BB1FT400 | Primary air flow |  | 0...11,21 mbar = 0...4,0 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
327 | [27 empty] | Measurement SRS | BB1FT400 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
328 |  | BB1 | PT | 401 | BB1PT401 | Secondary air pressure |  | SIL2 classified transmitter | [28 empty] | 0 | 6 | kPa | [6 empty] | 1 | [13 empty] | E+H | PMC51-AA22IA1CGJGCJA+LAZ1 | G1/2 |  | 4008 | MEAS_ANA_SRS | PT002 | SRS
329 | [27 empty] | Measurement SRS | BB1PT401 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
330 |  | BB1 | PT | 410 | BB1PT410 | Secondary air pressure inner front wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
331 | [27 empty] | Measurement | BB1PT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
332 |  | BB1 | TT | 551 | BB1TT551 | Flue gas temperature 2 | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
333 | [27 empty] | Measurement | BB1TT551 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
334 |  | BB1 | TT | 400 | BB1TT400 | Primary air temperature before preheater | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFG3000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
335 | [27 empty] | Measurement | BB1TT400 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
336 |  | BB1 | PT | 403 | BB1PT403 | Secondary air pressure inner back wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO
337 | [27 empty] | Measurement | BB1PT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
338 |  | BB1 | FT | 401 | BB1FT401 | Secondary air flow |  | 0...11,55 mbar = 0...4,6 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
339 | [27 empty] | Measurement SRS | BB1FT401 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
340 |  | BB1 | TT | 417 | BB1TT417 | Bed temperature 3 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
341 | [27 empty] | Measurement SRS | BB1TT417 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
342 |  | BB1 | PT | 550 | BB1PT550 | Flue gas pressure at the outlet of the boiler | [30 empty] | -35 | 35 | mbar |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO
343 | [27 empty] | Measurement | BB1PT550 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
344 |  | BB1 | TT | 012 | BB1TT012 | Condensate temperature from primary air preheater | [30 empty] | 0 | 250 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4008 | MEAS_ANA | TT001 | Field IO |  | Max scale changed | 3
345 | [27 empty] | Measurement | BB1TT012 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
346 |  | BB1 | TT | 413 | BB1TT413 | Bed temperature 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
347 | [27 empty] | Measurement SRS | BB1TT413 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
348 |  | BB1 | TT | 550 | BB1TT550 | Flue gas temperature 1 | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
349 | [27 empty] | Measurement | BB1TT550 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
350 |  | BB1 | TT | 412 | BB1TT412 | Boiler temperature after empty draft 2 | [30 empty] | 0 | 500 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
351 | [27 empty] | Measurement | BB1TT412 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
352 |  | BB1 | TT | 414 | BB1TT414 | Bed temperature 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
353 | [27 empty] | Measurement SRS | BB1TT414 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
354 |  | BB1 | PT | 405 | BB1PT405 | Boiler upper part pressure 2 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
355 | [27 empty] | Measurement SRS | BB1PT405 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
356 |  | BB1 | TT | 411 | BB1TT411 | Boiler temperature after empty draft 1 | [30 empty] | 0 | 500 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
357 | [27 empty] | Measurement | BB1TT411 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
358 |  | BB1 | QT | 550 | BB1QT550 | Fluegas oxygen measurement 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 25 | % | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | QT001/dn65 flange with counterflange. 1 meter probe | SRS
359 | [27 empty] | Measurement SRS | BB1QT550 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
360 |  | BB1 | FT | 550 | BB1FT550 | Recirculation gas flow |  | 0...10,19 mbar = 0...1,2 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
361 | [27 empty] | Measurement SRS | BB1FT550 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
362 |  | BB1 | QT | 551 | BB1QT551 | Fluegas oxygen measurement 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 25 | % | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | QT001/dn65 flange with counterflange. 1 meter probe | SRS
363 | [27 empty] | Measurement SRS | BB1QT551 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
364 |  | BB1 | QT | 552 | BB1QT552 | Fluegas CO measurement | [30 empty] | 0 | 5000 | ppm |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | QT001/dn65 flange with counterflange. 1 meter probe | Field IO
365 | [27 empty] | Measurement | BB1QT552 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
366 |  | BB1 | TT | 405 | BB1TT405 | Primary air temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFG3000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
367 | [27 empty] | Measurement | BB1TT405 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
368 |  | BB1 | PT | 406 | BB1PT406 | Boiler upper part pressure |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
369 | [27 empty] | Measurement SRS | BB1PT406 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
370 |  | BB1 | TT | 415 | BB1TT415 | Boiler bed temperature middle level | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEP |  |  | 4008 | MEAS_ANA | TT004 | Field IO
371 | [27 empty] | Measurement | BB1TT415 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
372 |  | BB1 | TT | 416 | BB1TT416 | Boiler bed temperature lower level | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEP |  |  | 4008 | MEAS_ANA | TT004 | Field IO
373 | [27 empty] | Measurement | BB1TT416 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
374 |  | BB1 | TT | 410 | BB1TT410 | Boiler 1st draft temperature | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TAF11-13ADA3GCFP+TEC420-YD12GEP |  |  | 4008 | MEAS_ANA | TT003 | Field IO
375 | [27 empty] | Measurement | BB1TT410 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
376 |  | BB1 | TT | 116 | BB1TT116 | Steam temperature to air preheater | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4008 | MEAS_ANA | TT001 | Field IO
377 | [27 empty] | Measurement | BB1TT116 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
378 |  | BB1 | TT | 308 | BB1TT308 | Furnace temperature connection | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TAF11-13ADA3GCFP+TEC420-YD12GEP |  |  | 4008 | MEAS_ANA | TT003 | Field IO
379 | [27 empty] | Measurement | BB1TT308 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
380 |  | BB1 | DM | 300 | BB1DM300 | Tertiary air damper 1 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
381 | [27 empty] | Setpoint position | BB1DM300 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
382 | [27 empty] | Position feedback | BB1DM300 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
383 |  | BB1 | DM | 400 | BB1DM400 | Primary air damper | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
384 | [27 empty] | Setpoint position | BB1DM400 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
385 | [27 empty] | Position feedback | BB1DM400 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
386 |  | BB1 | DM | 550 | BB1DM550 | Recirculation gas damper | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
387 | [27 empty] | Setpoint position | BB1DM550 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
388 | [27 empty] | Position feedback | BB1DM550 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
389 |  | BB1 | DM | 301 | BB1DM301 | Secondary air damper 4 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
390 | [27 empty] | Setpoint position | BB1DM301 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
391 | [27 empty] | Position feedback | BB1DM301 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
392 |  | BB1 | DM | 302 | BB1DM302 | Secondary air damper 3 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
393 | [27 empty] | Setpoint position | BB1DM302 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
394 | [27 empty] | Position feedback | BB1DM302 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
395 |  | BB1 | DM | 304 | BB1DM304 | Secondary air damper 1 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
396 | [27 empty] | Setpoint position | BB1DM304 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
397 | [27 empty] | Position feedback | BB1DM304 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
398 |  | BB1 | DM | 303 | BB1DM303 | Secondary air damper 2 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
399 | [27 empty] | Setpoint position | BB1DM303 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
400 | [27 empty] | Position feedback | BB1DM303 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
401 |  | BB1 | QT | 553 | BB1QT553 | Boiler room gas detector | [35 empty] | 1 | [21 empty] | 4008 | MEAS_ANA | XS001 | Field IO
402 | [27 empty] | Measurement | BB1QT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
403 |  | BB1 | TT | 408 | BB1TT408 | Secondary air fan motor bearing temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
404 | [27 empty] | Measurement | BB1TT408 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
403 |  | BB1 | TT | 423 | BB1TT423 | Secondary air fan motor bearing temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
404 | [27 empty] | Measurement | BB1TT408 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
405 |  | BB1 | TT | 406 | BB1TT406 | Secondary air fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
406 | [27 empty] | Measurement | BB1TT406 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
407 |  | BB1 | TT | 404 | BB1TT404 | Primary air fan motor bearing temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
408 | [27 empty] | Measurement | BB1TT404 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
407 |  | BB1 | TT | 409 | BB1TT409 | Primary air fan motor bearing temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
408 | [27 empty] | Measurement | BB1TT404 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
409 |  | BB1 | TT | 402 | BB1TT402 | Primary air fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
410 | [27 empty] | Measurement | BB1TT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
411 |  | BB1 | TT | 403 | BB1TT403 | Primary air fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
412 | [27 empty] | Measurement | BB1TT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
411 |  | BB1 | TT | 421 | BB1TT421 | Primary air fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
412 | [27 empty] | Measurement | BB1TT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
413 |  | BB1 | TT | 407 | BB1TT407 | Secondary air fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
414 | [27 empty] | Measurement | BB1TT407 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
413 |  | BB1 | TT | 422 | BB1TT422 | Secondary air fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
414 | [27 empty] | Measurement | BB1TT407 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
415 |  | BB1 | IV | 206 | BB1IV206 | Primary air preheater on-off valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA07.6-22 + RWG |  | Konwell/Auma | 4008 | MTR_VLV | AA003 |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
417 |  | BB1 | CV | 004 | BB1CV004 | Primary air preheater control valve | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
418 | [27 empty] | Setpoint position | BB1CV004 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
419 | [27 empty] | Position feedback | BB1CV004 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
420 |  | BB1 | GS | 215 | BB1GS215 | Primary air preheater on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4008 | MEAS_BIN | XS002/XS004 | MCC
421 | [27 empty] | Binary state | BB1GS215 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
422 |  | BB1 | GS | 216 | BB1GS216 | Primary air preheater on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4008 | MEAS_BIN | XS002/XS004 | MCC
423 | [27 empty] | Binary state | BB1GS216 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
424 |  | BB1 | IL | 001 | BB1IL001 | Alarm horn and light CO alarm | [34 empty] | 1 | [22 empty] | 4008 | ALM_HORN |  | Field IO |  | Description changed | 2
425 | [27 empty] | Command | BB1IL001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
426 |  | BB1 | PT | 409 | BB1PT409 | Secondary air pressure outer front wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
427 | [27 empty] | Measurement | BB1PT400 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
428 |  | BB1 | PT | 411 | BB1PT411 | Secondary air pressure outer back wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
429 | [27 empty] | Measurement | BB1PT401 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
430 |  | BB1 | PT | 407 | BB1PT407 | Tertiary air pressure right wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
431 | [27 empty] | Measurement | BB1PT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
432 |  | BB1 | PT | 408 | BB1PT408 | Tertiary air pressure left wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
433 | [27 empty] | Measurement | BB1PT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
434 |  | BB1 | EM | 400 | BB1EM400 | Primary air fan |  |  |  | 132 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4008 | FRQ_DIR |  |  |  | Size and voltage | 1
435 | [27 empty] | Running | BB1FF400 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
436 | [27 empty] | MCC Fault | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
437 | [27 empty] | Safety switch | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
438 | [27 empty] | VFD Alarm | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
439 | [27 empty] | Run command | BB1FF400 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
440 | [27 empty] | Current | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
441 | [27 empty] | Speed reference | BB1FF400 | [21 empty] | X | [13 empty] | FRQ_DIR
442 | [27 empty] | Actual speed | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
443 | [27 empty] | Torque | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
444 | [27 empty] | RPM | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
445 |  | BB1 | SI | 400 | BB1SI400 | Primary air fan safety interlock | [38 empty] | 1 | [18 empty] | 4008 | FAN_SRS_DO
446 | [27 empty] | Safety interlock | BB1SI400 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 410 | BB1SI410 | Primary air fan run status SRS | [37 empty] | 1 | [19 empty] | 4008 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 400 | BB1ST400 | Primary air fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
447 |  | BB1 | EM | 401 | BB1EM401 | Secondary air fan |  |  |  | 45 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4008 | FRQ_DIR |  |  |  | Size, name and voltage | 1
448 | [27 empty] | Running | BB1FF401 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
449 | [27 empty] | MCC Fault | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
450 | [27 empty] | Safety switch | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
451 | [27 empty] | VFD Alarm | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
452 | [27 empty] | Run command | BB1FF401 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
453 | [27 empty] | Current | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
454 | [27 empty] | Speed reference | BB1FF401 | [21 empty] | X | [13 empty] | FRQ_DIR
455 | [27 empty] | Actual speed | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
456 | [27 empty] | Torque | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
457 | [27 empty] | RPM | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
458 |  | BB1 | SI | 401 | BB1SI401 | Secondary air fan safety interlock | [38 empty] | 1 | [18 empty] | 4008 | FAN_SRS_DO
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 411 | BB1SI411 | Secondary air fan run status SRS | [37 empty] | 1 | [19 empty] | 4008 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 401 | BB1ST401 | Secondary air fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
107 |  | BB1 | HS | 601 | BB1HS601 | Fuel system emergency shutdown switch 1 |  | Near door that leads hydraulic units | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
108 | [27 empty] | Binary state SRS | BB1HS101 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 602 | BB1HS602 | Fuel system emergency shutdown switch 2 |  | Outside near lift doors fuel receiving station | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 603 | BB1HS603 | Fuel system emergency shutdown switch 3 |  | Screening station | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 604 | BB1HS604 | Fuel system emergency shutdown switch 4 |  | Outside, on Fuel silo level near door | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
460 |  | BB1 | GS | 621 | BB1GS621 | Unloading station 3, block 3, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
461 | [27 empty] | Binary state | BB1GS621 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
462 |  | BB1 | GS | 611 | BB1GS611 | Unloading station 2, block 2, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
463 | [27 empty] | Binary state | BB1GS611 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
464 |  | BB1 | GS | 606 | BB1GS606 | Unloading station 1, block 1, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
465 | [27 empty] | Binary state | BB1GS606 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
466 |  | BB1 | GS | 614 | BB1GS614 | Unloading station 2, block 2, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
467 | [27 empty] | Binary state | BB1GS614 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
468 |  | BB1 | GS | 619 | BB1GS619 | Unloading station 3, block 3, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
469 | [27 empty] | Binary state | BB1GS619 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
470 |  | BB1 | GS | 651 | BB1GS651 | Disc screen by-pass damper limit switch to screen | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack | Instrument type added | 1
471 | [27 empty] | Binary state | BB1GS651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
472 |  | BB1 | PS | 602 | BB1PS602 | Hydraulics unit 1, block 3, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
473 | [27 empty] | Binary state | BB1PT602 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
474 |  | BB1 | GS | 615 | BB1GS615 | Unloading station 2, block 2, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
475 | [27 empty] | Binary state | BB1GS615 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
476 |  | BB1 | GS | 623 | BB1GS623 | Unloading station 3, block 3, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
477 | [27 empty] | Binary state | BB1GS623 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
478 |  | BB1 | ST | 651 | BB1ST651 | Scraper conveyor 2, rotation guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
479 | [27 empty] | Binary state | BB1ST651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
480 |  | BB1 | GS | 603 | BB1GS603 | Unloading station 1, block 1, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
481 | [27 empty] | Binary state | BB1GS603 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
482 |  | BB1 | PS | 601 | BB1PS601 | Hydraulics unit 1, block 2, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
483 | [27 empty] | Binary state | BB1PT601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
484 |  | BB1 | GS | 650 | BB1GS650 | Disc screen by-pass damper limit switch by-pass pos. | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack | Instrument type added | 1
485 | [27 empty] | Binary state | BB1GS650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
486 |  | BB1 | GS | 622 | BB1GS622 | Unloading station 3, block 3, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
487 | [27 empty] | Binary state | BB1GS622 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
488 |  | BB1 | GS | 602 | BB1GS602 | Unloading station 1, block 1, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
489 | [27 empty] | Binary state | BB1GS602 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
490 |  | BB1 | LS | 655 | BB1LS655 | Scraper conveyor 2, turning point blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
491 | [27 empty] | Binary state | BB1LS655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
492 |  | BB1 | GS | 607 | BB1GS607 | Unloading station 1, block 1, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
493 | [27 empty] | Binary state | BB1GS607 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
494 |  | BB1 | GS | 605 | BB1GS605 | Unloading station 1, block 1, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
495 | [27 empty] | Binary state | BB1GS605 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
496 |  | BB1 | LS | 652 | BB1LS652 | Unloading station 2, block 2, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
497 | [27 empty] | Binary state | BB1LS652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
498 |  | BB1 | GS | 601 | BB1GS601 | Unloading station 1, block 1, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
499 | [27 empty] | Binary state | BB1GS601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
500 |  | BB1 | LS | 608 | BB1LS608 | Hydraulics unit 1, low oil level alarm | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | LS001 | Field IO | Fuel station IO-rack
501 | [27 empty] | Binary state | BB1LS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
502 |  | BB1 | LS | 656 | BB1LS656 | Scraper conveyor 2, fuel silo side blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO
503 | [27 empty] | Binary state | BB1LS656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
504 |  | BB1 | LS | 600 | BB1LS600 | Hydraulics unit 1, leaking pool limit switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | LS001 | Field IO | Fuel station IO-rack
505 | [27 empty] | Binary state | BB1LS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
506 |  | BB1 | GS | 609 | BB1GS609 | Unloading station 2, block 2, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
507 | [27 empty] | Binary state | BB1GS609 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
508 |  | BB1 | LS | 650 | BB1LS650 | Scraper conveyor 1 bed height level switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
509 | [27 empty] | Binary state | BB1LS650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
510 |  | BB1 | GS | 617 | BB1GS617 | Unloading station 3, block 3, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
511 | [27 empty] | Binary state | BB1GS617 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
512 |  | BB1 | LS | 651 | BB1LS651 | Unloading station 3, block 3, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
513 | [27 empty] | Binary state | BB1LS651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
514 |  | BB1 | GS | 612 | BB1GS612 | Unloading station 2, block 2, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
515 | [27 empty] | Binary state | BB1GS612 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
516 |  | BB1 | LS | 654 | BB1LS654 | Scraper conveyor 1, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
517 | [27 empty] | Binary state | BB1LS654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
518 |  | BB1 | GS | 613 | BB1GS613 | Unloading station 2, block 2, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
519 | [27 empty] | Binary state | BB1GS613 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
520 |  | BB1 | GS | 620 | BB1GS620 | Unloading station 3, block 3, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
521 | [27 empty] | Binary state | BB1GS620 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
522 |  | BB1 | GS | 618 | BB1GS618 | Unloading station 3, block 3, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
523 | [27 empty] | Binary state | BB1GS618 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
524 |  | BB1 | PS | 600 | BB1PS600 | Hydraulics unit 1, block 1, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
525 | [27 empty] | Binary state | BB1PT600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
526 |  | BB1 | GS | 608 | BB1GS608 | Unloading station 2, block 2, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
527 | [27 empty] | Binary state | BB1GS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
528 |  | BB1 | GS | 604 | BB1GS604 | Unloading station 1, block 1, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
529 | [27 empty] | Binary state | BB1GS604 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
530 |  | BB1 | LS | 653 | BB1LS653 | Unloading station 1, block 1, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
531 | [27 empty] | Binary state | BB1LS653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
532 |  | BB1 | GS | 616 | BB1GS616 | Unloading station 3, block 3, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
533 | [27 empty] | Binary state | BB1GS616 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
534 |  | BB1 | GS | 600 | BB1GS600 | Unloading station 1, block 1, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
535 | [27 empty] | Binary state | BB1GS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
536 |  | BB1 | ST | 650 | BB1ST650 | Scraper conveyor 1, rotation guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
537 | [27 empty] | Binary state | BB1ST650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
538 |  | BB1 | TT | 650 | BB1TT650 | Scraper conveyor 1, temperature measurement | [30 empty] | 0 | 150 | °C |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | TT006 | Field IO | Fuel station IO-rack
539 | [27 empty] | Measurement | BB1TT650 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
540 |  | BB1 | GS | 610 | BB1GS610 | Unloading station 2, block 2, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
541 | [27 empty] | Binary state | BB1GS610 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
542 |  | BB1 | LT | 611 | BB1LT611 | Unloading station 1 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
543 | [27 empty] | Measurement | BB1LT509 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
544 |  | BB1 | LT | 612 | BB1LT612 | Unloading station 3 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
545 | [27 empty] | Measurement | BB1LT513 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
546 |  | BB1 | LT | 613 | BB1LT613 | Unloading station 2 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
547 | [27 empty] | Measurement | BB1LT512 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
548 |  | BB1 | SV | 601 | BB1SV601 | Control Valve push feeders unloading station 1 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
549 | [27 empty] | Control out | BB1SV601 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
550 | [27 empty] | Control in | BB1SV601 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
551 |  | BB1 | ST | 675 | BB1ST675 | Leveling roller 3 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
552 | [27 empty] | Binary state | BB1ST703 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
553 |  | BB1 | SV | 603 | BB1SV603 | Control Valve push feeders unloading station 3 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
554 | [27 empty] | Control out | BB1SV603 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
555 | [27 empty] | Control in | BB1SV603 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
556 |  | BB1 | SV | 602 | BB1SV602 | Control Valve push feeders unloading station 2 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
557 | [27 empty] | Control out | BB1SV602 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
558 | [27 empty] | Control in | BB1SV602 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
559 |  | BB1 | TS | 608 | BB1TS608 | High temperature switch hydraulic oil | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack
560 | [27 empty] | Binary state | BB1TS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
561 |  | BB1 | ST | 673 | BB1ST673 | Leveling roller 1 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
562 | [27 empty] | Binary state | BB1ST701 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
563 |  | BB1 | TS | 600 | BB1TS600 | Hydraulics unit, thermostat for heater | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack
564 | [27 empty] | Binary state | BB1TS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
565 |  | BB1 | ST | 674 | BB1ST674 | Leveling roller 2 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
566 | [27 empty] | Binary state | BB1ST702 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
567 |  | BB1 | PS | 605 | BB1PS605 | Hydraulic oil return block 3 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
568 | [27 empty] | Binary state | BB1PS603 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
569 |  | BB1 | PS | 603 | BB1PS603 | Hydraulic oil return block 1 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
570 | [27 empty] | Binary state | BB1PS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
571 |  | BB1 | PS | 604 | BB1PS604 | Hydraulic oil return block 2 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
572 | [27 empty] | Binary state | BB1PS601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
573 |  | BB1 | EM | 603 | BB1EM603 | Fuel reception hydraulic unit 1, pump 1 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
574 | [27 empty] | Running | BB1PU603 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH |  |  |  | Motor details | 1
575 | [27 empty] | MCC Fault | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH |  |  |  | Motor details | 1
576 | [27 empty] | Safety switch | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
577 | [27 empty] | VFD Alarm | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
578 | [27 empty] | Run command | BB1PU603 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
579 | [27 empty] | Current | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
580 | [27 empty] | Speed reference | BB1PU603 | [21 empty] | X | [13 empty] | FRQ_DIRH
581 | [27 empty] | Actual speed | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
582 | [27 empty] | Torque | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
583 | [27 empty] | RPM | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
584 | [27 empty] | Local run command | BB1PU603 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
585 | [27 empty] | Local mode switch | BB1PU603 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 603 | BB1SI603 | Fuel reception hydraulic unit 1, pump 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
586 |  | BB1 | EM | 604 | BB1EM604 | Fuel reception hydraulic unit 1, pump 2 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
587 | [27 empty] | Running | BB1PU604 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH
588 | [27 empty] | MCC Fault | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
589 | [27 empty] | Safety switch | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
590 | [27 empty] | VFD Alarm | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
591 | [27 empty] | Run command | BB1PU604 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
592 | [27 empty] | Current | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
593 | [27 empty] | Speed reference | BB1PU604 | [21 empty] | X | [13 empty] | FRQ_DIRH
594 | [27 empty] | Actual speed | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
595 | [27 empty] | Torque | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
596 | [27 empty] | RPM | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
597 | [27 empty] | Local run command | BB1PU604 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
598 | [27 empty] | Local mode switch | BB1PU604 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 604 | BB1SI604 | Fuel reception hydraulic unit 1, pump 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
599 |  | BB1 | EM | 605 | BB1EM605 | Fuel reception hydraulic unit 1, pump 3 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
600 | [27 empty] | Running | BB1PU605 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH
601 | [27 empty] | MCC Fault | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
602 | [27 empty] | Safety switch | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
603 | [27 empty] | VFD Alarm | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
604 | [27 empty] | Run command | BB1PU605 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
605 | [27 empty] | Current | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
606 | [27 empty] | Speed reference | BB1PU605 | [21 empty] | X | [13 empty] | FRQ_DIRH
607 | [27 empty] | Actual speed | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
608 | [27 empty] | Torque | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
609 | [27 empty] | RPM | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
610 | [27 empty] | Local run command | BB1PU605 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
611 | [27 empty] | Local mode switch | BB1PU605 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 605 | BB1SI605 | Fuel reception hydraulic unit 1, pump 3 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
612 |  | BB1 | EM | 673 | BB1EM673 | Levelling roller 1 |  |  |  | 2.2 |  |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size changed | 3
613 | [27 empty] | Running FWD | BB1EM703 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
614 | [27 empty] | Running BWD | BB1EM703 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
615 | [27 empty] | MCC Fault | BB1EM703 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
616 | [27 empty] | Local FWD command | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
617 | [27 empty] | Local BWD command | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
618 | [27 empty] | Local mode switch | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
619 | [27 empty] | Run command FWD | BB1EM703 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
620 | [27 empty] | Run command BWD | BB1EM703 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
621 | [27 empty] | Current | BB1EM703 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
622 |  | BB1 | EM | 674 | BB1EM674 | Levelling roller 2 |  |  |  | 3 |  |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size changed | 3
623 | [27 empty] | Running FWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
624 | [27 empty] | Running BWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
625 | [27 empty] | MCC Fault | BB1EM704 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
626 | [27 empty] | Local FWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
627 | [27 empty] | Local BWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
628 | [27 empty] | Local mode switch | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
629 | [27 empty] | Run command FWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
630 | [27 empty] | Run command BWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
631 | [27 empty] | Current | BB1EM704 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
632 |  | BB1 | EM | 675 | BB1EM675 | Levelling roller 3 | [57 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor deleted | 2
633 | [27 empty] | Running FWD | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
634 | [27 empty] | Running BWD | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
635 | [27 empty] | MCC Fault | BB1EM703 | [28 empty] | NC | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
636 | [27 empty] | Local FWD command | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
637 | [27 empty] | Local BWD command | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
638 | [27 empty] | Local mode switch | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
639 | [27 empty] | Run command FWD | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
640 | [27 empty] | Run command BWD | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
641 | [27 empty] | Current | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
642 |  | BB1 | EM | 658 | BB1EM658 | Scraper Conveyor 1 |  |  |  | 15 |  |  | 415 | [26 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Tag changed and motor details | 1
643 | [27 empty] | Running FWD | BB1CO653 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
644 | [27 empty] | Running BWD | BB1CO653 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
645 | [27 empty] | MCC Fault | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
646 | [27 empty] | Safety switch | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
647 | [27 empty] | VFD Alarm | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
648 | [27 empty] | Local FWD command | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
649 | [27 empty] | Local BWD command | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
650 | [27 empty] | Local mode switch | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
651 | [27 empty] | Run command FWD | BB1CO653 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
652 | [27 empty] | Run command BWD | BB1CO653 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
653 | [27 empty] | Current | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
654 | [27 empty] | Speed reference | BB1CO653 | [21 empty] | X | [13 empty] | FRQ_REVH
655 | [27 empty] | Actual speed | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
656 | [27 empty] | Torque | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
657 | [27 empty] | RPM | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 658 | BB1SI658 | Scraper Conveyor 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
658 |  | BB1 | EM | 670 | BB1EM670 | Belt magnet |  |  |  | 2.2 | 4.2 | 1500 | 415 | [26 empty] | 2 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIRH_BUS |  |  |  | Motor details and type | 1
659 | [27 empty] | Running FWD | BB1CO654 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
660 | [27 empty] | Running BWD | BB1CO654 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
661 | [27 empty] | MCC Fault | BB1CO654 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
662 | [27 empty] | Local FWD command | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
663 | [27 empty] | Local BWD command | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
664 | [27 empty] | Local mode switch | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
665 | [27 empty] | Run command FWD | BB1CO654 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
666 | [27 empty] | Run command BWD | BB1CO654 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
667 | [27 empty] | Current | BB1CO654 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
685 |  | BB1 | ST | 654 | BB1ST654 | Belt magnet rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 661 | BB1GS661 | Belt magnet deviation detector 1 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCRT115EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 662 | BB1GS662 | Belt magnet deviation detector 2 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCRT115EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
668 |  | BB1 | EM | 659 | BB1EM659 | Belt Conveyor |  |  |  | 4 | 7.6 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Motor details and type | 1
669 | [27 empty] | Running FWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
670 | [27 empty] | Running BWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
671 | [27 empty] | MCC Fault | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
672 | [27 empty] | Safety switch | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
673 | [27 empty] | VFD Alarm | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
674 | [27 empty] | Local FWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
675 | [27 empty] | Local BWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
676 | [27 empty] | Local mode switch | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
677 | [27 empty] | Run command FWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
678 | [27 empty] | Run command BWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
679 | [27 empty] | Current | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
680 | [27 empty] | Speed reference | BB1CO655 | [21 empty] | X | [13 empty] | FRQ_REVH
681 | [27 empty] | Actual speed | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
682 | [27 empty] | Torque | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
683 | [27 empty] | RPM | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
684 | [7 empty] | Brake |  |  |  |  | 240 | [55 empty] | Feed added | 1
458 |  | BB1 | SI | 659 | BB1SI659 | Belt Conveyor safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
685 |  | BB1 | ST | 652 | BB1ST652 | Belt conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 659 | BB1GS659 | Belt conveyor deviation detector 1 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Steute | Ex ES 98 SR-11-3GD |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 660 | BB1GS660 | Belt conveyor deviation detector 2 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Steute | Ex ES 98 SR-11-3GD |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 663 | BB1GS663 | Belt conveyor oversize detector | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
687 |  | BB1 | EM | 675 | BB1EM75 | Disc screen drive 1 |  |  |  | 7.5 | 13.7 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Tag changed | 3
688 | [27 empty] | Running FWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
689 | [27 empty] | Running BWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
690 | [27 empty] | MCC Fault | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
691 | [27 empty] | Safety switch | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
692 | [27 empty] | VFD Alarm | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
693 | [27 empty] | Local FWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
694 | [27 empty] | Local BWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
695 | [27 empty] | Local mode switch | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
696 | [27 empty] | Run command FWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
697 | [27 empty] | Run command BWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
698 | [27 empty] | Current | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
699 | [27 empty] | Speed reference | BB1CO655 | [21 empty] | X | [13 empty] | FRQ_REVH
700 | [27 empty] | Actual speed | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
701 | [27 empty] | Torque | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
702 | [27 empty] | RPM | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 675 | BB1SI675 | Disc screen drive 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
703 |  | BB1 | EM | 676 | BB1EM676 | Disc screen drive 2 |  |  |  | 7.5 | 13.7 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH | XS002 |  |  | Tag changed | 3
704 | [27 empty] | Running FWD | BB1CO656 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
705 | [27 empty] | Running BWD | BB1CO656 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
706 | [27 empty] | MCC Fault | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
707 | [27 empty] | Safety switch | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
708 | [27 empty] | VFD Alarm | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
709 | [27 empty] | Local FWD command | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
710 | [27 empty] | Local BWD command | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
711 | [27 empty] | Local mode switch | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
712 | [27 empty] | Run command FWD | BB1CO656 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
713 | [27 empty] | Run command BWD | BB1CO656 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
714 | [27 empty] | Current | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
715 | [27 empty] | Speed reference | BB1CO656 | [21 empty] | X | [13 empty] | FRQ_REVH
716 | [27 empty] | Actual speed | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
717 | [27 empty] | Torque | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
718 | [27 empty] | RPM | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 676 | BB1SI676 | Disc screen drive 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
719 |  | BB1 | ST | 656 | BB1ST656 | Disc screen drive 1 rotation guard | [33 empty] | 1 | [19 empty] | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument type added | 1
720 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
721 |  | BB1 | ST | 657 | BB1ST657 | Disc screen drive 2 rotation guard | [33 empty] | 1 | [19 empty] | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument type added | 1
722 | [27 empty] | Binary state | BB1ST657 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
723 |  | BB1 | EM | 672 | BB1EM672 | Scraper Conveyor 2 |  |  |  | 18.5 |  |  | 415 | [26 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Motor size changed | 3
724 | [27 empty] | Running FWD | BB1CO657 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
725 | [27 empty] | Running BWD | BB1CO657 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
726 | [27 empty] | MCC Fault | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
727 | [27 empty] | Safety switch | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
728 | [27 empty] | VFD Alarm | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
729 | [27 empty] | Local FWD command | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
730 | [27 empty] | Local BWD command | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
731 | [27 empty] | Local mode switch | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
732 | [27 empty] | Run command FWD | BB1CO657 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
733 | [27 empty] | Run command BWD | BB1CO657 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
734 | [27 empty] | Current | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
735 | [27 empty] | Speed reference | BB1CO657 | [21 empty] | X | [13 empty] | FRQ_REVH
736 | [27 empty] | Actual speed | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
737 | [27 empty] | Torque | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
738 | [27 empty] | RPM | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 672 | BB1SI672 | Scraper Conveyor 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
739 |  | BB1 | IJ | 002 | BB1IJ002 | Scraper Conveyor 1 Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4009 | ALM_HORN |  | Field IO | Fuel station IO-rack
740 | [27 empty] | Command | BB1IJ002 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO | Fuel station IO-rack
741 |  | BB1 | IJ | 001 | BB1IJ001 | Scraper Conveyor 2 Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4009 | ALM_HORN |  | Field IO
742 | [27 empty] | Command | BB1IJ001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
743 |  | BB1 | EM | 601 | BB1EM601 | Dust extraction rotary feeder |  | preliminary size |  | 0.75 | [29 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size added | 3
744 | [27 empty] | Running FWD | BB1RV601 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
745 | [27 empty] | Running BWD | BB1RV601 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
746 | [27 empty] | MCC Fault | BB1RV601 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
747 | [27 empty] | Local FWD command | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
748 | [27 empty] | Local BWD command | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
749 | [27 empty] | Local mode switch | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
750 | [27 empty] | Run command FWD | BB1RV601 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
751 | [27 empty] | Run command BWD | BB1RV601 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
752 | [27 empty] | Current | BB1RV601 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
753 |  | BB1 | EM | 606 | BB1EM606 | Dust extraction fan |  | preliminary size |  | 30 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIR_BUS |  |  |  | Tag and motor size changed | 3
754 | [27 empty] | Running | BB1FF603 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
755 | [27 empty] | MCC Fault | BB1FF603 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
756 | [27 empty] | Run command | BB1FF603 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
757 | [27 empty] | Current | BB1FF603 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
758 |  | BB1 | EH | 600 | BB1EH600 | Electric heater hydraulic unit |  | preliminary size |  | 1.5 | [37 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIR_BUS
759 | [27 empty] | Running | BB1EH600 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
760 | [27 empty] | MCC Fault | BB1EH600 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
761 | [27 empty] | Run command | BB1EH600 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
762 | [27 empty] | Current | BB1EH600 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
763 |  | BB1 | CV | 402 | BB1CV402 | Fuel chute B carrying air control valve 2 | [35 empty] | 1 | 1 | [20 empty] | 4010 | CONT_VLV | AA002 | Field IO
764 | [27 empty] | Setpoint position | BB1CV402 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
765 | [27 empty] | Position feedback | BB1CV402 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
766 |  | BB1 | CV | 403 | BB1CV403 | Fuel chute A carrying air control valve 1 | [35 empty] | 1 | 1 | [20 empty] | 4010 | CONT_VLV | AA002 | Field IO
767 | [27 empty] | Setpoint position | BB1CV403 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
768 | [27 empty] | Position feedback | BB1CV403 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
769 |  | BB1 | GS | 652 | BB1GS652 | Explosion hatch limit switch 1 | [33 empty] | 1 | [19 empty] | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
770 | [27 empty] | Binary state | BB1GS652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
771 |  | BB1 | GS | 653 | BB1GS653 | Explosion hatch limit switch 2 | [33 empty] | 1 | [19 empty] | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
772 | [27 empty] | Binary state | BB1GS653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
773 |  | BB1 | GS | 654 | BB1GS654 | Explosion hatch limit switch 3 | [33 empty] | 0 | [22 empty] | LAITEX | 4010 | MEAS_BIN | XS002 |  |  | Instrument removed | 1
774 | [27 empty] | Binary state | BB1GS654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
775 |  | BB1 | GS | 655 | BB1GS655 | Explosion hatch limit switch 4 | [33 empty] | 0 | [22 empty] | LAITEX | 4010 | MEAS_BIN | XS002 |  |  | Instrument removed | 1
776 | [27 empty] | Binary state | BB1GS655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
777 |  | BB1 | LS | 657 | BB1LS657 | Fuel silo discharge screw blockage switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument type added | 1
778 | [27 empty] | Binary state | BB1LS657 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
779 |  | BB1 | LS | 658 | BB1LS658 | Fuel silo cross conveyor blockage switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Description changed | 2
780 | [27 empty] | Binary state | BB1LS658 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
779 |  | BB1 | LS |  | BB1LS | Fuel silo cross conveyor explosion hatch limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 2
780 | [27 empty] | Binary state | BB1LS658 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
781 |  | BB1 | LS | 659 | BB1LS659 | Fuel feeding screw 1 blockage switch | [33 empty] | 1 | [16 empty] | 3-wire |  |  | Telemechanique | XS630B1PAL10EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | 3-wire | 2
782 | [27 empty] | Binary state | BB1LS659 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
783 |  | BB1 | LS | 660 | BB1LS660 | Fuel feeding screw 2 blockage switch | [33 empty] | 1 | [16 empty] | 3-wire |  |  | Telemechanique | XS630B1PAL10EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | 3-wire | 2
784 | [27 empty] | Binary state | BB1LS660 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
785 |  | BB1 | LT | 650 | BB1LT650 | Fuel silo level radar 1 | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT10-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 | Field IO |  | Instrument type added | 1
786 | [27 empty] | Measurement | BB1LT650 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA |  | Field IO
785 |  | BB1 | LT | 651 | BB1LT651 | Fuel silo level radar 2 | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT10-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 |  |  | Instrument deleted | 2
786 | [27 empty] | Measurement | BB1LT650 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA
787 |  | BB1 | LT | 652 | BB1LT652 | Fuel pocket level | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT20-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 | Field IO |  | Instrument type added | 1
788 | [27 empty] | Measurement | BB1LT652 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA |  | Field IO
789 |  | BB1 | ST | 649 | BB1ST649 | Fuel silo cross conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Description modified | 3
790 | [27 empty] | Binary state | BB1ST649 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
791 |  | BB1 | ST | 652 | BB1ST652 | Rotating fuel spreader rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
792 | [27 empty] | Binary state | BB1ST652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
793 |  | BB1 | ST | 653 | BB1ST653 | Fuel feeding screw 2 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | 2-wire | 2
794 | [27 empty] | Binary state | BB1ST653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
795 |  | BB1 | ST | 654 | BB1ST654 | Fuel feeding rotary feeder 1 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
796 | [27 empty] | Binary state | BB1ST654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
797 |  | BB1 | ST | 655 | BB1ST655 | Fuel feeding rotary feeder 2 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
798 | [27 empty] | Binary state | BB1ST655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
799 |  | BB1 | ST | 659 | BB1ST659 | Fuel feeding screw 1 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | 2-wire | 2
800 | [27 empty] | Binary state | BB1ST659 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
801 |  | BB1 | SV | 400 | BB1SV400 | Sealing air to rotary feeder solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
802 | [27 empty] | Control command | BB1SV400 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
803 |  | BB1 | SV | 406 | BB1SV406 | Sealing air to rotary feeder solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
804 | [27 empty] | Control command | BB1SV406 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
805 |  | BB1 | SV | 950 | BB1SV950 | Fuel silo fire water control valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
806 | [27 empty] | Control command | BB1SV950 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
807 |  | BB1 | SV | 951 | BB1SV951 | Fuel pocket fire water control valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
808 | [27 empty] | Control command | BB1SV951 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
809 |  | BB1 | TT | 652 | BB1TT652 | Fuel silo temperature measurement | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TST41N-MRDD82HA4P |  |  | 4010 | MEAS_ANA | TT006 | Field IO
810 | [27 empty] | Measurement | BB1TT652 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
811 |  | BB1 | TT | 653 | BB1TT653 | Fuel pocket temperature | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TST41N-MRDD82HA4P |  |  | 4010 | MEAS_ANA | TT006 | Field IO
812 | [27 empty] | Measurement | BB1TT653 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
813 |  | BB1 | IV | 650 | BB1IV650 | Slide gate valve |  |  |  | 2.2 | 4.2 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor added | 1
814 | [27 empty] | Running FWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
815 | [27 empty] | Running BWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
816 | [27 empty] | MCC Fault | BB1EM704 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
817 | [27 empty] | Local FWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
818 | [27 empty] | Local BWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
819 | [27 empty] | Local mode switch | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
820 | [27 empty] | Run command FWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
821 | [27 empty] | Run command BWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
822 | [27 empty] | Current | BB1EM704 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
823 |  | BB1 | GS | 655 | BB1GS655 | Slide gate valve open limit switch | [33 empty] | 1 | [19 empty] | Telemecanique | XSAV-11801 |  |  | 4010 | MEAS_BIN |  | Field IO |  | Instrument added | 1
824 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
825 |  | BB1 | GS | 656 | BB1GS656 | Slide gate valve close limit switch | [33 empty] | 1 | [19 empty] | Telemecanique | XSAV-11801 |  |  | 4010 | MEAS_BIN |  | Field IO |  | Instrument added | 1
826 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
827 |  | BB1 | HC | 601 | BB1HC601 | Crane feed |  | 16 A breaker |  |  |  |  | 415 | [55 empty] | Crane added | 1
828 |  | BB1 | FL | 650 | BB1FL650 | Fuel silo dust filter control box feed |  | 10 A breaker |  |  |  |  | 240 | [27 empty] | 1 | [22 empty] | 4010 | MCCB_1ph |  |  |  | Voltage level added | 1
831 | [27 empty] | Cleaning on | BB1FF650 | [11 empty] | X | [16 empty] | Pot.free | [10 empty] | Signal added | 1
829 |  | BB1 | EM | 651 | BB1EM651 | Fuel silo dust filter fan | [41 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIR_BUS
830 | [27 empty] | Running | BB1FF650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
831 | [27 empty] | MCC Fault | BB1FF650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
832 | [27 empty] | Run command | BB1FF650 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
833 | [27 empty] | Current | BB1FF650 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
834 |  | BB1 | EM | 652 | BB1EM652 | Rotating fuel spreader |  |  |  | 0.75 | 1.7 | 1500 | 415 | [26 empty] | 2 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIRH_BUS |  |  |  | Size, current and voltage | 1
835 | [27 empty] | Running | BB1SD650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
836 | [27 empty] | MCC Fault | BB1SD650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
837 | [27 empty] | Local run command | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
838 | [27 empty] | Local mode switch | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
839 | [27 empty] | Run command | BB1SD650 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
840 | [27 empty] | Current | BB1SD650 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
841 |  | BB1 | EM | 662 | BB1EM662 | Fuel silo screw discharger |  |  |  | 22 | 39,5 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
842 | [27 empty] | Running FWD | BB1FD662 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
843 | [27 empty] | Running BWD | BB1FD662 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
844 | [27 empty] | MCC Fault | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
845 | [27 empty] | Safety switch | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
846 | [27 empty] | VFD Alarm | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
847 | [27 empty] | Local FWD command | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
848 | [27 empty] | Local BWD command | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
849 | [27 empty] | Local mode switch | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
850 | [27 empty] | Run command FWD | BB1FD662 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
851 | [27 empty] | Run command BWD | BB1FD662 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
852 | [27 empty] | Current | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
853 | [27 empty] | Speed reference | BB1FD662 | [21 empty] | X | [13 empty] | FRQ_REVH
854 | [27 empty] | Actual speed | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
855 | [27 empty] | Torque | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
856 | [27 empty] | RPM | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
857 |  | BB1 | EM | 650 | BB1EM650 | Slewing motor for screw |  |  |  | 2.2 | 4.2 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
858 | [27 empty] | Running FWD | BB1EM650 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
859 | [27 empty] | Running BWD | BB1EM650 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
860 | [27 empty] | MCC Fault | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
861 | [27 empty] | Safety switch | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
862 | [27 empty] | VFD Alarm | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
863 | [27 empty] | Local FWD command | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
864 | [27 empty] | Local BWD command | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
865 | [27 empty] | Local mode switch | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
866 | [27 empty] | Run command FWD | BB1EM650 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
867 | [27 empty] | Run command BWD | BB1EM650 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
868 | [27 empty] | Current | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
869 | [27 empty] | Speed reference | BB1EM650 | [21 empty] | X | [13 empty] | FRQ_REVH
870 | [27 empty] | Actual speed | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
871 | [27 empty] | Torque | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
872 | [27 empty] | RPM | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
873 |  | BB1 | EM | 660 | BB1EM660 | Cooling fan for slewing motor |  |  |  | 0.09 |  |  | 240 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor added | 1
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
877 |  | BB1 | EM | 654 | BB1EM654 | Lubrication unit |  | Fuse size C6A |  | 0.2 | 0.8 |  | 240 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Tag chanhed | 3
878 | [27 empty] | Running | BB1PU650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
879 | [27 empty] | MCC Fault | BB1PU650 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
880 | [27 empty] | Run command | BB1PU650 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
881 |  | BB1 | LS | 661 | BB1LS661 | Lubrication alarm screw discharger | [33 empty] | 1 | [19 empty] | SKF | KFGS | LAITEX |  | 4010 | MEAS_BIN |  | Field IO |  | Tag changed | 3
882 | [27 empty] | Binary state | BB1QA650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
883 |  | BB1 | EH | 662 | BB1EH662 | Heater for slipring unit |  |  |  | 0.4 | 1.7 |  | 240 | [26 empty] | 1 | [23 empty] | 4010 | MCCB_1ph |  |  |  | Details | 1
884 |  | BB1 | EM | 663 | BB1EM663 | Fuel silo cross conveyor |  |  |  | 4 | 7.6 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
885 | [27 empty] | Running FWD | BB1FD663 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
886 | [27 empty] | Running BWD | BB1FD663 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
887 | [27 empty] | MCC Fault | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
888 | [27 empty] | Safety switch | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
889 | [27 empty] | VFD Alarm | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
890 | [27 empty] | Local FWD command | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
891 | [27 empty] | Local BWD command | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
892 | [27 empty] | Local mode switch | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
893 | [27 empty] | Run command FWD | BB1FD663 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
894 | [27 empty] | Run command BWD | BB1FD663 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
895 | [27 empty] | Current | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
896 | [27 empty] | Speed reference | BB1FD663 | [21 empty] | X | [13 empty] | FRQ_REVH
897 | [27 empty] | Actual speed | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
898 | [27 empty] | Torque | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
899 | [27 empty] | RPM | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
900 |  | BB1 | EM | 664 | BB1EM664 | Fuel feeding screw 1 |  |  |  | 5.5 | 10 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
901 | [27 empty] | Running FWD | BB1FD664 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
902 | [27 empty] | Running BWD | BB1FD664 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
903 | [27 empty] | MCC Fault | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
904 | [27 empty] | Safety switch | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
905 | [27 empty] | VFD Alarm | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
906 | [27 empty] | Local FWD command | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
907 | [27 empty] | Local BWD command | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
908 | [27 empty] | Local mode switch | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
909 | [27 empty] | Run command FWD | BB1FD664 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
910 | [27 empty] | Run command BWD | BB1FD664 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
911 | [27 empty] | Current | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
912 | [27 empty] | Speed reference | BB1FD664 | [21 empty] | X | [13 empty] | FRQ_REVH
913 | [27 empty] | Actual speed | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
914 | [27 empty] | Torque | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
915 | [27 empty] | RPM | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
916 |  | BB1 | EM | 653 | BB1EM653 | Cooling fan fuel feeding screw 1 |  |  |  | 0.15 | 0.33 |  | 415 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor details | 1
917 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
918 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
919 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
920 |  | BB1 | EM | 665 | BB1EM665 | Fuel feeding screw 2 |  |  |  | 5.5 | 10 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
921 | [27 empty] | Running FWD | BB1FD665 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
922 | [27 empty] | Running BWD | BB1FD665 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
923 | [27 empty] | MCC Fault | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
924 | [27 empty] | Safety switch | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
925 | [27 empty] | VFD Alarm | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
926 | [27 empty] | Local FWD command | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
927 | [27 empty] | Local BWD command | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
928 | [27 empty] | Local mode switch | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
929 | [27 empty] | Run command FWD | BB1FD665 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
930 | [27 empty] | Run command BWD | BB1FD665 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
931 | [27 empty] | Current | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
932 | [27 empty] | Speed reference | BB1FD665 | [21 empty] | X | [13 empty] | FRQ_REVH
933 | [27 empty] | Actual speed | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
934 | [27 empty] | Torque | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
935 | [27 empty] | RPM | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
936 |  | BB1 | EM | 655 | BB1EM655 | Cooling fan fuel feeding screw 2 |  |  |  | 0.15 | 0.33 |  | 415 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor details | 1
937 | [27 empty] | Running | BB1FF654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
938 | [27 empty] | MCC Fault | BB1FF654 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
939 | [27 empty] | Run command | BB1FF654 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
940 |  | BB1 | EM | 657 | BB1EM657 | Fuel feeding rotary valve 1 |  |  |  | 7.5 | 13.7 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor details | 1
941 | [27 empty] | Running FWD | BB1RV650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
942 | [27 empty] | Running BWD | BB1RV650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
943 | [27 empty] | MCC Fault | BB1RV650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
944 | [27 empty] | Local FWD command | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
945 | [27 empty] | Local BWD command | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
946 | [27 empty] | Local mode switch | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
947 | [27 empty] | Run command FWD | BB1RV650 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
948 | [27 empty] | Run command BWD | BB1RV650 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
949 | [27 empty] | Current | BB1RV650 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
950 |  | BB1 | EM | 656 | BB1EM656 | Fuel feeding rotary valve 2 |  |  |  | 7.5 | 13.7 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor details | 1
951 | [27 empty] | Running FWD | BB1RV651 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
952 | [27 empty] | Running BWD | BB1RV651 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
953 | [27 empty] | MCC Fault | BB1RV651 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
954 | [27 empty] | Local FWD command | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
955 | [27 empty] | Local BWD command | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
956 | [27 empty] | Local mode switch | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
957 | [27 empty] | Run command FWD | BB1RV651 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
958 | [27 empty] | Run command BWD | BB1RV651 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
959 | [27 empty] | Current | BB1RV651 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
960 |  | BB1 | GS | 802 | BB1GS802 | Bottom ash valve limit switch | [33 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | XS002/XS004 | Field IO
961 | [27 empty] | Binary state | BB1GS802 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
962 |  | BB1 | GS | 803 | BB1GS803 | Bottom ash dropping chute closing device limit switch | [33 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | XS002/XS004 | Field IO
963 | [27 empty] | Binary state | BB1GS803 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
964 |  | BB1 | LS | 852 | BB1LS852 | Fly ash container level switch |  | harting connector |  |  |  |  | 24 VDC | [26 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | LS001 | Field IO
965 | [27 empty] | Binary state | BB1LS852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
966 |  | BB1 | PT | 552 | BB1PT552 | ESP inlet pressure transmitter |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA | PT002
967 | [27 empty] | Measurement | BB1PT552 | [12 empty] | X | [22 empty] | MEAS_ANA
968 |  | BB1 | PT | 553 | BB1PT553 | ESP outlet pressure transmitter |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA | PT002
969 | [27 empty] | Measurement | BB1PT553 | [12 empty] | X | [22 empty] | MEAS_ANA
970 |  | BB1 | QT | 554 | BB1QT554 | Opacity after ESP | [6 empty] | 24 VDC | [23 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | QT001 | Field IO
971 | [27 empty] | Measurement | BB1QT554 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
972 |  | BB1 | ST | 805 | BB1ST805 | Heated ESP collection screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
973 | [27 empty] | Binary state | BB1ST805 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
974 |  | BB1 | ST | 808 | BB1ST808 | ESP hopper 2 screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
975 | [27 empty] | Binary state | BB1ST808 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
976 |  | BB1 | ST | 809 | BB1ST809 | ESP hopper 1 screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
977 | [27 empty] | Binary state | BB1ST809 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
978 |  | BB1 | ST | 804 | BB1ST804 | ESP Rotary valve rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
979 | [27 empty] | Binary state | BB1ST804 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
980 |  | BB1 | TT | 553 | BB1TT553 | Flue gas fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
980 |  | BB1 | TT | 557 | BB1TT557 | Flue gas fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO |  | signal added | 3
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
980 |  | BB1 | TT | 558 | BB1TT558 | Flue gas fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO |  | signal added | 3
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
982 |  | BB1 | TT | 554 | BB1TT554 | Flue gas fan bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
983 | [27 empty] | Measurement | BB1TT554 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
984 |  | BB1 | TT | 555 | BB1TT555 | Flue gas fan bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
985 | [27 empty] | Measurement | BB1TT555 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
986 |  | BB1 | TT | 556 | BB1TT556 | Flue gas temperature before stack | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4011 | MEAS_ANA | TT003 | Field IO
987 | [27 empty] | Measurement | BB1TT556 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
988 |  | BB1 | TT | 850 | BB1TT850 | ESP Ash hopper 1 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
989 | [27 empty] | Measurement | BB1TT850 | [12 empty] | X | [22 empty] | MEAS_ANA
990 |  | BB1 | TT | 851 | BB1TT851 | ESP Ash hopper 2 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
991 | [27 empty] | Measurement | BB1TT851 | [12 empty] | X | [22 empty] | MEAS_ANA
992 |  | BB1 | EH | 808 | BB1EH808 | ESP Ash hopper 2 heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
993 | [27 empty] | RCBO fault | BB1EH808 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
994 | [27 empty] | On command | BB1EH808 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
995 |  | BB1 | EH | 809 | BB1EH809 | ESP Ash hopper 1 heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
996 | [27 empty] | RCBO fault | BB1EH809 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
997 | [27 empty] | On command | BB1EH809 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
998 |  | BB1 | TS | 808 | BB1TS808 | ESP Ash hopper 2 overheat thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS001
999 | [27 empty] | Binary state | BB1TS808 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1000 |  | BB1 | TS | 809 | BB1TS809 | ESP Ash hopper 1 overheat thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS001
1001 | [27 empty] | Binary state | BB1TS809 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1002 |  | BB1 | TS | 501 | BB1TS501 | ESP Insulator 1 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1003 | [27 empty] | Measurement | BB1TS501 | [12 empty] | X | [22 empty] | MEAS_ANA
1004 |  | BB1 | TS | 508 | BB1TS508 | ESP Insulator 2 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1005 | [27 empty] | Measurement | BB1TS508 | [12 empty] | X | [22 empty] | MEAS_ANA
1006 |  | BB1 | TT | 552 | BB1TT552 | Flue gas temperature before ESP |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1007 | [27 empty] | Measurement | BB1TT552 | [12 empty] | X | [22 empty] | MEAS_ANA
1008 |  | BB1 | EM | 509 | BB1EM509 | ESP DE rapping drive 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1009 | [27 empty] | Running | BB1EM509 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1010 | [27 empty] | MCC Fault | BB1EM509 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1011 | [27 empty] | Run command | BB1EM509 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1012 |  | BB1 | EM | 510 | BB1EM510 | ESP CE rapping drive 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1013 | [27 empty] | Running | BB1EM510 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1014 | [27 empty] | MCC Fault | BB1EM510 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1015 | [27 empty] | Run command | BB1EM510 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1016 |  | BB1 | EM | 511 | BB1EM511 | ESP DE rapping drive 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1017 | [27 empty] | Running | BB1EM511 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1018 | [27 empty] | MCC Fault | BB1EM511 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1019 | [27 empty] | Run command | BB1EM511 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1020 |  | BB1 | EM | 512 | BB1EM512 | ESP CE rapping drive 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1021 | [27 empty] | Running | BB1EM512 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1022 | [27 empty] | MCC Fault | BB1EM512 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1023 | [27 empty] | Run command | BB1EM512 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1024 |  | BB1 | EH | 501 | BB1EH501 | ESP insulators heating chamber 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1025 | [27 empty] | Running | BB1EH501 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1026 | [27 empty] | MCC Fault | BB1EH501 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1027 | [27 empty] | Run command | BB1EH501 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1028 |  | BB1 | EH | 505 | BB1EH505 | ESP insulators heating chamber 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1029 | [27 empty] | Running | BB1EH505 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1030 | [27 empty] | MCC Fault | BB1EH505 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1031 | [27 empty] | Run command | BB1EH505 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1032 |  | BB1 | IE | 501 | BB1IE501 | ESP HV Trafo 1 |  | Supply from ESP MCC | [55 empty] | 4011 | OESA_3ph
1033 |  | BB1 | IE | 502 | BB1IE502 | ESP HV Trafo 2 |  | Supply from ESP MCC | [55 empty] | 4011 | OESA_3ph
1034 |  | BB1 | FG | 300 | BB1FG300 | ESP hardwired signals to/from Boiler PLC | [33 empty] | 8 | 6 | [22 empty] | 4011 | ESP_DI_DO
1035 | [27 empty] | Collective Alarm | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1036 | [27 empty] | Collective Warning | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1037 | [27 empty] | ESP in Standby | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1038 | [27 empty] | ESP in Operation | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1039 | [27 empty] | ESP spare DI1 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1040 | [27 empty] | ESP spare DI2 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1041 | [27 empty] | ESP spare DI3 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1042 | [27 empty] | ESP spare DI4 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1043 | [27 empty] | ESP External release filter | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1044 | [27 empty] | ESP spare DO1 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1045 | [27 empty] | ESP spare DO2 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1046 | [27 empty] | ESP spare DO3 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1047 | [27 empty] | ESP spare DO4 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1048 | [27 empty] | ESP spare DO5 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1049 |  | BB1 | EM | 809 | BB1EM809 | ESP ash hopper 1 screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1050 | [27 empty] | Running FWD | BB1EM809 | [10 empty] | X | [24 empty] | DOL_REVH
1051 | [27 empty] | Running BWD | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1052 | [27 empty] | MCC Fault | BB1EM809 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1053 | [27 empty] | Local FWD command | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1054 | [27 empty] | Local BWD command | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1055 | [27 empty] | Local mode switch | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1056 | [27 empty] | Run command FWD | BB1EM809 | [11 empty] | X | [23 empty] | DOL_REVH
1057 | [27 empty] | Run command BWD | BB1EM809 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1058 |  | BB1 | EM | 808 | BB1EM808 | ESP ash hopper 2 screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1059 | [27 empty] | Running FWD | BB1EM808 | [10 empty] | X | [24 empty] | DOL_REVH
1060 | [27 empty] | Running BWD | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1061 | [27 empty] | MCC Fault | BB1EM808 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1062 | [27 empty] | Local FWD command | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1063 | [27 empty] | Local BWD command | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1064 | [27 empty] | Local mode switch | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1065 | [27 empty] | Run command FWD | BB1EM808 | [11 empty] | X | [23 empty] | DOL_REVH
1066 | [27 empty] | Run command BWD | BB1EM808 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1067 |  | BB1 | EM | 805 | BB1EM805 | ESP collection screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1068 | [27 empty] | Running FWD | BB1EM805 | [10 empty] | X | [24 empty] | DOL_REVH
1069 | [27 empty] | Running BWD | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1070 | [27 empty] | MCC Fault | BB1EM805 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1071 | [27 empty] | Local FWD command | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1072 | [27 empty] | Local BWD command | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1073 | [27 empty] | Local mode switch | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1074 | [27 empty] | Run command FWD | BB1EM805 | [11 empty] | X | [23 empty] | DOL_REVH
1075 | [27 empty] | Run command BWD | BB1EM805 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1076 |  | BB1 | EH | 805 | BB1EH805 | ESP collection screw heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1077 | [27 empty] | RCBO fault | BB1EH805 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1078 | [27 empty] | On command | BB1EH805 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1079 |  | BB1 | TS | 805 | BB1TS805 | ESP collection screw heating thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN
1080 | [27 empty] | Binary state | BB1TS805 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1081 |  | BB1 | EM | 804 | BB1EM804 | ESP Rotary valve |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1082 | [27 empty] | Running FWD | BB1EM804 | [10 empty] | X | [24 empty] | DOL_REVH
1083 | [27 empty] | Running BWD | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1084 | [27 empty] | MCC Fault | BB1EM804 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1085 | [27 empty] | Local FWD command | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1086 | [27 empty] | Local BWD command | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1087 | [27 empty] | Local mode switch | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1088 | [27 empty] | Run command FWD | BB1EM804 | [11 empty] | X | [23 empty] | DOL_REVH
1089 | [27 empty] | Run command BWD | BB1EM804 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1090 |  | BB1 | EH | 804 | BB1EH804 | ESP Rotary valve heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1091 | [27 empty] | RCBO fault | BB1EH804 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1092 | [27 empty] | On command | BB1EH804 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1093 |  | BB1 | TS | 804 | BB1TS804 | ESP Rotary valve heating thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN
1094 | [27 empty] | Binary state | BB1TS804 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1095 |  | BB1 | EM | 815 | BB1EM815 | Fly ash container screw | [41 empty] | 3 | 2 | 1 | [13 empty] | 4011 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1101 |  | BB1 | EM | 550 | BB1EM550 | Flue gas fan |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4011 | FRQ_DIR |  |  |  | Size and voltage | 1
1102 | [27 empty] | Running | BB1FF550 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
1103 | [27 empty] | MCC Fault | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1104 | [27 empty] | Safety switch | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1105 | [27 empty] | VFD Alarm | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1106 | [27 empty] | Run command | BB1FF550 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
1107 | [27 empty] | Current | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1108 | [27 empty] | Speed reference | BB1FF550 | [21 empty] | X | [13 empty] | FRQ_DIR
1109 | [27 empty] | Actual speed | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1110 | [27 empty] | Torque | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1111 | [27 empty] | RPM | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1112 |  | BB1 | SI | 550 | BB1SI550 | Flue gas fan safety interlock | [38 empty] | 1 | [18 empty] | 4011 | FAN_SRS_DO
1113 | [27 empty] | Safety interlock | BB1SI550 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 560 | BB1SI560 | Flue gas fan run status SRS | [37 empty] | 1 | [19 empty] | 4011 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 550 | BB1ST550 | Flue gas fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
458 |  | BB1 |  |  | BB1 | Flue gas fan heating |  | RCBO + Contactor |  |  |  |  | 240 | [27 empty] | 1 | [22 empty] | 4011 |  |  |  |  | Heater added | 3
459 | [27 empty] | Heater On control | BB1SI401 | [11 empty] | X | [27 empty] | Heater added | 3
1114 |  | BB1 | CV | 405 | BB1CV405 | Bottom ash valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1115 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV405 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1116 |  | BB1 | GS | 855 | BB1GS855 | Bottom ash valve solenoid valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1117 | [27 empty] | Binary state | BB1GS855 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1118 |  | BB1 | GS | 856 | BB1GS856 | Bottom ash valve solenoid valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1119 | [27 empty] | Binary state | BB1GS856 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1120 |  | BB1 | CV | 406 | BB1CV406 | Bottom ash valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1121 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV406 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1122 |  | BB1 | GS | 857 | BB1GS857 | Bottom ash valve solenoid valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1123 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1124 |  | BB1 | GS | 858 | BB1GS858 | Bottom ash valve solenoid valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1125 | [27 empty] | Binary state | BB1GS858 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1126 |  | BB1 | CV | 412 | BB1CV412 | Bottom ash sieve bypass solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1127 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV412 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1128 |  | BB1 | GS | 850 | BB1GS850 | Bottom ash sieve bypass valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1129 | [27 empty] | Binary state | BB1GS850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1130 |  | BB1 | GS | 851 | BB1GS851 | Bottom ash sieve bypass valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1131 | [27 empty] | Binary state | BB1GS851 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1132 |  | BB1 | CV | 413 | BB1CV413 | Control valve of pneumatic transmitter damper |  | Pneuplan PLC |  |  | Pneuplan PLC |  | 24 | [27 empty] | 2 | [21 empty] | Pneuplan | 4012 | BIN_VLV_2DO | AA004 | Field IO
1133 | [27 empty] | Open command | BB1CV413 | [11 empty] | X | [23 empty] | BIN_VLV_2DO |  | Field IO
1134 | [27 empty] | Close command | BB1CV413 | [11 empty] | X | [23 empty] | BIN_VLV_2DO |  | Field IO
1135 |  | BB1 | CV | 414 | BB1CV414 | Work air to pneumatic transmitter pneumatic valve |  | Pneuplan PLC |  |  | Pneuplan PLC |  | 24 | [27 empty] | 1 | [21 empty] | Pneuplan | 4012 | BIN_VLV | AA004 | Field IO
1136 | [27 empty] | Control command | BB1CV414 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1137 |  | BB1 | FS | 003 | BB1FS003 | Bottom ash cooling flow switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | FS001 | Field IO
1138 | [27 empty] | Binary state | BB1FS003 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1139 |  | BB1 | SV | 405 | BB1SV405 | Sand filling valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA003 | Field IO
1140 | [27 empty] | Control command | BB1SV405 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1141 |  | BB1 | GS | 801 | BB1GS801 | Sand filling valve position open limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | AA005 | Field IO
1142 | [27 empty] | Binary state | BB1GS801 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1143 |  | BB1 | GS | 800 | BB1GS800 | Sand filling valve position close limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS001 | Field IO
1144 | [27 empty] | Binary state | BB1GS800 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1145 |  | BB1 | GS | 854 | BB1GS854 | Bottom ash dropping chute limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO |  | Tag changed | 3
1146 | [27 empty] | Binary state | BB1GS852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1147 |  | BB1 | GS | 853 | BB1GS853 | Bottom ash dropping chute closing device limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO
1148 | [27 empty] | Binary state | BB1GS853 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1149 |  | BB1 | GS | 859 | BB1GS859 | Bottom ash to container in place |  | Harting connector (jumper in container side..> DI=1 connector in place) | [31 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO |  | Tag changed | 3
1150 | [27 empty] | Binary state | BB1GS854 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1151 |  | BB1 | LS | 850 | BB1LS850 | Bottom ash container level switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | LS001 | Field IO
1152 | [27 empty] | Binary state | BB1LS850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1153 |  | BB1 | LS | 851 | BB1LS851 | Bottom ash container level switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | LS001 | Field IO
1154 | [27 empty] | Binary state | BB1LS851 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1155 |  | BB1 | LT | 800 | BB1LT800 | Recycled bed material hopper level switch |  | Pneuplan PLC |  |  | Pneuplan PLC | [30 empty] | 1 | [20 empty] | Pneuplan | 4012 | MEAS_ANA |  | Field IO
1156 | [27 empty] | Measurement | BB1LT800 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1157 |  | BB1 | LT | 802 | BB1LT802 | Sand silo level measurement | [6 empty] | 24 VDC | [23 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4012 | MEAS_ANA | LT003 | Field IO
1158 | [27 empty] | Measurement | BB1LT802 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1159 |  | BB1 | PT | 009 | BB1PT009 | Cooling water pressure before pump | [30 empty] | 0 | 6 | bar(g) |  |  | 1 | [13 empty] | Pressure |  |  |  | E+H | PMP51-AA22IA1PGJGCJA1+Z1 | G1/2 |  | 4012 | MEAS_ANA | PT001.1 | Field IO
1160 | [27 empty] | Measurement | BB1PT009 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1161 |  | BB1 | PT | 800 | BB1PT800 | Recycled bed material damper pressure switch |  | Pneuplan PLC |  |  | Pneuplan PLC | [28 empty] | 1 | [22 empty] | Pneuplan | 4012 | MEAS_BIN |  | Field IO
1162 | [27 empty] | Binary state | BB1PT800 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1153 |  | BB1 | EM | 856 | BB1EM856 | Purified sand screw conveyor | [33 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor added | 2
1154 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1155 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1156 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1157 | [27 empty] | Local FWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1158 | [27 empty] | Local BWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1159 | [27 empty] | Local mode switch | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1160 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1161 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1162 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1151 |  | BB1 | ST | 856 | BB1ST856 | Purified sand screw conveyor rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument added | 2
1152 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO |  | Instrument added | 2
1163 |  | BB1 | EM | 852 | BB1EM852 | Bottom ash conveyor |  |  |  | 2.2 | 4.2 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4012 | FRQ_REVH |  |  |  | Tag changed | 2
1164 | [27 empty] | Running FWD | BB1EM850 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1165 | [27 empty] | Running BWD | BB1EM850 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1166 | [27 empty] | MCC Fault | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1167 | [27 empty] | Safety switch | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1168 | [27 empty] | VFD Alarm | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1169 | [27 empty] | Local FWD command | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1170 | [27 empty] | Local BWD command | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1171 | [27 empty] | Local mode switch | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1172 | [27 empty] | Run command FWD | BB1EM850 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1173 | [27 empty] | Run command BWD | BB1EM850 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1174 | [27 empty] | Current | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1175 | [27 empty] | Speed reference | BB1EM850 | [21 empty] | X | [13 empty] | FRQ_REVH
1176 | [27 empty] | Actual speed | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1177 | [27 empty] | Torque | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1178 | [27 empty] | RPM | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1179 |  | BB1 | ST | 850 | BB1ST850 | Bottom ash conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemecanique | XSAV-11801 |  |  | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
1180 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1179 |  | BB1 | GS | 852 | BB1GS852 | Bottom ash conveyor blockage detector | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemecanique | XS530B1MAL2 |  |  | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument added | 1
1180 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
741 |  | BB1 | IJ | 004 | BB1IJ004 | Bottom ash conveyor Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4012 | ALM_HORN |  | Field IO |  | Instrument added | 2
742 | [27 empty] | Command | BB1IJ001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
1181 |  | BB1 | EM | 850 | BB1EM850 | 2nd pass fly ash rotary valve |  |  |  |  | 0,37 |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor details | 1
1182 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1183 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1184 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1185 | [27 empty] | Local FWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1186 | [27 empty] | Local BWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1187 | [27 empty] | Local mode switch | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1188 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1189 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1190 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1191 |  | BB1 | ST | 852 | BB1ST852 | 2nd pass fly ash rotary valve rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO
1192 | [27 empty] | Binary state | BB1ST852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1193 |  | BB1 | EM | 851 | BB1EM851 | 3rd pass fly ash rotary valve |  |  |  |  | 0,37 |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor details | 1
1194 | [27 empty] | Running FWD | BB1EM851 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1195 | [27 empty] | Running BWD | BB1EM851 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1196 | [27 empty] | MCC Fault | BB1EM851 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1197 | [27 empty] | Local FWD command | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1198 | [27 empty] | Local BWD command | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1199 | [27 empty] | Local mode switch | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1200 | [27 empty] | Run command FWD | BB1EM851 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1201 | [27 empty] | Run command BWD | BB1EM851 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1202 | [27 empty] | Current | BB1EM851 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1203 |  | BB1 | ST | 853 | BB1ST853 | 3rd pass fly ash rotary valve rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO
1204 | [27 empty] | Binary state | BB1ST853 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1205 |  | BB1 | SV | 401 | BB1SV401 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA005 | Field IO
1206 | [27 empty] | Control command | BB1SV401 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1207 |  | BB1 | SV | 402 | BB1SV402 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA005 | Field IO
1208 | [27 empty] | Control command | BB1SV402 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1209 |  | BB1 | SV | 403 | BB1SV403 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 0 | [22 empty] | 4012 | BIN_VLV | AA005 |  |  | Removed | 1
1210 | [27 empty] | Control command | BB1SV403 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  |  |  | Removed | 1
1211 |  | BB1 | SV | 404 | BB1SV404 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 0 | [22 empty] | 4012 | BIN_VLV | AA005 |  |  | Removed | 1
1212 | [27 empty] | Control command | BB1SV404 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  |  |  | Removed | 1
1213 |  | BB1 | TT | 031 | BB1TT031 | Cooling water temperature after bottom ash conveyor | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4012 | MEAS_ANA | TT001 | Field IO
1214 | [27 empty] | Measurement | BB1TT031 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1215 |  | BB1 | EM | 014 | BB1EM008 | Conveyor cooling pump |  |  |  | 1.1 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [12 empty] | Grundfos | 4012 | DOL_DIR_BUS |  |  |  | Motor size changed | 3
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1220 |  | BB1 | EM | 855 | BB1EM855 | Ash container screw |  |  |  | 1.5 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4012 | DOL_REV_BUS |  |  |  | Motor details | 1
1221 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1222 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1224 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS
1225 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS
1227 |  | BB1 | EM | 018 | BB1EM009 | Bottom ash conveyor heat exchanger fan |  | preliminary 6x0,72 kW, 1.42 A |  | 7.5 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4012 | DOL_DIR_BUS |  |  |  | Tag changed | 2
1228 | [27 empty] | Running | BB1FF009 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1229 | [27 empty] | MCC Fault | BB1FF009 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1230 | [27 empty] | Run command | BB1FF009 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1231 | [27 empty] | Current | BB1FF009 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1232 |  | BB1 | FM | 001 | BB1FM001 | Bottom ash sieve feed |  | supply fuse 16A |  | 1.4 |  |  | 415 | [26 empty] | 5 | 1 | [22 empty] | 4012 | OESA_3ph |  |  |  | Details | 1
1236 | [27 empty] | Emergency stop | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1237 | [7 empty] | ask preliminary drawings from KPA | [19 empty] | Running | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
[28 empty] | manual/auto | [11 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1238 | [27 empty] | Thermistor fault | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1239 | [27 empty] | Voltage OK | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1241 | [27 empty] | Start/stop | BB1BU500 | [11 empty] | X | [16 empty] | pot.free | [6 empty] | OESA_3ph |  |  |  | signals added | 1
1233 |  | BB1 | HC | 601 | BB1HC601 | Electrical hoist feed |  |  |  |  | 2,8 |  | 415 | [50 empty] | 4012 | OESA_3ph
1234 |  | BB1 | TN | ??? | BB1TN??? | Sand transmitter 230 Vac feed | [33 empty] | 1 | [23 empty] | 4012 | MCCB_1ph
1235 |  | BB1 | BU | 500 | BB1BU500 | Burner signals | [33 empty] | 5 | 5 | 2 | 2 |  |  |  |  | 6 | 5 | 2 | 2 | [12 empty] | 4013 | BURNER
1236 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1237 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1238 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1239 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1240 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1241 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1242 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1243 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1244 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1245 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1246 | [27 empty] | AI reservation | BB1BU500 | [12 empty] | X | [22 empty] | BURNER
1247 | [27 empty] | AI reservation | BB1BU500 | [12 empty] | X | [22 empty] | BURNER
1248 | [27 empty] | AO reservation | BB1BU500 | [13 empty] | X | [21 empty] | BURNER
1249 | [27 empty] | AO reservation | BB1BU500 | [13 empty] | X | [21 empty] | BURNER
1250 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1251 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1252 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1253 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1254 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1255 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1256 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1257 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1258 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1259 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1260 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1261 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1262 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1263 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1264 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1265 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1266 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1267 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1268 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1269 |  | BB1 | EM | 402 | BB1EM402 | Compressor 1 |  | Preliminary size |  | 30 |  |  | 415 | [26 empty] | 3 | 2 | [22 empty] | 4014 | COMPR |  | Field IO |  | Motor size and tag changed | 3
1270 | [27 empty] | Fault | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1271 | [27 empty] | Running | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1272 | [27 empty] | Reserve | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1273 | [27 empty] | Remote run command | BB1EM400 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1274 | [27 empty] | Fault acknowledge | BB1EM400 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1275 |  | BB1 | EM | 403 | BB1EM403 | Compressor 2 |  | Preliminary size |  | 30 |  |  | 415 | [26 empty] | 3 | 2 | [22 empty] | 4014 | COMPR |  | Field IO |  | Motor size and tag changed | 3
1276 | [27 empty] | Fault | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1277 | [27 empty] | Running | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1278 | [27 empty] | Reserve | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1279 | [27 empty] | Remote run command | BB1EM402 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1280 | [27 empty] | Fault acknowledge | BB1EM402 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1281 |  | BB1 | DR | 400 | BB1DR400 | Compressor 1 dryer |  |  |  | 4 |  |  | 415 | [26 empty] | 1 | [23 empty] | 4014 | MCCB_1ph |  |  |  | motor details | 1
1282 |  | BB1 | DR | 401 | BB1DR401 | Compressor 2 dryer |  |  |  | 4 |  |  | 415 | [26 empty] | 1 | [23 empty] | 4014 | MCCB_1ph |  |  |  | motor details | 1
1283 |  | BB1 | PT | 478 | BB1PT478 | Instrument air pressure | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4014 | MEAS_ANA | PT002 | Field IO
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1283 |  | BB1 | PT | 402 | BB1PT402 | Instrument air pressure after dryer | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4014 | MEAS_ANA | PT002 | Field IO |  | Instrument added | 3
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
1283 |  | BB1 | TT | 430 | BB1TT430 | Instrument air tank temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [19 empty] | G1/2 |  | 4014 | MEAS_ANA | TT003 | Field IO |  | Instrument added | 3
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
1285 |  | BB1 | GS | 020 | BB1GS020 | Emergency shower use switch | [33 empty] | 1 | [23 empty] | 4014 | MEAS_BIN | XS001 | Field IO
1286 | [27 empty] | Binary state | BB1GS020 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1287 |  | BB1 | TT | 401 | BB1TT401 | Boiler room upper part temperature | [35 empty] | 1 | [17 empty] | E+H | TST434-J1A3BP | Wall mount |  | 4014 | MEAS_ANA | TT007 | Field IO
1288 | [27 empty] | Measurement | BB1TT401 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1289 |  | BB1 | EM | 401 | BB1EM401 | Exhaust fan 1 |  |  |  | 1.9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1290 | [27 empty] | Running FWD | BB1EM401 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1291 | [27 empty] | Running BWD | BB1EM401 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1292 | [27 empty] | MCC Fault | BB1EM401 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1293 | [27 empty] | Run command FWD | BB1EM401 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1294 | [27 empty] | Run command BWD | BB1EM401 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1295 | [27 empty] | Current | BB1EM401 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1296 |  | BB1 | EM | 402 | BB1EM402 | Exhaust fan 2 |  |  |  | 1.9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1297 | [27 empty] | Running FWD | BB1EM402 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1298 | [27 empty] | Running BWD | BB1EM402 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1299 | [27 empty] | MCC Fault | BB1EM402 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1300 | [27 empty] | Run command FWD | BB1EM402 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1301 | [27 empty] | Run command BWD | BB1EM402 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1302 | [27 empty] | Current | BB1EM402 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1303 |  | BB1 | EM | 403 | BB1EM403 | Exhaust fan 3 |  |  |  | 1.9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1304 | [27 empty] | Running FWD | BB1EM403 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1305 | [27 empty] | Running BWD | BB1EM403 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1306 | [27 empty] | MCC Fault | BB1EM403 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1307 | [27 empty] | Run command FWD | BB1EM403 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1308 | [27 empty] | Run command BWD | BB1EM403 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1309 | [27 empty] | Current | BB1EM403 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1310 |  | BB1 | EM | 405 | BB1EM405 | Air intake grill 1 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1311 |  |  |  |  | BB1GS401 | [22 empty] | Open limit switch | BB1EM405 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1312 | [27 empty] | Open command | BB1EM405 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1313 |  | BB1 | EM | 406 | BB1EM406 | Air intake grill 2 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1314 |  |  |  |  | BB1GS412 | [22 empty] | Open limit switch | BB1EM406 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1315 | [27 empty] | Open command | BB1EM406 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1316 |  | BB1 | EM | 407 | BB1EM407 | Air intake grill 3 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1317 |  |  |  |  | BB1GS413 | [22 empty] | Open limit switch | BB1EM407 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1318 | [27 empty] | Open command | BB1EM407 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1319 |  | BB1 | EM | 408 | BB1EM408 | Boiler house heater 1 |  |  |  | 15 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4014 | DOL_DIR_BUS |  |  |  | Motor feed type changed | 2
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1323 |  | BB1 | EM | 409 | BB1EM409 | Boiler house heater 2 |  |  |  | 15 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4014 | DOL_DIR_BUS |  |  |  | Motor feed type changed | 2
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Sheet1 (hidden)
TAG | DESCRIPTION | DEVICE_COUNT | DO | DI | AO | AI | SDO | SDI | SAO | SAI
KPA_FLOORX_IO | KPA NON ASSIGNED IO | 485 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR0_IO | KPA LEVEL 0 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR1_IO | KPA LEVEL 1 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR2_IO | KPA LEVEL 2 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR3_IO | KPA LEVEL 3 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR4_IO | KPA LEVEL 4 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FUEL_STATION_IO | KPA FUEL STATION REMOTE IO CABINET | 132 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_MCC | KPA REMOTE IO INTERNAL TO MCC | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_PLC | KPA PLC CABINET | 87 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
ESP_PLC | ESP PLC CABINET | 8 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
ESP_MCC | ESP REMOTE IO INTERNAL TO MCC | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## _Parameters
Parameter | Value
jobNumber | 38025
dwgCategory | ELE
protoPath | S:\Elecdes\prototypes\gen6\INSTRUMENTATION\
protoPathMotor | S:\Elecdes\prototypes\gen6\MOTORS\