## PROTOTYPE_FIELDS
{Note} | Default values for prototypes. Blank fields will not be included when given prototype dbf is generated.
Field | POWERFLEX_ISO_TH | POWERFLEX_ISOL | POWERFLEX_TH | LRUN_LOCAL_FWD_REV | LRUN_LOCAL_RUN | Column3 | Column2 | Column1
PREFIX | ##PREFIX## | ##PREFIX## | ##PREFIX## | ##PREFIX## | ##PREFIX##
DRAWING | ##DRAWING## | ##DRAWING## | ##DRAWING## | ##DRAWING2## | ##DRAWING2##
PROTOTYPE | S:\Elecdes\prototypes\gen6\MOTORS\POWERFLEX_ISO_TH | S:\Elecdes\prototypes\gen6\MOTORS\POWERFLEX_ISOL | S:\Elecdes\prototypes\gen6\MOTORS\POWERFLEX_TH | S:\Elecdes\prototypes\gen6\MOTORS\LRUN_LOCAL_FWD_REV | S:\Elecdes\prototypes\gen6\MOTORS\LRUN_LOCAL_RUN
X1NAME | ##X1NAME## | ##X1NAME## | ##X1NAME##
X1DESC
X2NAME |  |  |  | KPA_FLOORX_IO | KPA_FLOORX_IO
X2DESC |  |  |  | KPA NON ASSIGNED IO | KPA NON ASSIGNED IO
X3NAME |  |  |  | ##X3NAME## | ##X3NAME##
X3DESC |  |  |  | OPERATOR PANEL | OPERATOR PANEL
X4NAME |  |  |  | KPA_FLOORX_IO | KPA_FLOORX_IO
X4DESC |  |  |  | KPA NON ASSIGNED IO | KPA NON ASSIGNED IO
X1VDC24
X1VDC0
X1XIO
X1XIOF
X1XIOK
X1V230 | ##X1V230## | ##X1V230## | ##X1V230##
X1N230 | ##X1N230## | ##X1N230## | ##X1N230##
X1XDB
X1XDBF
X1XDBK
X1XDBQ | ##X1XDBQ## | ##X1XDBQ## | ##X1XDBQ##
Q1CATN | ##Q1CATN## | ##Q1CATN## | ##Q1CATN##
Q1CATD | ##Q1CATD## | ##Q1CATD## | ##Q1CATD##
Q1NAME1 | ##Q1NAME1## | ##Q1NAME1## | ##Q1NAME1##
Q1NAME2 | ##Q1NAME2## | ##Q1NAME2## | ##Q1NAME2##
Q1TCATN | ##Q1TCATN## | ##Q1TCATN## | ##Q1TCATN##
Q1TCATD | ##Q1TCATD## | ##Q1TCATD## | ##Q1TCATD##
Q1TNAME | ##Q1TNAME## | ##Q1TNAME## | ##Q1TNAME##
Q1TSETTO | ##Q1TSETTO## | ##Q1TSETTO## | ##Q1TSETTO##
P1NAME |  |  |  | ##P1NAME## | ##P1NAME##
P1RACK |  |  |  | ##P1RACK## | ##P1RACK##
P1SLOT |  |  |  | ##P1SLOT## | ##P1SLOT##
P1CHAN |  |  |  | ##P1CHAN## | ##P1CHAN##
P1MFG |  |  |  | 2 | 2
P1CATN |  |  |  | ##P1CATN## | ##P1CATN##
P1CATD |  |  |  | ##P1CATD## | ##P1CATD##
P1CATD2 |  |  |  | ##P1CATD2## | ##P1CATD2##
P1TAG |  |  |  | ##P1TAG## | ##P1TAG##
P1DESC2 |  |  |  | ##P1DESC2## | ##P1DESC2##
P1DESC3 |  |  |  | ##P1DESC3## | ##P1DESC3##
P1DESC4 |  |  |  | ##P1DESC4## | ##P1DESC4##
P1T1 |  |  |  | ##P1T1## | ##P1T1##
P1T2 |  |  |  | ##P1T2## | ##P1T2##
P1T1TYPE |  |  |  | ##P1T1TYPE## | ##P1T1TYPE##
P1T2TYPE |  |  |  | ##P1T2TYPE## | ##P1T2TYPE##
P2NAME |  |  |  | ##P2NAME## | ##P2NAME##
P2RACK |  |  |  | ##P2RACK## | ##P2RACK##
P2SLOT |  |  |  | ##P2SLOT## | ##P2SLOT##
P2CHAN |  |  |  | ##P2CHAN## | ##P2CHAN##
P2MFG |  |  |  | 2 | 2
P2CATN |  |  |  | ##P2CATN## | ##P2CATN##
P2CATD |  |  |  | ##P2CATD## | ##P2CATD##
P2CATD2 |  |  |  | ##P2CATD2## | ##P2CATD2##
P2TAG |  |  |  | ##P2TAG## | ##P2TAG##
P2DESC2 |  |  |  | ##P2DESC2## | ##P2DESC2##
P2DESC3 |  |  |  | ##P2DESC3## | ##P2DESC3##
P2DESC4 |  |  |  | ##P2DESC4## | ##P2DESC4##
P2T1 |  |  |  | ##P2T1## | ##P2T1##
P2T2 |  |  |  | ##P2T2## | ##P2T2##
P2T1TYPE |  |  |  | ##P2T1TYPE## | ##P2T1TYPE##
P2T2TYPE |  |  |  | ##P2T2TYPE## | ##P2T2TYPE##
P3NAME |  |  |  | ##P3NAME## | ##P3NAME##
P3RACK |  |  |  | ##P3RACK## | ##P3RACK##
P3SLOT |  |  |  | ##P3SLOT## | ##P3SLOT##
P3CHAN |  |  |  | ##P3CHAN## | ##P3CHAN##
P3MFG |  |  |  | 2 | 2
P3CATN |  |  |  | ##P3CATN## | ##P3CATN##
P3CATD |  |  |  | ##P3CATD## | ##P3CATD##
P3CATD2 |  |  |  | ##P3CATD2## | ##P3CATD2##
P3TAG |  |  |  | ##P3TAG## | ##P3TAG##
P3DESC2 |  |  |  | ##P3DESC2## | ##P3DESC2##
P3DESC3 |  |  |  | ##P3DESC3## | ##P3DESC3##
P3DESC4 |  |  |  | ##P3DESC4## | ##P3DESC4##
P3T1 |  |  |  | ##P3T1## | ##P3T1##
P3T2 |  |  |  | ##P3T2## | ##P3T2##
P3T1TYPE |  |  |  | ##P3T1TYPE## | ##P3T1TYPE##
P3T2TYPE |  |  |  | ##P3T2TYPE## | ##P3T2TYPE##
P4NAME |  |  |  | ##P4NAME## | ##P4NAME##
P4RACK |  |  |  | ##P4RACK## | ##P4RACK##
P4SLOT |  |  |  | ##P4SLOT## | ##P4SLOT##
P4CHAN |  |  |  | ##P4CHAN## | ##P4CHAN##
P4MFG |  |  |  | 2 | 2
P4CATN |  |  |  | ##P4CATN## | ##P4CATN##
P4CATD |  |  |  | ##P4CATD## | ##P4CATD##
P4CATD2 |  |  |  | ##P4CATD2## | ##P4CATD2##
P4TAG |  |  |  | ##P4TAG## | ##P4TAG##
P4DESC2 |  |  |  | ##P4DESC2## | ##P4DESC2##
P4DESC3 |  |  |  | ##P4DESC3## | ##P4DESC3##
P4DESC4 |  |  |  | ##P4DESC4## | ##P4DESC4##
P4T1 |  |  |  | ##P4T1## | ##P4T1##
P4T2 |  |  |  | ##P4T2## | ##P4T2##
P4T1TYPE |  |  |  | ##P4T1TYPE## | ##P4T1TYPE##
P4T2TYPE |  |  |  | ##P4T2TYPE## | ##P4T2TYPE##
D1TAG | ##D1TAG## | ##D1TAG## | ##D1TAG##
D1DESC2 | POWERFLEX 753 SERIES VSD | POWERFLEX 753 SERIES VSD | POWERFLEX 753 SERIES VSD
D1DESC3 | ##D1DESC3## | ##D1DESC3## | ##D1DESC3##
D1DESC4
D1TYPE
D1T1
D1T2
D1MFG
D1CATN | ##D1CATN## | ##D1CATN## | ##D1CATN##
D1CATD | ##D1CATD## | ##D1CATD## | ##D1CATD##
D1KW | ##D1KW## | ##D1KW## | ##D1KW##
D2TAG | ##D2TAG## | ##D2TAG## | ##D2TAG##
D2DESC2
D2DESC3
D2DESC4
D2TYPE
D2T1
D2T2
D2MFG
D2CATN | ##D2CATN## | ##D2CATN## | ##D2CATN##
D2CATD | ##D2CATD## | ##D2CATD## | ##D2CATD##
D3TAG | ##D3TAG## | ##D3TAG## | ##D3TAG##
D3DESC2 | ##D3DESC2## | ##D3DESC2## | ##D3DESC2##
D3DESC3 | ##D3DESC3## | ##D3DESC3## | ##D3DESC3##
D3DESC4 | ##D3DESC4## | ##D3DESC4## | ##D3DESC4##
D3KW | ##D3KW## | ##D3KW## | ##D3KW##
D3TYPE
D3T1
D3T2
D3MFG
D3CATN | ##D3CATN## | ##D3CATN## | ##D3CATN##
D3CATD | ##D3CATD## | ##D3CATD## | ##D3CATD##
C1TAG | ##C1TAG## | ##C1TAG## | ##C1TAG##
C1CATN | ##C1CATN## | ##C1CATN## | ##C1CATN##
C1CATD | ##C1CATD## | ##C1CATD## | ##C1CATD##
C1CORE1 | RD | RD | RD
C1CORE2 | WH | WH | WH
C1CORE3 | BU | BU | BU
C1CORE4 | GN/YL | GN/YL | GN/YL
C1CORE5
C1CORE6
C1CORE7
C2TAG | ##C2TAG## | ##C2TAG## | ##C2TAG##
C2CATN | ##C2CATN## | ##C2CATN## | ##C2CATN##
C2CATD | ##C2CATD## | ##C2CATD## | ##C2CATD##
C2CORE1 | RD | RD | RD
C2CORE2 | WH | WH | WH
C2CORE3 | BU | BU | BU
C2CORE4 | GN/YL | GN/YL | GN/YL
C2CORE5
C3TAG | ##C3TAG## | ##C3TAG##
C3CATN | ##C3CATN## | ##C3CATN##
C3CATD | ##C3CATD## | ##C3CATD##
C3CORE1 | RD | RD
C3CORE2 | WH | WH
C3CORE3 | BU | BU
C3CORE4 | GN/YL | GN/YL
C3CORE5
C4TAG | ##C4TAG## |  | ##C4TAG##
C5TAG |  |  |  | ##C5TAG## | ##C5TAG##
C6TAG |  |  |  | ##C6TAG## | ##C6TAG##
Note on A1: Author: Basic DBF structure outlined on this sheet. Create new prototypes by entering its name into a Column Header.

## TAG_DATA
{Note} | Prototype Mapping |  | Z_DRAWING |  |  | X_PANEL |  |  |  |  | 24V Connections |  |  |  |  | 230V Connections |  |  |  |  | P_PANEL | Q_PROTECTION | [7 empty] | P_IO | [58 empty] | P_IO | D_DEVICES | [5 empty] | DEVICE 2 | DEVICE 2 |  | DEVICE 3 | [6 empty] | D_DEVICES | C_CABLE
Tag | Typical | ProtoName | PREFIX | DRAWING | DRAWING2 | X1NAME | X1DESC | X2NAME | X2DESC | X3NAME | X1VDC24 | X1VDC0 | X1XIO | X1XIOF | X1XIOK | X1V230 | X1N230 | X1XDB | X1XDBF | X1XDBK | X1XDBQ | Q1CATN | Q1CATD | Q1NAME1 | Q1NAME2 | Q1TCATN | Q1TCATD | Q1TNAME | Q1TSETTO | P1NAME | P1RACK | P1SLOT | P1CHAN | P1CATN | P1CATD | P1CATD2 | P1TAG | P1DESC2 | P1DESC3 | P1DESC4 | P1T1 | P1T2 | P1T1TYPE | P1T2TYPE | P2NAME | P2RACK | P2SLOT | P2CHAN | P2CATN | P2CATD | P2CATD2 | P2TAG | P2DESC2 | P2DESC3 | P2DESC4 | P2T1 | P2T2 | P2T1TYPE | P2T2TYPE | P3NAME | P3RACK | P3SLOT | P3CHAN | P3CATN | P3CATD | P3CATD2 | P3TAG | P3DESC2 | P3DESC3 | P3DESC4 | P3T1 | P3T2 | P3T1TYPE | P3T2TYPE | P4NAME | P4RACK | P4SLOT | P4CHAN | P4CATN | P4CATD | P4CATD2 | P4TAG | P4DESC2 | P4DESC3 | P4DESC4 | P4T1 | P4T2 | P4T1TYPE | P4T2TYPE | D1TAG | D1DESC2 | D1DESC3 | D1CATN | D1CATD | D1KW | D2TAG | D2CATN | D2CATD | D3TAG | D3DESC2 | D3DESC3 | D3DESC4 | D3TYPE | D3CATN | D3CATD | D3KW | C1TAG | C1CATN | C1CATD | C2TAG | C2CATN | C2CATD | C3TAG | C3CATN | C3CATD | C4TAG | C5TAG | C6TAG | Notes
BB1EM001 | FRQ_DIR | POWERFLEX_TH | 38025-ELE | 01-500._L0 | 01-400._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15000 | F1500 |  | Q1500 | LV430834 | 3P CIRCUIT BREAKER, NSX160H, 150A, MA150 70kA | SCHNEIDER NSX160H/MA150 | COMPACT NSX | LV430500 | 3P TRIP UNIT, MA150, NSX160, 160A | MA150 | 150A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM001_VSD |  | 75kW, 400VAC | 20F11GC140AA0NNNNN | PowerFlex 753 Series VSD, 75kW, 400VAC | 75 |  |  |  | BB1EM001 | FEED WATER PUMP 1 |  |  | MOTOR | MOTOR 75kW | MOTOR 75kW, 3 PHASE | 75 | <KPA_MCC>/T5R/2 BB1EM001 | 70-3C+E | 70mm^2 - 3C+E | <KPA_MCC>/T5R/2 BB1EM001_VSD/1 | 70-3C+E-V | 70mm^2 - 3C+E - VSD |  |  |  | BB1EM001/TH
BB1EM002 | FRQ_DIR | POWERFLEX_TH | 38025-ELE | 01-501._L0 | 01-401._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15010 | F1501 |  | Q1501 | LV430834 | 3P CIRCUIT BREAKER, NSX160H, 150A, MA150 70kA | SCHNEIDER NSX160H/MA150 | COMPACT NSX | LV430500 | 3P TRIP UNIT, MA150, NSX160, 160A | MA150 | 150A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM002_VSD |  | 75kW, 400VAC | 20F11GC140AA0NNNNN | PowerFlex 753 Series VSD, 75kW, 400VAC | 75 |  |  |  | BB1EM002 | FEED WATER PUMP 2 |  |  | MOTOR | MOTOR 75kW | MOTOR 75kW, 3 PHASE | 75 | <KPA_MCC>/T4F/4 BB1EM002 | 70-3C+E | 70mm^2 - 3C+E | <KPA_MCC>/T4F/4 BB1EM002_VSD/1 | 70-3C+E-V | 70mm^2 - 3C+E - VSD |  |  |  | BB1EM002/TH
BB1EM400 | FRQ_DIR | POWERFLEX_TH | 38025-ELE | 01-502._L0 | 01-402._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15020 | F1502 |  | Q1502 | LV432776 | 3P CIRCUIT BREAKER, NSX400N, 320A, ML2.3 M 50kA | SCHNEIDER NSX400N/ML2.3 M | COMPACT NSX | LV432072 | Micrologic 2.3-M 320 A, for Compact NSX (MOTOR) | ML2.3 M | 320A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM400_VSD |  | 132kW, 400VAC | 20F11GC260AA0NNNNN | PowerFlex 1323 Series VSD, 132kW, 400VAC | 132 |  |  |  | BB1EM400 | PRIMARY AIR FAN |  |  | MOTOR | MOTOR 132kW | MOTOR 132kW, 3 PHASE | 132 | <KPA_MCC>/T5R/1 BB1EM400 | 150-3C+E | 150mm^2 - 3C+E | <KPA_MCC>/T5R/1 BB1EM400_VSD/1 | 150-3C+E-V | 150mm^2 - 3C+E - VSD |  |  |  | BB1EM400/TH
BB1EM401 | FRQ_DIR | POWERFLEX_TH | 38025-ELE | 01-503._L0 | 01-403._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15030 | F1503 |  | Q1503 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 13 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM401_ISOLATOR | EXHAUST FAN 1 ISOLATOR |  |  | V+ | 02 | 24VDC | DI | [7 empty] | BB1EM402 | COMPRESSOR 1 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM402_ISOLATOR | EXHAUST FAN 2 ISOLATOR |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM403 | COMPRESSOR 2 |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM401_VSD |  | 45kW, 400VAC | 20F11GC085AA0NNNNN | PowerFlex 753 Series VSD, 45kW, 400VAC | 45 |  |  |  | BB1EM401 | SECONDARY AIR FAN |  |  | MOTOR | MOTOR 45kW | MOTOR 45kW, 3 PHASE | 45 | <KPA_MCC>/T5R/3 BB1EM401 | 25-3C+E | 25mm^2 - 3C+E | <KPA_MCC>/T5R/3 BB1EM401_VSD/1 | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | BB1EM401/TH
BB1EM550 | FRQ_DIR | POWERFLEX_TH | 38025-ELE | 01-504._L0 | 01-404._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15040 | F1504 |  | Q1504 | LV430834 | 3P CIRCUIT BREAKER, NSX160H, 150A, MA150 70kA | SCHNEIDER NSX160H/MA150 | COMPACT NSX | LV430500 | 3P TRIP UNIT, MA150, NSX160, 160A | MA150 | 150A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM550_VSD |  | 75kW, 400VAC | 20F11GC140AA0NNNNN | PowerFlex 753 Series VSD, 75kW, 400VAC | 75 |  |  |  | BB1EM550 | FLUE GAS FAN |  |  | MOTOR | MOTOR 75kW | MOTOR 75kW, 3 PHASE | 75 | <KPA_MCC>/T1F/2 BB1EM550 | 70-3C+E | 70mm^2 - 3C+E | <KPA_MCC>/T1F/2 BB1EM550_VSD/1 | 70-3C+E-V | 70mm^2 - 3C+E - VSD |  |  |  | BB1EM550/TH
BB1EM603 | FRQ_DIRH | POWERFLEX_TH | 38025-ELE | 01-505._L0 | 01-405._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15050 | F1505 |  | Q1505 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 01 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM603_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_MODE | V+ | 00 | 24VDC | DI | RIO_ | 01 | 01 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM603_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_RUN | V+ | 01 | 24VDC | DI | RIO_ | 01 | 01 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM603_ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | ISOLATOR | V+ | 02 | 24VDC | DI | RIO_ | 01 | 01 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM604_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_MODE | V+ | 03 | 24VDC | DI | BB1EM603_VSD |  | 37kW, 400VAC | 20F11GC072AA0NNNNN | PowerFlex 753 Series VSD, 37kW, 400VAC | 37 |  |  |  | BB1EM603 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  | MOTOR | MOTOR 37kW | MOTOR 37kW, 3 PHASE | 37 | <KPA_MCC>/T1F/3 BB1EM603 | 25-3C+E | 25mm^2 - 3C+E | <KPA_MCC>/T1F/3 BB1EM603_VSD/1 | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | BB1EM603/TH
BB1EM604 | FRQ_DIRH | POWERFLEX_TH | 38025-ELE | 01-506._L0 | 01-406._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15060 | F1506 |  | Q1506 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 01 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM604_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_MODE | V+ | 03 | 24VDC | DI | RIO_ | 01 | 02 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM604_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_RUN | V+ | 00 | 24VDC | DI | RIO_ | 01 | 02 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM604_ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | ISOLATOR | V+ | 01 | 24VDC | DI | RIO_ | 01 | 02 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM605_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_MODE | V+ | 02 | 24VDC | DI | BB1EM604_VSD |  | 37kW, 400VAC | 20F11GC072AA0NNNNN | PowerFlex 753 Series VSD, 37kW, 400VAC | 37 |  |  |  | BB1EM604 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  | MOTOR | MOTOR 37kW | MOTOR 37kW, 3 PHASE | 37 | <KPA_MCC>/T1F/4 BB1EM604 | 25-3C+E | 25mm^2 - 3C+E | <KPA_MCC>/T1F/4 BB1EM604_VSD/1 | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | BB1EM604/TH
BB1EM605 | FRQ_DIRH | POWERFLEX_TH | 38025-ELE | 01-507._L0 | 01-407._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15070 | F1507 |  | Q1507 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 02 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM605_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_MODE | V+ | 02 | 24VDC | DI | RIO_ | 01 | 02 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM605_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_RUN | V+ | 03 | 24VDC | DI | RIO_ | 01 | 03 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM605_ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | ISOLATOR | V+ | 00 | 24VDC | DI | RIO_ | 01 | 03 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM658_LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | BB1EM605_VSD |  | 37kW, 400VAC | 20F11GC072AA0NNNNN | PowerFlex 753 Series VSD, 37kW, 400VAC | 37 |  |  |  | BB1EM605 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  | MOTOR | MOTOR 37kW | MOTOR 37kW, 3 PHASE | 37 | <KPA_MCC>/T1F/5 BB1EM605 | 25-3C+E | 25mm^2 - 3C+E | <KPA_MCC>/T1F/5 BB1EM605_VSD/1 | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | BB1EM605/TH
BB1EM658 | FRQ_REVH | POWERFLEX_ISO_TH | 38025-ELE | 01-508._L0 | 01-408._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15080 | F1508 |  | Q1508 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | RIO_ | 01 | 03 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM658_LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 03 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM658_LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 03 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM658_LOCAL_RUN_REV | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 04 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM658_ISOLATOR | SCRAPER CONVEYOR 1 | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM658_VSD |  | 15kW, 400VAC | 20F11GC030AA0NNNNN | PowerFlex 753 Series VSD, 15kW, 400VAC | 15 | BB1EM658 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | BB1EM658 | SCRAPER CONVEYOR 1 |  |  | MOTOR | MOTOR 15kW | MOTOR 15kW, 3 PHASE | 15 | <KPA_MCC>/T4F/5 BB1EM658 | 10-3C+E | 10mm^2 - 3C+E | <KPA_MCC>/T4F/5 BB1EM658_VSD/1 | 10-3C+E-V | 10mm^2 - 3C+E - VSD | <KPA_MCC>/T4F/5 BB1EM658_VSD/2 | 10-3C+E-V | 10mm^2 - 3C+E - VSD | BB1EM658/TH
BB1EM659 | FRQ_REVH | POWERFLEX_ISOL | 38025-ELE | 01-509._L0 | 01-409._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q104 | 0 | 15090 | F1509 |  | Q1509 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | RIO_ | 01 | 04 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM659_LOCAL_MODE | BELT CONVEYOR | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 04 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM659_LOCAL_RUN_FWD | BELT CONVEYOR | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 04 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM659_LOCAL_RUN_REV | BELT CONVEYOR | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 05 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM659_ISOLATOR | BELT CONVEYOR | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM659_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | 4 | BB1EM659 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM659 | BELT CONVEYOR |  |  | MOTOR | MOTOR 4kW | MOTOR 4kW, 3 PHASE | 4 | <KPA_MCC>/T1R BB1EM659 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T1R BB1EM659_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T1R BB1EM659_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM659/TH
BB1EM676 | FRQ_REVH | POWERFLEX_ISOL | 38025-ELE | 01-510._L0 | 01-410._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q104 | 0 | 15100 | F1510 |  | Q1510 | GV2L22 | 3P CIRCUIT BREAKER, TESYS GV2L, 25A | SCHNEIDER GV2L22 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 22A | RIO_ | 01 | 05 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM676_LOCAL_MODE | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 05 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM676_LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 05 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM676_LOCAL_RUN_REV | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 06 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM676_ISOLATOR | DISC SCREEN DRIVE 2 | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM676_VSD |  | 7.5kW, 400VAC | 20F11GC022AA0NNNNN | PowerFlex 753 Series VSD, 11kW, 400VAC | 7.5 | BB1EM676 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM676 | DISC SCREEN DRIVE 2 |  |  | MOTOR | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE | 7.5 | <KPA_MCC>/T1R BB1EM676 | 4-3C+E | 4mm^2 - 3C+E | <KPA_MCC>/T1R BB1EM676_VSD/1 | 4-3C+E-V | 4mm^2 - 3C+E - VSD | <KPA_MCC>/T1R BB1EM676_VSD/2 | 4-3C+E-V | 4mm^2 - 3C+E - VSD | BB1EM676/TH
BB1EM672 | FRQ_REVH | POWERFLEX_ISO_TH | 38025-ELE | 01-511._L0 | 01-411._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15110 | F1511 |  | Q1511 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | RIO_ | 01 | 06 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM672_LOCAL_MODE | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 06 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM672_LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 06 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM672_LOCAL_RUN_REV | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 07 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM672_ISOLATOR | SCRAPER CONVEYOR 2 | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM672_VSD |  | 18,5kW, 400VAC | 20F11GC043AA0NNNNN | PowerFlex 753 Series VSD, 22kW, 400VAC | 18,5 | BB1EM672 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | BB1EM672 | SCRAPER CONVEYOR 2 |  |  | MOTOR | MOTOR 18,5kW | MOTOR 18,5kW, 3 PHASE | 18,5 | <KPA_MCC>/T4F/6 BB1EM672 | 10-3C+E | 10mm^2 - 3C+E | <KPA_MCC>/T4F/6 BB1EM672_VSD/1 | 10-3C+E-V | 10mm^2 - 3C+E - VSD | <KPA_MCC>/T4F/6 BB1EM672_VSD/2 | 10-3C+E-V | 10mm^2 - 3C+E - VSD | BB1EM672/TH
BB1EM662 | FRQ_REVH | POWERFLEX_ISO_TH | 38025-ELE | 01-512._L0 | 01-412._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15120 | F1512 |  | Q1512 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 07 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM662_LOCAL_MODE | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 07 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM662_LOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 07 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM662_LOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 08 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM662_ISOLATOR | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM662_VSD |  | 22kW, 400VAC | 20F11GC060AA0NNNNN | PowerFlex 753 Series VSD, 30kW, 400VAC | 22 | BB1EM662 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | BB1EM662 | FUEL SILO SCREW DISCHARGE |  |  | MOTOR | MOTOR 22kW | MOTOR 22kW, 3 PHASE | 22 | <KPA_MCC>/T4F/7 BB1EM662 | 16-3C+E | 16mm^2 - 3C+E | <KPA_MCC>/T4F/7 BB1EM662_VSD/1 | 16-3C+E-V | 16mm^2 - 3C+E - VSD | <KPA_MCC>/T4F/7 BB1EM662_VSD/2 | 16-3C+E-V | 16mm^2 - 3C+E - VSD | BB1EM662/TH
BB1EM650 | FRQ_REVH | POWERFLEX_ISOL | 38025-ELE | 01-513._L0 | 01-413._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q104 | 0 | 15130 | F1513 |  | Q1513 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | RIO_ | 01 | 08 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM650_LOCAL_MODE | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 08 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM650_LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 08 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM650_LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 09 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM650_ISOLATOR | SLEWING MOTOR FOR SCREW | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM650_VSD |  | 4kW, 400VAC | 20F11GC5P7AA0NNNNN | PowerFlex 753 Series VSD, 2.2kW, 400VAC | 2.2 | BB1EM650 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM650 | SLEWING MOTOR FOR SCREW |  |  | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | 2.2 | <KPA_MCC>/T1R BB1EM650 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T1R BB1EM650_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T1R BB1EM650_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM650/TH
BB1EM663 | FRQ_REVH | POWERFLEX_ISOL | 38025-ELE | 01-514._L0 | 01-414._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q105 | 0 | 15140 | F1514 |  | Q1514 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | RIO_ | 01 | 09 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM663_LOCAL_MODE | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 09 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM663_LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 09 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM663_LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 10 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM663_ISOLATOR | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM663_VSD |  | 4kW, 400VAC | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | 4 | BB1EM663 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM663 | FUEL SILO CROSS CONVEYOR |  |  | MOTOR | MOTOR 4kW | MOTOR 4kW, 3 PHASE | 4 | <KPA_MCC>/T4R BB1EM663 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T4R BB1EM663_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T4R BB1EM663_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM663/TH
BB1EM664 | FRQ_REVH | POWERFLEX_ISOL | 38025-ELE | 01-515._L0 | 01-415._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q105 | 0 | 15150 | F1515 |  | Q1515 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | RIO_ | 01 | 10 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM664_LOCAL_MODE | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 10 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM664_LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 10 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM664_LOCAL_RUN_REV | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 11 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM664_ISOLATOR | FUEL FEEDING SCREW 1 | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM664_VSD |  | 5.5kW, 400VAC | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | 5.5 | BB1EM664 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM664 | FUEL FEEDING SCREW 1 |  |  | MOTOR | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE | 5.5 | <KPA_MCC>/T4R BB1EM664 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T4R BB1EM664_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T4R BB1EM664_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM664/TH
BB1EM665 | FRQ_REVH | POWERFLEX_ISOL | 38025-ELE | 01-516._L0 | 01-416._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q105 | 0 | 15160 | F1516 |  | Q1516 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | RIO_ | 01 | 11 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM665_LOCAL_MODE | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 11 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM665_LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 11 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM665_LOCAL_RUN_REV | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 12 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM665_ISOLATOR | FUEL FEEDING SCREW 2 | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM665_VSD |  | 5.5kW, 400VAC | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | 5.5 | BB1EM665 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM665 | FUEL FEEDING SCREW 2 |  |  | MOTOR | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE | 5.5 | <KPA_MCC>/T4R BB1EM665 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T4R BB1EM665_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T4R BB1EM665_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM665/TH
BB1EM852 | FRQ_REVH | POWERFLEX_ISOL | 38025-ELE | 01-517._L0 | 01-417._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q105 | 0 | 15170 | F1517 |  | Q1517 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | RIO_ | 01 | 12 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM852_LOCAL_MODE | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | V+ | 01 | 24VDC | DI | RIO_ | 01 | 12 | 02 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1EM852_LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | V+ | 02 | 24VDC | DI | RIO_ | 01 | 12 | 03 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1EM852_LOCAL_RUN_REV | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | V+ | 03 | 24VDC | DI | RIO_ | 01 | 13 | 00 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1EM852_ISOLATOR | BOTTOM ASH CONVEYOR | ISOLATOR |  | V+ | 00 | 24VDC | DI | BB1EM852_VSD |  | 4kW, 400VAC | 20F11GC5P7AA0NNNNN | PowerFlex 753 Series VSD, 2.2kW, 400VAC | 2.2 | BB1EM852 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM852 | BOTTOM ASH CONVEYOR |  |  | MOTOR | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | 2.2 | <KPA_MCC>/T4R BB1EM852 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T4R BB1EM852_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T4R BB1EM852_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM852/TH
BB1EM606 | FRQ_DIR | POWERFLEX_TH | 38025-ELE | 01-518._L0 | 01-418._L0 | <KPA_MCC> | MAIN MCC | 0 | 0 | [6 empty] | Q100 | 0 | 15180 | F1518 |  | Q1518 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | RIO_ | 01 | 13 | 01 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1EM606_ISOLATOR | DUST EXTRACTION FAN | ISOLATOR |  | V+ | 01 | 24VDC | DI | [7 empty] | BB1EH600_ISOLATOR | ELECTRIC HEATER | HYDRAULIC UNIT ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM651_ISOLATOR | FUEL SILO DUST FILTER FAN | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | BB1EM008_ISOLATOR | CONVEYOR COOLING PUMP | ISOLATOR |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | BB1EM606_VSD |  | 30kW, 400VAC | 20F11GC072AA0NNNNN | PowerFlex 753 Series VSD, 37kW, 400VAC | 30 |  |  |  | BB1EM606 | DUST EXTRACTION FAN |  |  | MOTOR | MOTOR 30kW | MOTOR 30kW, 3 PHASE | 30 | <KPA_MCC>/T5R/4 BB1EM606 | 16-3C+E | 16mm^2 - 3C+E | <KPA_MCC>/T5R/4 BB1EM606_VSD/1 | 16-3C+E-V | 16mm^2 - 3C+E - VSD |  |  |  | BB1EM606/TH
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
| #N/A | [28 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | [7 empty] | #N/A |  |  |  | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
Note on A1: Author: This is the primary output sheet. All fields are generated, no user input required unless overriding a generated value

## Z_DRAWING
Tag Info | Drawing Filename
_Tag | _Type | Prefix | SubProject | _Base | _Index | _Number | _Append | Drawing | _Base2 | _Index2 | _Number2 | _Append2 | Drawing2 | testIndex | Notes
DETAIL | ELE | 38025-ELE | 1 | 100 | 0 | 100 |  | 01-100._L0 |  | 0 |  |  | 01-._L0 | 1100 | 1
DETAIL | ELE | 38025-ELE | 1 | 100 | 1 | 101 |  | 01-101._L0 |  | 1 |  |  | 01-._L0 | 1101 | 1
DETAIL | ELE | 38025-ELE | 1 | 100 | 2 | 102 |  | 01-102._L0 |  | 2 |  |  | 01-._L0 | 1102 | 1
DETAIL | ELE | 38025-ELE | 1 | 100 | 3 | 103 |  | 01-103._L0 |  | 3 |  |  | 01-._L0 | 1103 | 1
DETAIL | ELE | 38025-ELE | 1 | 100 | 4 | 104 |  | 01-104._L0 |  | 4 |  |  | 01-._L0 | 1104 | 1
DETAIL | ELE | 38025-ELE | 1 | 100 | 5 | 105 |  | 01-105._L0 |  | 5 |  |  | 01-._L0 | 1105 | 1
DETAIL | ELE | 38025-ELE | 1 | 100 | 6 | 106 |  | 01-106._L0 |  | 6 |  |  | 01-._L0 | 1106 | 1
DETAIL | ELE | 38025-ELE | 1 | 100 | 7 | 107 |  | 01-107._L0 | 400 | 7 | 407 |  | 01-407._L0 | 1107 | 1407
DETAIL | ELE | 38025-ELE | 1 | 100 | 8 | 108 |  | 01-108._L0 | 400 | 8 | 408 |  | 01-408._L0 | 1108 | 1408
DETAIL | ELE | 38025-ELE | 1 | 100 | 9 | 109 |  | 01-109._L0 | 400 | 9 | 409 |  | 01-409._L0 | 1109 | 1409
BB1EM001 | ELE | 38025-ELE | 1 | 500 | 0 | 500 |  | 01-500._L0 | 400 | 0 | 400 |  | 01-400._L0 | 1500 | 1400
BB1EM002 | ELE | 38025-ELE | 1 | 500 | 1 | 501 |  | 01-501._L0 | 400 | 1 | 401 |  | 01-401._L0 | 1501 | 1401
BB1EM400 | ELE | 38025-ELE | 1 | 500 | 2 | 502 |  | 01-502._L0 | 400 | 2 | 402 |  | 01-402._L0 | 1502 | 1402
BB1EM401 | ELE | 38025-ELE | 1 | 500 | 3 | 503 |  | 01-503._L0 | 400 | 3 | 403 |  | 01-403._L0 | 1503 | 1403
BB1EM550 | ELE | 38025-ELE | 1 | 500 | 4 | 504 |  | 01-504._L0 | 400 | 4 | 404 |  | 01-404._L0 | 1504 | 1404
BB1EM603 | ELE | 38025-ELE | 1 | 500 | 5 | 505 |  | 01-505._L0 | 400 | 5 | 405 |  | 01-405._L0 | 1505 | 1405
BB1EM604 | ELE | 38025-ELE | 1 | 500 | 6 | 506 |  | 01-506._L0 | 400 | 6 | 406 |  | 01-406._L0 | 1506 | 1406
BB1EM605 | ELE | 38025-ELE | 1 | 500 | 7 | 507 |  | 01-507._L0 | 400 | 7 | 407 |  | 01-407._L0 | 1507 | 1407
BB1EM658 | ELE | 38025-ELE | 1 | 500 | 8 | 508 |  | 01-508._L0 | 400 | 8 | 408 |  | 01-408._L0 | 1508 | 1408
BB1EM659 | ELE | 38025-ELE | 1 | 500 | 9 | 509 |  | 01-509._L0 | 400 | 9 | 409 |  | 01-409._L0 | 1509 | 1409
BB1EM676 | ELE | 38025-ELE | 1 | 500 | 10 | 510 |  | 01-510._L0 | 400 | 10 | 410 |  | 01-410._L0 | 1510 | 1410
BB1EM672 | ELE | 38025-ELE | 1 | 500 | 11 | 511 |  | 01-511._L0 | 400 | 11 | 411 |  | 01-411._L0 | 1511 | 1411
BB1EM662 | ELE | 38025-ELE | 1 | 500 | 12 | 512 |  | 01-512._L0 | 400 | 12 | 412 |  | 01-412._L0 | 1512 | 1412
BB1EM650 | ELE | 38025-ELE | 1 | 500 | 13 | 513 |  | 01-513._L0 | 400 | 13 | 413 |  | 01-413._L0 | 1513 | 1413
BB1EM663 | ELE | 38025-ELE | 1 | 500 | 14 | 514 |  | 01-514._L0 | 400 | 14 | 414 |  | 01-414._L0 | 1514 | 1414
BB1EM664 | ELE | 38025-ELE | 1 | 500 | 15 | 515 |  | 01-515._L0 | 400 | 15 | 415 |  | 01-415._L0 | 1515 | 1415
BB1EM665 | ELE | 38025-ELE | 1 | 500 | 16 | 516 |  | 01-516._L0 | 400 | 16 | 416 |  | 01-416._L0 | 1516 | 1416
BB1EM852 | ELE | 38025-ELE | 1 | 500 | 17 | 517 |  | 01-517._L0 | 400 | 17 | 417 |  | 01-417._L0 | 1517 | 1417
BB1EM606 | ELE | 38025-ELE | 1 | 500 | 18 | 518 |  | 01-518._L0 | 400 | 18 | 418 |  | 01-418._L0 | 1518 | 1418
| ELE | 38025-ELE | 1 | 500 | 19 | 519 |  | 01-519._L0 | 400 | 19 | 419 |  | 01-419._L0 | 1519 | 1419
| ELE | 38025-ELE | 1 |  | 20 |  |  | 01-._L0 |  | 20 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 21 |  |  | 01-._L0 |  | 21 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 22 |  |  | 01-._L0 |  | 22 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 23 |  |  | 01-._L0 |  | 23 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 24 |  |  | 01-._L0 |  | 24 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 25 |  |  | 01-._L0 |  | 25 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 26 |  |  | 01-._L0 |  | 26 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 27 |  |  | 01-._L0 |  | 27 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 28 |  |  | 01-._L0 |  | 28 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 29 |  |  | 01-._L0 |  | 29 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 30 |  |  | 01-._L0 |  | 30 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 31 |  |  | 01-._L0 |  | 31 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 32 |  |  | 01-._L0 |  | 32 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 33 |  |  | 01-._L0 |  | 33 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 34 |  |  | 01-._L0 |  | 34 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 35 |  |  | 01-._L0 |  | 35 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 36 |  |  | 01-._L0 |  | 36 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 37 |  |  | 01-._L0 |  | 37 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 38 |  |  | 01-._L0 |  | 38 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 39 |  |  | 01-._L0 |  | 39 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 40 |  |  | 01-._L0 |  | 40 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 41 |  |  | 01-._L0 |  | 41 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 42 |  |  | 01-._L0 |  | 42 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 43 |  |  | 01-._L0 |  | 43 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 44 |  |  | 01-._L0 |  | 44 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 45 |  |  | 01-._L0 |  | 45 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 46 |  |  | 01-._L0 |  | 46 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 47 |  |  | 01-._L0 |  | 47 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 48 |  |  | 01-._L0 |  | 48 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 49 |  |  | 01-._L0 |  | 49 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 50 |  |  | 01-._L0 |  | 50 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 51 |  |  | 01-._L0 |  | 51 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 52 |  |  | 01-._L0 |  | 52 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 53 |  |  | 01-._L0 |  | 53 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 54 |  |  | 01-._L0 |  | 54 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 55 |  |  | 01-._L0 |  | 55 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 56 |  |  | 01-._L0 |  | 56 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 57 |  |  | 01-._L0 |  | 57 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 58 |  |  | 01-._L0 |  | 58 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 59 |  |  | 01-._L0 |  | 59 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 60 |  |  | 01-._L0 |  | 60 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 61 |  |  | 01-._L0 |  | 61 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 62 |  |  | 01-._L0 |  | 62 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 63 |  |  | 01-._L0 |  | 63 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 64 |  |  | 01-._L0 |  | 64 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 65 |  |  | 01-._L0 |  | 65 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 66 |  |  | 01-._L0 |  | 66 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 67 |  |  | 01-._L0 |  | 67 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 68 |  |  | 01-._L0 |  | 68 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 69 |  |  | 01-._L0 |  | 69 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 70 |  |  | 01-._L0 |  | 70 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 71 |  |  | 01-._L0 |  | 71 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 72 |  |  | 01-._L0 |  | 72 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 73 |  |  | 01-._L0 |  | 73 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 74 |  |  | 01-._L0 |  | 74 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 75 |  |  | 01-._L0 |  | 75 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 76 |  |  | 01-._L0 |  | 76 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 77 |  |  | 01-._L0 |  | 77 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 78 |  |  | 01-._L0 |  | 78 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 79 |  |  | 01-._L0 |  | 79 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 80 |  |  | 01-._L0 |  | 80 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 81 |  |  | 01-._L0 |  | 81 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 82 |  |  | 01-._L0 |  | 82 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 83 |  |  | 01-._L0 |  | 83 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 84 |  |  | 01-._L0 |  | 84 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 85 |  |  | 01-._L0 |  | 85 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 86 |  |  | 01-._L0 |  | 86 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 87 |  |  | 01-._L0 |  | 87 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 88 |  |  | 01-._L0 |  | 88 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 89 |  |  | 01-._L0 |  | 89 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 90 |  |  | 01-._L0 |  | 90 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 91 |  |  | 01-._L0 |  | 91 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 92 |  |  | 01-._L0 |  | 92 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 93 |  |  | 01-._L0 |  | 93 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 94 |  |  | 01-._L0 |  | 94 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 95 |  |  | 01-._L0 |  | 95 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 96 |  |  | 01-._L0 |  | 96 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 97 |  |  | 01-._L0 |  | 97 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 98 |  |  | 01-._L0 |  | 98 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 99 |  |  | 01-._L0 |  | 99 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 100 |  |  | 01-._L0 |  | 100 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 101 |  |  | 01-._L0 |  | 101 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 102 |  |  | 01-._L0 |  | 102 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 103 |  |  | 01-._L0 |  | 103 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 104 |  |  | 01-._L0 |  | 104 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 105 |  |  | 01-._L0 |  | 105 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 106 |  |  | 01-._L0 |  | 106 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 107 |  |  | 01-._L0 |  | 107 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 108 |  |  | 01-._L0 |  | 108 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 109 |  |  | 01-._L0 |  | 109 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 110 |  |  | 01-._L0 |  | 110 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 111 |  |  | 01-._L0 |  | 111 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 112 |  |  | 01-._L0 |  | 112 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 113 |  |  | 01-._L0 |  | 113 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 114 |  |  | 01-._L0 |  | 114 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 115 |  |  | 01-._L0 |  | 115 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 116 |  |  | 01-._L0 |  | 116 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 117 |  |  | 01-._L0 |  | 117 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 118 |  |  | 01-._L0 |  | 118 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 119 |  |  | 01-._L0 |  | 119 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 120 |  |  | 01-._L0 |  | 120 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 121 |  |  | 01-._L0 |  | 121 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 122 |  |  | 01-._L0 |  | 122 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 123 |  |  | 01-._L0 |  | 123 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 124 |  |  | 01-._L0 |  | 124 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 125 |  |  | 01-._L0 |  | 125 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 126 |  |  | 01-._L0 |  | 126 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 127 |  |  | 01-._L0 |  | 127 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 128 |  |  | 01-._L0 |  | 128 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 129 |  |  | 01-._L0 |  | 129 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 130 |  |  | 01-._L0 |  | 130 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 131 |  |  | 01-._L0 |  | 131 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 132 |  |  | 01-._L0 |  | 132 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 133 |  |  | 01-._L0 |  | 133 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 134 |  |  | 01-._L0 |  | 134 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 135 |  |  | 01-._L0 |  | 135 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 136 |  |  | 01-._L0 |  | 136 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 137 |  |  | 01-._L0 |  | 137 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 138 |  |  | 01-._L0 |  | 138 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 139 |  |  | 01-._L0 |  | 139 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 140 |  |  | 01-._L0 |  | 140 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 141 |  |  | 01-._L0 |  | 141 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 142 |  |  | 01-._L0 |  | 142 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 143 |  |  | 01-._L0 |  | 143 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 144 |  |  | 01-._L0 |  | 144 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 145 |  |  | 01-._L0 |  | 145 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 146 |  |  | 01-._L0 |  | 146 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 147 |  |  | 01-._L0 |  | 147 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 148 |  |  | 01-._L0 |  | 148 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 149 |  |  | 01-._L0 |  | 149 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 150 |  |  | 01-._L0 |  | 150 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 151 |  |  | 01-._L0 |  | 151 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 152 |  |  | 01-._L0 |  | 152 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 153 |  |  | 01-._L0 |  | 153 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 154 |  |  | 01-._L0 |  | 154 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 155 |  |  | 01-._L0 |  | 155 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 156 |  |  | 01-._L0 |  | 156 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 157 |  |  | 01-._L0 |  | 157 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 158 |  |  | 01-._L0 |  | 158 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 159 |  |  | 01-._L0 |  | 159 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 160 |  |  | 01-._L0 |  | 160 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 161 |  |  | 01-._L0 |  | 161 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 162 |  |  | 01-._L0 |  | 162 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 163 |  |  | 01-._L0 |  | 163 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 164 |  |  | 01-._L0 |  | 164 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 165 |  |  | 01-._L0 |  | 165 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 166 |  |  | 01-._L0 |  | 166 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 167 |  |  | 01-._L0 |  | 167 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 168 |  |  | 01-._L0 |  | 168 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 169 |  |  | 01-._L0 |  | 169 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 170 |  |  | 01-._L0 |  | 170 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 171 |  |  | 01-._L0 |  | 171 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 172 |  |  | 01-._L0 |  | 172 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 173 |  |  | 01-._L0 |  | 173 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 174 |  |  | 01-._L0 |  | 174 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 175 |  |  | 01-._L0 |  | 175 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 176 |  |  | 01-._L0 |  | 176 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 177 |  |  | 01-._L0 |  | 177 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 178 |  |  | 01-._L0 |  | 178 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 179 |  |  | 01-._L0 |  | 179 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 180 |  |  | 01-._L0 |  | 180 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 181 |  |  | 01-._L0 |  | 181 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 182 |  |  | 01-._L0 |  | 182 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 183 |  |  | 01-._L0 |  | 183 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 184 |  |  | 01-._L0 |  | 184 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 185 |  |  | 01-._L0 |  | 185 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 186 |  |  | 01-._L0 |  | 186 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 187 |  |  | 01-._L0 |  | 187 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 188 |  |  | 01-._L0 |  | 188 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 189 |  |  | 01-._L0 |  | 189 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 190 |  |  | 01-._L0 |  | 190 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 191 |  |  | 01-._L0 |  | 191 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 192 |  |  | 01-._L0 |  | 192 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 193 |  |  | 01-._L0 |  | 193 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 194 |  |  | 01-._L0 |  | 194 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 195 |  |  | 01-._L0 |  | 195 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 196 |  |  | 01-._L0 |  | 196 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 197 |  |  | 01-._L0 |  | 197 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 198 |  |  | 01-._L0 |  | 198 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 199 |  |  | 01-._L0 |  | 199 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 200 |  |  | 01-._L0 |  | 200 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 201 |  |  | 01-._L0 |  | 201 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 202 |  |  | 01-._L0 |  | 202 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 203 |  |  | 01-._L0 |  | 203 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 204 |  |  | 01-._L0 |  | 204 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 205 |  |  | 01-._L0 |  | 205 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 206 |  |  | 01-._L0 |  | 206 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 207 |  |  | 01-._L0 |  | 207 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 208 |  |  | 01-._L0 |  | 208 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 209 |  |  | 01-._L0 |  | 209 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 210 |  |  | 01-._L0 |  | 210 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 211 |  |  | 01-._L0 |  | 211 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 212 |  |  | 01-._L0 |  | 212 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 213 |  |  | 01-._L0 |  | 213 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 214 |  |  | 01-._L0 |  | 214 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 215 |  |  | 01-._L0 |  | 215 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 216 |  |  | 01-._L0 |  | 216 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 217 |  |  | 01-._L0 |  | 217 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 218 |  |  | 01-._L0 |  | 218 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 219 |  |  | 01-._L0 |  | 219 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 220 |  |  | 01-._L0 |  | 220 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 221 |  |  | 01-._L0 |  | 221 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 222 |  |  | 01-._L0 |  | 222 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 223 |  |  | 01-._L0 |  | 223 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 224 |  |  | 01-._L0 |  | 224 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 225 |  |  | 01-._L0 |  | 225 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 226 |  |  | 01-._L0 |  | 226 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 227 |  |  | 01-._L0 |  | 227 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 228 |  |  | 01-._L0 |  | 228 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 229 |  |  | 01-._L0 |  | 229 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 230 |  |  | 01-._L0 |  | 230 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 231 |  |  | 01-._L0 |  | 231 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 232 |  |  | 01-._L0 |  | 232 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 233 |  |  | 01-._L0 |  | 233 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 234 |  |  | 01-._L0 |  | 234 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 235 |  |  | 01-._L0 |  | 235 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 236 |  |  | 01-._L0 |  | 236 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 237 |  |  | 01-._L0 |  | 237 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 238 |  |  | 01-._L0 |  | 238 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 239 |  |  | 01-._L0 |  | 239 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 240 |  |  | 01-._L0 |  | 240 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 241 |  |  | 01-._L0 |  | 241 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 242 |  |  | 01-._L0 |  | 242 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 243 |  |  | 01-._L0 |  | 243 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 244 |  |  | 01-._L0 |  | 244 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 245 |  |  | 01-._L0 |  | 245 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 246 |  |  | 01-._L0 |  | 246 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 247 |  |  | 01-._L0 |  | 247 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 248 |  |  | 01-._L0 |  | 248 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 249 |  |  | 01-._L0 |  | 249 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 250 |  |  | 01-._L0 |  | 250 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 251 |  |  | 01-._L0 |  | 251 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 252 |  |  | 01-._L0 |  | 252 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 253 |  |  | 01-._L0 |  | 253 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 254 |  |  | 01-._L0 |  | 254 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 255 |  |  | 01-._L0 |  | 255 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 256 |  |  | 01-._L0 |  | 256 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 257 |  |  | 01-._L0 |  | 257 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 258 |  |  | 01-._L0 |  | 258 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 259 |  |  | 01-._L0 |  | 259 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 260 |  |  | 01-._L0 |  | 260 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 261 |  |  | 01-._L0 |  | 261 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 262 |  |  | 01-._L0 |  | 262 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 263 |  |  | 01-._L0 |  | 263 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 264 |  |  | 01-._L0 |  | 264 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 265 |  |  | 01-._L0 |  | 265 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 266 |  |  | 01-._L0 |  | 266 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 267 |  |  | 01-._L0 |  | 267 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 268 |  |  | 01-._L0 |  | 268 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 269 |  |  | 01-._L0 |  | 269 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 270 |  |  | 01-._L0 |  | 270 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 271 |  |  | 01-._L0 |  | 271 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 272 |  |  | 01-._L0 |  | 272 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 273 |  |  | 01-._L0 |  | 273 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 274 |  |  | 01-._L0 |  | 274 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 275 |  |  | 01-._L0 |  | 275 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 276 |  |  | 01-._L0 |  | 276 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 277 |  |  | 01-._L0 |  | 277 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 278 |  |  | 01-._L0 |  | 278 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 279 |  |  | 01-._L0 |  | 279 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 280 |  |  | 01-._L0 |  | 280 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 281 |  |  | 01-._L0 |  | 281 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 282 |  |  | 01-._L0 |  | 282 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 283 |  |  | 01-._L0 |  | 283 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 284 |  |  | 01-._L0 |  | 284 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 285 |  |  | 01-._L0 |  | 285 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 286 |  |  | 01-._L0 |  | 286 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 287 |  |  | 01-._L0 |  | 287 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 288 |  |  | 01-._L0 |  | 288 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 289 |  |  | 01-._L0 |  | 289 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 290 |  |  | 01-._L0 |  | 290 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 291 |  |  | 01-._L0 |  | 291 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 292 |  |  | 01-._L0 |  | 292 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 293 |  |  | 01-._L0 |  | 293 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 294 |  |  | 01-._L0 |  | 294 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 295 |  |  | 01-._L0 |  | 295 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 296 |  |  | 01-._L0 |  | 296 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 297 |  |  | 01-._L0 |  | 297 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 298 |  |  | 01-._L0 |  | 298 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 299 |  |  | 01-._L0 |  | 299 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 300 |  |  | 01-._L0 |  | 300 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 301 |  |  | 01-._L0 |  | 301 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 302 |  |  | 01-._L0 |  | 302 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 303 |  |  | 01-._L0 |  | 303 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 304 |  |  | 01-._L0 |  | 304 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 305 |  |  | 01-._L0 |  | 305 |  |  | 01-._L0 | 1 | 1
| ELE | 38025-ELE | 1 |  | 306 |  |  | 01-._L0 |  | 306 |  |  | 01-._L0 | 1 | 1
Note on A1: Author: Generation of drawing number set is performed on this page

## X_PANEL
Tag | Description | _DeviceCount | 24VDC | 0VDC | Terminal | Fuse | 230VL1 | 230VN | DBTerminal | DBFuse | DBBreaker | Notes
KPA_FLOORX_IO | KPA NON ASSIGNED IO | 383
KPA_FLOOR0_IO | KPA LEVEL 0 REMOTE IO CABINET | 0
KPA_FLOOR1_IO | KPA LEVEL 1 REMOTE IO CABINET | 0
KPA_FLOOR2_IO | KPA LEVEL 2 REMOTE IO CABINET | 0
KPA_FLOOR3_IO | KPA LEVEL 3 REMOTE IO CABINET | 0
KPA_FLOOR4_IO | KPA LEVEL 4 REMOTE IO CABINET | 0
KPA_FUEL_STATION_IO | KPA FUEL STATION REMOTE IO CABINET | 0
<KPA_MCC> | KPA REMOTE IO INTERNAL TO MCC | 412
KPA_PLC | KPA PLC CABINET | 0
ESP_PLC | ESP PLC CABINET | 0
ESP_MCC | ESP REMOTE IO INTERNAL TO MCC | 0
0
Panel Assignment |  |  | Indices
_Drawing | _Tag | Assignment | 24VDC | 0VDC | Terminal | Fuse | 230V | 230VN | DBTerminal | DBFuse | DBBreaker | TIER | Notes | Q1CATN | Q1CATD | Q1NAME1 | Q1NAME2 | Q1TCATN | Q1TCATD | Q1TNAME | Q1TSETTO | X1NAME | X1DESC | X2NAME | X2DESC | C4NAME | C5NAME | W3NAME | W4NAME | W5NAME | W6NAME | W7NAME | W8NAME
01-100._L0 | DETAIL | <KPA_MCC> |  |  | 11000 | F1100 |  |  | 11000 | F1100 | Q100 |  | INCOMER | [8 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-101._L0 | DETAIL | <KPA_MCC> |  |  | 11010 | F1101 |  |  | 11010 | F1101 | Q101 |  | PWR MONITOR | [8 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-102._L0 | DETAIL | <KPA_MCC> |  |  | 11020 | F1102 |  |  | 11020 | F1102 | Q102 |  | AHF | [8 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-103._L0 | DETAIL | <KPA_MCC> |  |  | 11030 | F1103 |  |  | 11030 | F1103 | Q103 |  | SURGE PROTECTION | [8 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-104._L0 | DETAIL | <KPA_MCC> |  |  | 11040 | F1104 |  |  | 11040 | F1104 | Q104 |  | FEEDERS | [8 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-105._L0 | DETAIL | <KPA_MCC> |  |  | 11050 | F1105 |  |  | 11050 | F1105 | Q108 |  | FEEDERS | [8 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-106._L0 | DETAIL | <KPA_MCC> |  |  | 11060 | F1106 |  |  | 11060 | F1106 | Q111 |  | FEEDERS | [8 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-107._L0 | DETAIL | <KPA_MCC> |  |  | 11070 | F1107 |  |  | 11070 | F1107 | Q1107 | [10 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-108._L0 | DETAIL | <KPA_MCC> |  |  | 11080 | F1108 |  |  | 11080 | F1108 | Q1108 | [10 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-109._L0 | DETAIL | <KPA_MCC> |  |  | 11090 | F1109 |  |  | 11090 | F1109 | Q1109 | [10 empty] | <KPA_MCC> |  |  |  | /1 | DETAIL/ISO
01-500._L0 | BB1EM001 | <KPA_MCC> |  |  | 15000 | F1500 | Q100 |  | 15000 | F1500 | Q1500 | T5R/2 | NSX160H/MA150 | LV430834 | 3P CIRCUIT BREAKER, NSX160H, 150A, MA150 70kA | SCHNEIDER NSX160H/MA150 | COMPACT NSX | LV430500 | 3P TRIP UNIT, MA150, NSX160, 160A | MA150 | 150A | <KPA_MCC> | MAIN MCC
01-501._L0 | BB1EM002 | <KPA_MCC> |  |  | 15010 | F1501 | Q100 |  | 15010 | F1501 | Q1501 | T4F/4 | NSX160H/MA150 | LV430834 | 3P CIRCUIT BREAKER, NSX160H, 150A, MA150 70kA | SCHNEIDER NSX160H/MA150 | COMPACT NSX | LV430500 | 3P TRIP UNIT, MA150, NSX160, 160A | MA150 | 150A | <KPA_MCC> | MAIN MCC
01-502._L0 | BB1EM400 | <KPA_MCC> |  |  | 15020 | F1502 | Q100 |  | 15020 | F1502 | Q1502 | T5R/1 | NSX400N/ML2.3 M | LV432776 | 3P CIRCUIT BREAKER, NSX400N, 320A, ML2.3 M 50kA | SCHNEIDER NSX400N/ML2.3 M | COMPACT NSX | LV432072 | Micrologic 2.3-M 320 A, for Compact NSX (MOTOR) | ML2.3 M | 320A | <KPA_MCC> | MAIN MCC
01-503._L0 | BB1EM401 | <KPA_MCC> |  |  | 15030 | F1503 | Q100 |  | 15030 | F1503 | Q1503 | T5R/3 | NSX100H/MA100 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | <KPA_MCC> | MAIN MCC
01-504._L0 | BB1EM550 | <KPA_MCC> |  |  | 15040 | F1504 | Q100 |  | 15040 | F1504 | Q1504 | T1F/2 | NSX160H/MA150 | LV430834 | 3P CIRCUIT BREAKER, NSX160H, 150A, MA150 70kA | SCHNEIDER NSX160H/MA150 | COMPACT NSX | LV430500 | 3P TRIP UNIT, MA150, NSX160, 160A | MA150 | 150A | <KPA_MCC> | MAIN MCC
01-505._L0 | BB1EM603 | <KPA_MCC> |  |  | 15050 | F1505 | Q100 |  | 15050 | F1505 | Q1505 | T1F/3 | NSX100H/MA100 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | <KPA_MCC> | MAIN MCC
01-506._L0 | BB1EM604 | <KPA_MCC> |  |  | 15060 | F1506 | Q100 |  | 15060 | F1506 | Q1506 | T1F/4 | NSX100H/MA100 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | <KPA_MCC> | MAIN MCC
01-507._L0 | BB1EM605 | <KPA_MCC> |  |  | 15070 | F1507 | Q100 |  | 15070 | F1507 | Q1507 | T1F/5 | NSX100H/MA100 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | <KPA_MCC> | MAIN MCC
01-508._L0 | BB1EM658 | <KPA_MCC> |  |  | 15080 | F1508 | Q100 |  | 15080 | F1508 | Q1508 | T4F/5 | NSX100H/MA50 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | <KPA_MCC> | MAIN MCC
01-509._L0 | BB1EM659 | <KPA_MCC> |  |  | 15090 | F1509 | Q104 |  | 15090 | F1509 | Q1509 | T1R | GV2L14 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | <KPA_MCC> | MAIN MCC
01-510._L0 | BB1EM676 | <KPA_MCC> |  |  | 15100 | F1510 | Q104 |  | 15100 | F1510 | Q1510 | T1R | GV2L22 | GV2L22 | 3P CIRCUIT BREAKER, TESYS GV2L, 25A | SCHNEIDER GV2L22 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 22A | <KPA_MCC> | MAIN MCC
01-511._L0 | BB1EM672 | <KPA_MCC> |  |  | 15110 | F1511 | Q100 |  | 15110 | F1511 | Q1511 | T4F/6 | NSX100H/MA50 | LV429761 | 3P CIRCUIT BREAKER, NSX100H, 50A, MA50 70kA | SCHNEIDER NSX100H/MA50 | COMPACT NSX | LV429121 | 3P TRIP UNIT, MA50, NSX100, 50A | MA50 | 50A | <KPA_MCC> | MAIN MCC
01-512._L0 | BB1EM662 | <KPA_MCC> |  |  | 15120 | F1512 | Q100 |  | 15120 | F1512 | Q1512 | T4F/7 | NSX100H/MA100 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | <KPA_MCC> | MAIN MCC
01-513._L0 | BB1EM650 | <KPA_MCC> |  |  | 15130 | F1513 | Q104 |  | 15130 | F1513 | Q1513 | T1R | GV2L10 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | <KPA_MCC> | MAIN MCC
01-514._L0 | BB1EM663 | <KPA_MCC> |  |  | 15140 | F1514 | Q105 |  | 15140 | F1514 | Q1514 | T4R | GV2L14 | GV2L14 | 3P CIRCUIT BREAKER, TESYS GV2L, 10A | SCHNEIDER GV2L14 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 14A | <KPA_MCC> | MAIN MCC
01-515._L0 | BB1EM664 | <KPA_MCC> |  |  | 15150 | F1515 | Q105 |  | 15150 | F1515 | Q1515 | T4R | GV2L16 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | <KPA_MCC> | MAIN MCC
01-516._L0 | BB1EM665 | <KPA_MCC> |  |  | 15160 | F1516 | Q105 |  | 15160 | F1516 | Q1516 | T4R | GV2L16 | GV2L16 | 3P CIRCUIT BREAKER, TESYS GV2L, 14A | SCHNEIDER GV2L16 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 16A | <KPA_MCC> | MAIN MCC
01-517._L0 | BB1EM852 | <KPA_MCC> |  |  | 15170 | F1517 | Q105 |  | 15170 | F1517 | Q1517 | T4R | GV2L10 | GV2L10 | 3P CIRCUIT BREAKER, TESYS GV2L, 6.3A | SCHNEIDER GV2L10 | MOTOR CIRCUIT BREAKER | _ | INTEGRATED PROTECTION |  | 10A | <KPA_MCC> | MAIN MCC
01-518._L0 | BB1EM606 | <KPA_MCC> |  |  | 15180 | F1518 | Q100 |  | 15180 | F1518 | Q1518 | T5R/4 | NSX100H/MA100 | LV429760 | 3P CIRCUIT BREAKER, NSX100H, 100A, MA100 70kA | SCHNEIDER NSX100H/MA100 | COMPACT NSX | LV429120 | 3P TRIP UNIT, MA100, NSX100, 100A | MA100 | 100A | <KPA_MCC> | MAIN MCC
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
01-._L0 | 0 | KPA_FLOORX_IO |  |  | 10 | F1 |  |  | 10 | F1 | Q1 | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 | KPA_FLOORX_IO |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | KPA_FLOORX_IO |  |  |  | /1 | 0/ISO
0 | 0 |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | 0 |  |  |  | /1 | 0/ISO
0 | 0 |  |  |  | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | [10 empty] | 0 |  |  |  | /1 | 0/ISO

## W_WIRE
Tag | _Typical | W1 | W2 | WireNameLoopA | WireNameLoopB | WireNameIO | WireNameUserA | WireNameUserB | Notes
<004> | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
BB1FS003 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS001 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS002 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS003 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS004 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS005 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS006 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS007 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS008 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS009 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS010 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS011 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS012 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS020 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS200 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS201 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS203 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS204 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS205 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS206 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS207 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS208 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS209 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS210 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS211 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS212 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS213 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS214 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS215 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS216 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS217 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS218 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS219 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS220 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS221 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS222 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS223 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS224 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS225 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS226 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS227 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS228 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS230 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS231 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS232 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS233 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS600 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS601 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS602 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS603 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS604 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS605 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS606 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS607 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS608 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS609 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS610 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS611 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS612 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS613 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS614 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS615 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS616 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS617 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS618 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS619 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS620 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS621 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS622 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS623 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS650 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS651 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS652 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS653 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS654 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS655 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS656 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS659 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS660 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS661 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS662 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS663 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS800 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS801 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS802 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS803 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS850 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS851 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS852 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS853 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS854 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS855 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS856 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS857 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1GS858 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS600 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS608 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS650 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS651 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS652 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS653 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS654 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS655 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS656 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS657 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS658 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS659 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS660 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS661 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS700 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS701 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS850 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1LS851 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS600 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS601 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS602 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS603 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS604 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1PS605 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST649 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST650 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST651 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST652 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST653 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST654 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST655 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST656 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST657 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST659 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST673 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST674 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST675 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST850 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST852 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST853 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1ST856 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1TS600 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
BB1TS608 | MEAS_BIN |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
DETAIL | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
BB1EM658_LOCAL_MODE | #N/A |  |  | RIO_01:03.DI:V+ |  | RIO_01:03.DI:01 | /K1
BB1EM658_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:03.DI:V+ |  | RIO_01:03.DI:02 | /K1
BB1EM658_LOCAL_RUN_REV | #N/A |  |  | RIO_01:03.DI:V+ |  | RIO_01:03.DI:03 | /K1
BB1EM658_ISOLATOR | #N/A |  |  | RIO_01:04.DI:V+ |  | RIO_01:04.DI:00 | /K1
BB1EM659_LOCAL_MODE | #N/A |  |  | RIO_01:04.DI:V+ |  | RIO_01:04.DI:01 | /K1
BB1EM659_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:04.DI:V+ |  | RIO_01:04.DI:02 | /K1
BB1EM659_LOCAL_RUN_REV | #N/A |  |  | RIO_01:04.DI:V+ |  | RIO_01:04.DI:03 | /K1
BB1EM659_ISOLATOR | #N/A |  |  | RIO_01:05.DI:V+ |  | RIO_01:05.DI:00 | /K1
BB1EM676_LOCAL_MODE | #N/A |  |  | RIO_01:05.DI:V+ |  | RIO_01:05.DI:01 | /K1
BB1EM676_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:05.DI:V+ |  | RIO_01:05.DI:02 | /K1
BB1EM676_LOCAL_RUN_REV | #N/A |  |  | RIO_01:05.DI:V+ |  | RIO_01:05.DI:03 | /K1
BB1EM676_ISOLATOR | #N/A |  |  | RIO_01:06.DI:V+ |  | RIO_01:06.DI:00 | /K1
BB1EM672_LOCAL_MODE | #N/A |  |  | RIO_01:06.DI:V+ |  | RIO_01:06.DI:01 | /K1
BB1EM672_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:06.DI:V+ |  | RIO_01:06.DI:02 | /K1
BB1EM672_LOCAL_RUN_REV | #N/A |  |  | RIO_01:06.DI:V+ |  | RIO_01:06.DI:03 | /K1
BB1EM672_ISOLATOR | #N/A |  |  | RIO_01:07.DI:V+ |  | RIO_01:07.DI:00 | /K1
BB1EM662_LOCAL_MODE | #N/A |  |  | RIO_01:07.DI:V+ |  | RIO_01:07.DI:01 | /K1
BB1EM662_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:07.DI:V+ |  | RIO_01:07.DI:02 | /K1
BB1EM662_LOCAL_RUN_REV | #N/A |  |  | RIO_01:07.DI:V+ |  | RIO_01:07.DI:03 | /K1
BB1EM662_ISOLATOR | #N/A |  |  | RIO_01:08.DI:V+ |  | RIO_01:08.DI:00 | /K1
BB1EM650_LOCAL_MODE | #N/A |  |  | RIO_01:08.DI:V+ |  | RIO_01:08.DI:01 | /K1
BB1EM650_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:08.DI:V+ |  | RIO_01:08.DI:02 | /K1
BB1EM650_LOCAL_RUN_REV | #N/A |  |  | RIO_01:08.DI:V+ |  | RIO_01:08.DI:03 | /K1
BB1EM650_ISOLATOR | #N/A |  |  | RIO_01:09.DI:V+ |  | RIO_01:09.DI:00 | /K1
BB1EM663_LOCAL_MODE | #N/A |  |  | RIO_01:09.DI:V+ |  | RIO_01:09.DI:01 | /K1
BB1EM663_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:09.DI:V+ |  | RIO_01:09.DI:02 | /K1
BB1EM663_LOCAL_RUN_REV | #N/A |  |  | RIO_01:09.DI:V+ |  | RIO_01:09.DI:03 | /K1
BB1EM663_ISOLATOR | #N/A |  |  | RIO_01:10.DI:V+ |  | RIO_01:10.DI:00 | /K1
BB1EM664_LOCAL_MODE | #N/A |  |  | RIO_01:10.DI:V+ |  | RIO_01:10.DI:01 | /K1
BB1EM664_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:10.DI:V+ |  | RIO_01:10.DI:02 | /K1
BB1EM664_LOCAL_RUN_REV | #N/A |  |  | RIO_01:10.DI:V+ |  | RIO_01:10.DI:03 | /K1
BB1EM664_ISOLATOR | #N/A |  |  | RIO_01:11.DI:V+ |  | RIO_01:11.DI:00 | /K1
BB1EM665_LOCAL_MODE | #N/A |  |  | RIO_01:11.DI:V+ |  | RIO_01:11.DI:01 | /K1
BB1EM665_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:11.DI:V+ |  | RIO_01:11.DI:02 | /K1
BB1EM665_LOCAL_RUN_REV | #N/A |  |  | RIO_01:11.DI:V+ |  | RIO_01:11.DI:03 | /K1
BB1EM665_ISOLATOR | #N/A |  |  | RIO_01:12.DI:V+ |  | RIO_01:12.DI:00 | /K1
BB1EM852_LOCAL_MODE | #N/A |  |  | RIO_01:12.DI:V+ |  | RIO_01:12.DI:01 | /K1
BB1EM852_LOCAL_RUN_FWD | #N/A |  |  | RIO_01:12.DI:V+ |  | RIO_01:12.DI:02 | /K1
BB1EM852_LOCAL_RUN_REV | #N/A |  |  | RIO_01:12.DI:V+ |  | RIO_01:12.DI:03 | /K1
BB1EM852_ISOLATOR | #N/A |  |  | RIO_01:13.DI:V+ |  | RIO_01:13.DI:00 | /K1
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A
| #N/A |  |  | #N/A | #N/A | #N/A | #N/A

## P_IO
IO Mapping |  |  |  | Description |  | Panel | Addressing | [10 empty] | Terminals | [5 empty] | Terminal Type/Names |  |  |  |  | Catalog
PLCTag | CardType | IOType | _Typical | Description2 | Description3 | Description4 | Panel | _PLC | _RackRaw | _SlotRaw | _ChannelRaw | _IsMax | Rack | Slot | Channel | LoopAddressA | LoopAddressB | AddressIO | TerminalIO | LoopTerminalA | LoopTerminalB | GndTerminal | T1 | T2 | T1Type | T2Type | LoopNameA | LoopNameB | GndName | CatalogNo | CatalogDesc2 | CatalogDesc | Notes
BB1EM603_LOCAL_MODE | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 0 | 0 | 01 | 01 | 00 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM603_LOCAL_RUN | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 1 | 0 | 01 | 01 | 01 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM603_ISOLATOR | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 2 | 0 | 01 | 01 | 02 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM604_LOCAL_MODE | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  | KPA_FLOORX_IO | RIO_ | 1 | 1 | 3 | TRUE | 01 | 01 | 03 | RIO_01:01.DI:V+ |  | RIO_01:01.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM604_LOCAL_RUN | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 0 | 0 | 01 | 02 | 00 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM604_ISOLATOR | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 1 | 0 | 01 | 02 | 01 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM605_LOCAL_MODE | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 2 | 0 | 01 | 02 | 02 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM605_LOCAL_RUN | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  | KPA_FLOORX_IO | RIO_ | 1 | 2 | 3 | TRUE | 01 | 02 | 03 | RIO_01:02.DI:V+ |  | RIO_01:02.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM605_ISOLATOR | DI | DI | FRQ_DIRH | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 0 | 0 | 01 | 03 | 00 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM658_LOCAL_MODE | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 1 | 0 | 01 | 03 | 01 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM658_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 2 | 0 | 01 | 03 | 02 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM658_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 3 | 3 | TRUE | 01 | 03 | 03 | RIO_01:03.DI:V+ |  | RIO_01:03.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM658_ISOLATOR | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 1 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 0 | 0 | 01 | 04 | 00 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM659_LOCAL_MODE | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 1 | 0 | 01 | 04 | 01 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM659_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 2 | 0 | 01 | 04 | 02 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM659_LOCAL_RUN_REV | DI | DI | FRQ_REVH | BELT CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 4 | 3 | TRUE | 01 | 04 | 03 | RIO_01:04.DI:V+ |  | RIO_01:04.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM659_ISOLATOR | DI | DI | FRQ_REVH | BELT CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 0 | 0 | 01 | 05 | 00 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM676_LOCAL_MODE | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 1 | 0 | 01 | 05 | 01 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM676_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 2 | 0 | 01 | 05 | 02 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM676_LOCAL_RUN_REV | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 5 | 3 | TRUE | 01 | 05 | 03 | RIO_01:05.DI:V+ |  | RIO_01:05.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM676_ISOLATOR | DI | DI | FRQ_REVH | DISC SCREEN DRIVE 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 0 | 0 | 01 | 06 | 00 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM672_LOCAL_MODE | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 1 | 0 | 01 | 06 | 01 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM672_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 2 | 0 | 01 | 06 | 02 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM672_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 6 | 3 | TRUE | 01 | 06 | 03 | RIO_01:06.DI:V+ |  | RIO_01:06.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM672_ISOLATOR | DI | DI | FRQ_REVH | SCRAPER CONVEYOR 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 0 | 0 | 01 | 07 | 00 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM662_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 1 | 0 | 01 | 07 | 01 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM662_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 2 | 0 | 01 | 07 | 02 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM662_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 7 | 3 | TRUE | 01 | 07 | 03 | RIO_01:07.DI:V+ |  | RIO_01:07.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM662_ISOLATOR | DI | DI | FRQ_REVH | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 0 | 0 | 01 | 08 | 00 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM650_LOCAL_MODE | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 1 | 0 | 01 | 08 | 01 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM650_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 2 | 0 | 01 | 08 | 02 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM650_LOCAL_RUN_REV | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 8 | 3 | TRUE | 01 | 08 | 03 | RIO_01:08.DI:V+ |  | RIO_01:08.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM650_ISOLATOR | DI | DI | FRQ_REVH | SLEWING MOTOR FOR SCREW | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 0 | 0 | 01 | 09 | 00 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM663_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 1 | 0 | 01 | 09 | 01 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM663_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 2 | 0 | 01 | 09 | 02 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM663_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 9 | 3 | TRUE | 01 | 09 | 03 | RIO_01:09.DI:V+ |  | RIO_01:09.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM663_ISOLATOR | DI | DI | FRQ_REVH | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 0 | 0 | 01 | 10 | 00 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM664_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 1 | 0 | 01 | 10 | 01 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM664_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 2 | 0 | 01 | 10 | 02 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM664_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 10 | 3 | TRUE | 01 | 10 | 03 | RIO_01:10.DI:V+ |  | RIO_01:10.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM664_ISOLATOR | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 1 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 11 | 0 | 0 | 01 | 11 | 00 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM665_LOCAL_MODE | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 11 | 1 | 0 | 01 | 11 | 01 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM665_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 11 | 2 | 0 | 01 | 11 | 02 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM665_LOCAL_RUN_REV | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 11 | 3 | TRUE | 01 | 11 | 03 | RIO_01:11.DI:V+ |  | RIO_01:11.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM665_ISOLATOR | DI | DI | FRQ_REVH | FUEL FEEDING SCREW 2 | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 12 | 0 | 0 | 01 | 12 | 00 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM852_LOCAL_MODE | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | KPA_FLOORX_IO | RIO_ | 1 | 12 | 1 | 0 | 01 | 12 | 01 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM852_LOCAL_RUN_FWD | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | KPA_FLOORX_IO | RIO_ | 1 | 12 | 2 | 0 | 01 | 12 | 02 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
BB1EM852_LOCAL_RUN_REV | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | KPA_FLOORX_IO | RIO_ | 1 | 12 | 3 | TRUE | 01 | 12 | 03 | RIO_01:12.DI:V+ |  | RIO_01:12.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
BB1EM852_ISOLATOR | DI | DI | FRQ_REVH | BOTTOM ASH CONVEYOR | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 0 | 0 | 01 | 13 | 00 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
BB1EM606_ISOLATOR | DI | DI | FRQ_DIR | DUST EXTRACTION FAN | ISOLATOR |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 1 | 0 | 01 | 13 | 01 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
BB1EM401_ISOLATOR | DI | DI | FRQ_DIR | EXHAUST FAN 1 ISOLATOR |  |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 2 | 0 | 01 | 13 | 02 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 13 | 3 | TRUE | 01 | 13 | 03 | RIO_01:13.DI:V+ |  | RIO_01:13.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 0 | 0 | 01 | 14 | 00 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 1 | 0 | 01 | 14 | 01 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 2 | 0 | 01 | 14 | 02 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 14 | 3 | TRUE | 01 | 14 | 03 | RIO_01:14.DI:V+ |  | RIO_01:14.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 0 | 0 | 01 | 15 | 00 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 1 | 0 | 01 | 15 | 01 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 2 | 0 | 01 | 15 | 02 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 15 | 3 | TRUE | 01 | 15 | 03 | RIO_01:15.DI:V+ |  | RIO_01:15.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 0 | 0 | 01 | 16 | 00 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 1 | 0 | 01 | 16 | 01 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 2 | 0 | 01 | 16 | 02 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 16 | 3 | TRUE | 01 | 16 | 03 | RIO_01:16.DI:V+ |  | RIO_01:16.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 0 | 0 | 01 | 17 | 00 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 1 | 0 | 01 | 17 | 01 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 2 | 0 | 01 | 17 | 02 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 17 | 3 | TRUE | 01 | 17 | 03 | RIO_01:17.DI:V+ |  | RIO_01:17.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 0 | 0 | 01 | 18 | 00 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 1 | 0 | 01 | 18 | 01 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 2 | 0 | 01 | 18 | 02 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 18 | 3 | TRUE | 01 | 18 | 03 | RIO_01:18.DI:V+ |  | RIO_01:18.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 0 | 0 | 01 | 19 | 00 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 1 | 0 | 01 | 19 | 01 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 2 | 0 | 01 | 19 | 02 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 19 | 3 | TRUE | 01 | 19 | 03 | RIO_01:19.DI:V+ |  | RIO_01:19.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 0 | 0 | 01 | 20 | 00 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 1 | 0 | 01 | 20 | 01 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 2 | 0 | 01 | 20 | 02 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 20 | 3 | TRUE | 01 | 20 | 03 | RIO_01:20.DI:V+ |  | RIO_01:20.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 0 | 0 | 01 | 21 | 00 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 1 | 0 | 01 | 21 | 01 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 2 | 0 | 01 | 21 | 02 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 21 | 3 | TRUE | 01 | 21 | 03 | RIO_01:21.DI:V+ |  | RIO_01:21.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 0 | 0 | 01 | 22 | 00 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 1 | 0 | 01 | 22 | 01 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 2 | 0 | 01 | 22 | 02 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 22 | 3 | TRUE | 01 | 22 | 03 | RIO_01:22.DI:V+ |  | RIO_01:22.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 0 | 0 | 01 | 23 | 00 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 1 | 0 | 01 | 23 | 01 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 2 | 0 | 01 | 23 | 02 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 23 | 3 | TRUE | 01 | 23 | 03 | RIO_01:23.DI:V+ |  | RIO_01:23.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 0 | 0 | 01 | 24 | 00 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 1 | 0 | 01 | 24 | 01 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 2 | 0 | 01 | 24 | 02 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 24 | 3 | TRUE | 01 | 24 | 03 | RIO_01:24.DI:V+ |  | RIO_01:24.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 0 | 0 | 01 | 25 | 00 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 1 | 0 | 01 | 25 | 01 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 2 | 0 | 01 | 25 | 02 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 25 | 3 | TRUE | 01 | 25 | 03 | RIO_01:25.DI:V+ |  | RIO_01:25.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 0 | 0 | 01 | 26 | 00 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 1 | 0 | 01 | 26 | 01 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 2 | 0 | 01 | 26 | 02 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 26 | 3 | TRUE | 01 | 26 | 03 | RIO_01:26.DI:V+ |  | RIO_01:26.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 0 | 0 | 01 | 27 | 00 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 1 | 0 | 01 | 27 | 01 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 2 | 0 | 01 | 27 | 02 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 27 | 3 | TRUE | 01 | 27 | 03 | RIO_01:27.DI:V+ |  | RIO_01:27.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 0 | 0 | 01 | 28 | 00 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 1 | 0 | 01 | 28 | 01 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 2 | 0 | 01 | 28 | 02 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 28 | 3 | TRUE | 01 | 28 | 03 | RIO_01:28.DI:V+ |  | RIO_01:28.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 0 | 0 | 01 | 29 | 00 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 1 | 0 | 01 | 29 | 01 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 2 | 0 | 01 | 29 | 02 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 29 | 3 | TRUE | 01 | 29 | 03 | RIO_01:29.DI:V+ |  | RIO_01:29.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 0 | 0 | 01 | 30 | 00 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 1 | 0 | 01 | 30 | 01 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 2 | 0 | 01 | 30 | 02 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 30 | 3 | TRUE | 01 | 30 | 03 | RIO_01:30.DI:V+ |  | RIO_01:30.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 0 | 0 | 01 | 31 | 00 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 1 | 0 | 01 | 31 | 01 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 2 | 0 | 01 | 31 | 02 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 31 | 3 | TRUE | 01 | 31 | 03 | RIO_01:31.DI:V+ |  | RIO_01:31.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 0 | 0 | 01 | 32 | 00 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 1 | 0 | 01 | 32 | 01 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 2 | 0 | 01 | 32 | 02 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 32 | 3 | TRUE | 01 | 32 | 03 | RIO_01:32.DI:V+ |  | RIO_01:32.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 0 | 0 | 01 | 33 | 00 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 1 | 0 | 01 | 33 | 01 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 2 | 0 | 01 | 33 | 02 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 33 | 3 | TRUE | 01 | 33 | 03 | RIO_01:33.DI:V+ |  | RIO_01:33.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 0 | 0 | 01 | 34 | 00 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 1 | 0 | 01 | 34 | 01 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 2 | 0 | 01 | 34 | 02 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 34 | 3 | TRUE | 01 | 34 | 03 | RIO_01:34.DI:V+ |  | RIO_01:34.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 0 | 0 | 01 | 35 | 00 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 1 | 0 | 01 | 35 | 01 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 2 | 0 | 01 | 35 | 02 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 35 | 3 | TRUE | 01 | 35 | 03 | RIO_01:35.DI:V+ |  | RIO_01:35.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 0 | 0 | 01 | 36 | 00 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 1 | 0 | 01 | 36 | 01 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 2 | 0 | 01 | 36 | 02 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 36 | 3 | TRUE | 01 | 36 | 03 | RIO_01:36.DI:V+ |  | RIO_01:36.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 0 | 0 | 01 | 37 | 00 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 1 | 0 | 01 | 37 | 01 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 2 | 0 | 01 | 37 | 02 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 37 | 3 | TRUE | 01 | 37 | 03 | RIO_01:37.DI:V+ |  | RIO_01:37.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 0 | 0 | 01 | 38 | 00 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 1 | 0 | 01 | 38 | 01 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 2 | 0 | 01 | 38 | 02 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 38 | 3 | TRUE | 01 | 38 | 03 | RIO_01:38.DI:V+ |  | RIO_01:38.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 0 | 0 | 01 | 39 | 00 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 1 | 0 | 01 | 39 | 01 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 2 | 0 | 01 | 39 | 02 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 39 | 3 | TRUE | 01 | 39 | 03 | RIO_01:39.DI:V+ |  | RIO_01:39.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 0 | 0 | 01 | 40 | 00 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 1 | 0 | 01 | 40 | 01 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 2 | 0 | 01 | 40 | 02 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 40 | 3 | TRUE | 01 | 40 | 03 | RIO_01:40.DI:V+ |  | RIO_01:40.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 0 | 0 | 01 | 41 | 00 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 1 | 0 | 01 | 41 | 01 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 2 | 0 | 01 | 41 | 02 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 41 | 3 | TRUE | 01 | 41 | 03 | RIO_01:41.DI:V+ |  | RIO_01:41.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 0 | 0 | 01 | 42 | 00 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 1 | 0 | 01 | 42 | 01 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 2 | 0 | 01 | 42 | 02 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 42 | 3 | TRUE | 01 | 42 | 03 | RIO_01:42.DI:V+ |  | RIO_01:42.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 0 | 0 | 01 | 43 | 00 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 1 | 0 | 01 | 43 | 01 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 2 | 0 | 01 | 43 | 02 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 43 | 3 | TRUE | 01 | 43 | 03 | RIO_01:43.DI:V+ |  | RIO_01:43.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 0 | 0 | 01 | 44 | 00 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 1 | 0 | 01 | 44 | 01 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 2 | 0 | 01 | 44 | 02 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 44 | 3 | TRUE | 01 | 44 | 03 | RIO_01:44.DI:V+ |  | RIO_01:44.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 0 | 0 | 01 | 45 | 00 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 1 | 0 | 01 | 45 | 01 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 2 | 0 | 01 | 45 | 02 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 45 | 3 | TRUE | 01 | 45 | 03 | RIO_01:45.DI:V+ |  | RIO_01:45.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 0 | 0 | 01 | 46 | 00 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 1 | 0 | 01 | 46 | 01 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 2 | 0 | 01 | 46 | 02 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 46 | 3 | TRUE | 01 | 46 | 03 | RIO_01:46.DI:V+ |  | RIO_01:46.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 0 | 0 | 01 | 47 | 00 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 1 | 0 | 01 | 47 | 01 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 2 | 0 | 01 | 47 | 02 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 47 | 3 | TRUE | 01 | 47 | 03 | RIO_01:47.DI:V+ |  | RIO_01:47.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 0 | 0 | 01 | 48 | 00 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 1 | 0 | 01 | 48 | 01 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 2 | 0 | 01 | 48 | 02 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 48 | 3 | TRUE | 01 | 48 | 03 | RIO_01:48.DI:V+ |  | RIO_01:48.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 0 | 0 | 01 | 49 | 00 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:00 | 0 | 1 |  |  | V+ | 00 | 24VDC | DI | V+ |  |  | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 1 | 0 | 01 | 49 | 01 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:01 | 1 | 3 |  |  | V+ | 01 | 24VDC | DI | V+ |  |  | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 2 | 0 | 01 | 49 | 02 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:02 | 2 | 5 |  |  | V+ | 02 | 24VDC | DI | V+ |  |  | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D
| DI |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 49 | 3 | TRUE | 01 | 49 | 03 | RIO_01:49.DI:V+ |  | RIO_01:49.DI:03 | 3 | 7 |  |  | V+ | 03 | 24VDC | DI | V+ |  |  | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D
|  |  |  | [SPARE] |  |  | KPA_FLOORX_IO | RIO_ | 1 | 50 | 0 | #N/A | 01 | 50 | 00 | #N/A | #N/A | RIO_01:50.:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO | RIO_ | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  |  |  | #N/A |  |  | KPA_FLOORX_IO |  | 1 | #N/A | #N/A | #N/A | 01 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## D_DEVICES
IO DEVICE LIST |  |  |  | Description |  |  |  |  | Types |  |  |  |  | Device List
DeviceTag | _Suffix | PLCTag | PLCAddress | _InitialDescription | Desc1 | Desc2 | Desc3 | LongDescription | DeviceCode | DeviceType | IOType | Typical | Notes | DeviceTag | Typical | INITIAL_DESC | DESC1 | DESC2 | DESC3 | LDESC | DeviceCode | Type | D1Tag | D1CatN | D1CatD | D2Tag | D2CatN | D2CatD | D3Tag | D3Desc1 | D3Desc2 | D3CatN | D3CatD | VSDkW | MotorKW
BB1IL001 |  | BB1IL001 | <IO NOT ASSIGNED> | Alarm horn and light CO alarm | ALARM HORN AND LIGHT | CO ALARM |  | ALARM HORN AND LIGHT CO ALARM | IL | ALARM | DO | ALM_HORN |  | BB1IL001 | ALM_HORN | Alarm horn and light CO alarm | ALARM HORN AND LIGHT | CO ALARM |  | ALARM HORN AND LIGHT CO ALARM | IL | ALARM | BB1IL001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IJ002 |  | BB1IJ002 | <IO NOT ASSIGNED> | Scraper Conveyor 1 Alarm horn and lamp | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  | SCRAPER CONVEYOR 1 ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN |  | BB1IJ002 | ALM_HORN | Scraper Conveyor 1 Alarm horn and lamp | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  | SCRAPER CONVEYOR 1 ALARM HORN AND LAMP | IJ | ALARM | BB1IJ002 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IJ001 |  | BB1IJ001 | <IO NOT ASSIGNED> | Scraper Conveyor 2 Alarm horn and lamp | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  | SCRAPER CONVEYOR 2 ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN |  | BB1IJ001 | ALM_HORN | Scraper Conveyor 2 Alarm horn and lamp | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  | SCRAPER CONVEYOR 2 ALARM HORN AND LAMP | IJ | ALARM | BB1IJ001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IJ004 |  | BB1IJ004 | <IO NOT ASSIGNED> | Bottom ash conveyor Alarm horn and lamp | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  | BOTTOM ASH CONVEYOR ALARM HORN AND LAMP | IJ | ALARM | DO | ALM_HORN |  | BB1IJ004 | ALM_HORN | Bottom ash conveyor Alarm horn and lamp | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  | BOTTOM ASH CONVEYOR ALARM HORN AND LAMP | IJ | ALARM | BB1IJ004 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM405 |  | BB1EM405 | <IO NOT ASSIGNED> | Air intake grill 1 OPEN | AIR INTAKE GRILL 1 | OPEN |  | AIR INTAKE GRILL 1 OPEN | EM | MOTOR | DO | BELIMO_VLV |  | BB1EM405 | BELIMO_VLV | Air intake grill 1 OPEN | AIR INTAKE GRILL 1 | OPEN |  | AIR INTAKE GRILL 1 OPEN | EM | MOTOR | BB1EM405 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS401 |  | BB1GS401 | <IO NOT ASSIGNED> | Air intake grill 1 OPENED LIMIT | AIR INTAKE GRILL 1 | OPENED LIMIT |  | AIR INTAKE GRILL 1 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV |  | BB1GS401 | BELIMO_VLV | Air intake grill 1 OPENED LIMIT | AIR INTAKE GRILL 1 | OPENED LIMIT |  | AIR INTAKE GRILL 1 OPENED LIMIT | GS | GATE SWITCH | BB1GS401 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM406 |  | BB1EM406 | <IO NOT ASSIGNED> | Air intake grill 2 OPEN | AIR INTAKE GRILL 2 | OPEN |  | AIR INTAKE GRILL 2 OPEN | EM | MOTOR | DO | BELIMO_VLV |  | BB1EM406 | BELIMO_VLV | Air intake grill 2 OPEN | AIR INTAKE GRILL 2 | OPEN |  | AIR INTAKE GRILL 2 OPEN | EM | MOTOR | BB1EM406 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS412 |  | BB1GS412 | <IO NOT ASSIGNED> | Air intake grill 2 OPENED LIMIT | AIR INTAKE GRILL 2 | OPENED LIMIT |  | AIR INTAKE GRILL 2 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV |  | BB1GS412 | BELIMO_VLV | Air intake grill 2 OPENED LIMIT | AIR INTAKE GRILL 2 | OPENED LIMIT |  | AIR INTAKE GRILL 2 OPENED LIMIT | GS | GATE SWITCH | BB1GS412 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM407 |  | BB1EM407 | <IO NOT ASSIGNED> | Air intake grill 3 OPEN | AIR INTAKE GRILL 3 | OPEN |  | AIR INTAKE GRILL 3 OPEN | EM | MOTOR | DO | BELIMO_VLV |  | BB1EM407 | BELIMO_VLV | Air intake grill 3 OPEN | AIR INTAKE GRILL 3 | OPEN |  | AIR INTAKE GRILL 3 OPEN | EM | MOTOR | BB1EM407 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS413 |  | BB1GS413 | <IO NOT ASSIGNED> | Air intake grill 3 OPENED LIMIT | AIR INTAKE GRILL 3 | OPENED LIMIT |  | AIR INTAKE GRILL 3 OPENED LIMIT | GS | GATE SWITCH | DI | BELIMO_VLV |  | BB1GS413 | BELIMO_VLV | Air intake grill 3 OPENED LIMIT | AIR INTAKE GRILL 3 | OPENED LIMIT |  | AIR INTAKE GRILL 3 OPENED LIMIT | GS | GATE SWITCH | BB1GS413 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV410 |  | BB1SV410 | <IO NOT ASSIGNED> | Feed water tank overflow valve | FEED WATER TANK | OVERFLOW VALVE |  | FEED WATER TANK OVERFLOW VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV410 | BIN_VLV | Feed water tank overflow valve | FEED WATER TANK | OVERFLOW VALVE |  | FEED WATER TANK OVERFLOW VALVE | SV | SOLENOID VALVE | BB1SV410 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IV004 |  | BB1IV004 | <IO NOT ASSIGNED> | Boiler bottom blow down on-off valve | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  | BOILER BOTTOM BLOW DOWN ON-OFF VALVE | IV | ISOLATING VALVE | DO | BIN_VLV |  | BB1IV004 | BIN_VLV | Boiler bottom blow down on-off valve | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  | BOILER BOTTOM BLOW DOWN ON-OFF VALVE | IV | ISOLATING VALVE | BB1IV004 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV001 |  | BB1SV001 | <IO NOT ASSIGNED> | Blow down tank cooling on/off valve | BLOW DOWN TANK COOLING | ON/OFF VALVE |  | BLOW DOWN TANK COOLING ON/OFF VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV001 | BIN_VLV | Blow down tank cooling on/off valve | BLOW DOWN TANK COOLING | ON/OFF VALVE |  | BLOW DOWN TANK COOLING ON/OFF VALVE | SV | SOLENOID VALVE | BB1SV001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV400 |  | BB1SV400 | <IO NOT ASSIGNED> | Sealing air to rotary feeder solenoid valve | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV400 | BIN_VLV | Sealing air to rotary feeder solenoid valve | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | BB1SV400 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV406 |  | BB1SV406 | <IO NOT ASSIGNED> | Sealing air to rotary feeder solenoid valve | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV406 | BIN_VLV | Sealing air to rotary feeder solenoid valve | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE | SV | SOLENOID VALVE | BB1SV406 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV950 |  | BB1SV950 | <IO NOT ASSIGNED> | Fuel silo fire water control valve | FUEL SILO FIRE WATER | CONTROL VALVE |  | FUEL SILO FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV950 | BIN_VLV | Fuel silo fire water control valve | FUEL SILO FIRE WATER | CONTROL VALVE |  | FUEL SILO FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | BB1SV950 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV951 |  | BB1SV951 | <IO NOT ASSIGNED> | Fuel pocket fire water control valve | FUEL POCKET FIRE WATER | CONTROL VALVE |  | FUEL POCKET FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV951 | BIN_VLV | Fuel pocket fire water control valve | FUEL POCKET FIRE WATER | CONTROL VALVE |  | FUEL POCKET FIRE WATER CONTROL VALVE | SV | SOLENOID VALVE | BB1SV951 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV405 |  | BB1CV405 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve | BOTTOM ASH VALVE | SOLENOID VALVE |  | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV |  | BB1CV405 | BIN_VLV | Bottom ash valve solenoid valve | BOTTOM ASH VALVE | SOLENOID VALVE |  | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | BB1CV405 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV406 |  | BB1CV406 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve | BOTTOM ASH VALVE | SOLENOID VALVE |  | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV |  | BB1CV406 | BIN_VLV | Bottom ash valve solenoid valve | BOTTOM ASH VALVE | SOLENOID VALVE |  | BOTTOM ASH VALVE SOLENOID VALVE | CV | CONTROL VALVE | BB1CV406 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV412 |  | BB1CV412 | <IO NOT ASSIGNED> | Bottom ash sieve bypass solenoid valve | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  | BOTTOM ASH SIEVE BYPASS SOLENOID VALVE | CV | CONTROL VALVE | DO | BIN_VLV |  | BB1CV412 | BIN_VLV | Bottom ash sieve bypass solenoid valve | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  | BOTTOM ASH SIEVE BYPASS SOLENOID VALVE | CV | CONTROL VALVE | BB1CV412 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV414 |  | BB1CV414 | <IO NOT ASSIGNED> | Work air to pneumatic transmitter pneumatic valve | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE | WORK AIR TO PNEUMATIC TRANSMITTER PNEUMATIC VAL VE | CV | CONTROL VALVE | DO | BIN_VLV |  | BB1CV414 | BIN_VLV | Work air to pneumatic transmitter pneumatic valve | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE | WORK AIR TO PNEUMATIC TRANSMITTER PNEUMATIC VAL VE | CV | CONTROL VALVE | BB1CV414 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV405 |  | BB1SV405 | <IO NOT ASSIGNED> | Sand filling valve solenoid valve | SAND FILLING VALVE | SOLENOID VALVE |  | SAND FILLING VALVE SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV405 | BIN_VLV | Sand filling valve solenoid valve | SAND FILLING VALVE | SOLENOID VALVE |  | SAND FILLING VALVE SOLENOID VALVE | SV | SOLENOID VALVE | BB1SV405 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV401 |  | BB1SV401 | <IO NOT ASSIGNED> | Bottom ash purging air solenoid valve | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV401 | BIN_VLV | Bottom ash purging air solenoid valve | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | BB1SV401 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1SV402 |  | BB1SV402 | <IO NOT ASSIGNED> | Bottom ash purging air solenoid valve | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | DO | BIN_VLV |  | BB1SV402 | BIN_VLV | Bottom ash purging air solenoid valve | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  | BOTTOM ASH PURGING AIR SOLENOID VALVE | SV | SOLENOID VALVE | BB1SV402 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV413 |  | BB1CV413 | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER | CV | CONTROL VALVE | DO | BIN_VLV_2DO |  | BB1CV413 | BIN_VLV_2DO | Control valve of pneumatic transmitter damper | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER | CV | CONTROL VALVE | BB1CV413 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV413 | _OPEN | BB1CV413_OPEN | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper OPEN | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER OPEN | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER OPEN | CV | CONTROL VALVE | DO | BIN_VLV_2DO |  | BB1BU500 | BURNER | Burner signals | BURNER SIGNALS |  |  | BURNER SIGNALS | BU | BURNER | BB1BU500 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV413 | _CLOSE | BB1CV413_CLOSE | <IO NOT ASSIGNED> | Control valve of pneumatic transmitter damper CLOSE | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER CLOSE | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER CLOSE | CV | CONTROL VALVE | DO | BIN_VLV_2DO |  | BB1PU800 | CHEMICAL_PUMP | Chemical dosing pump 1 | CHEMICAL DOSING PUMP 1 |  |  | CHEMICAL DOSING PUMP 1 | PU | PUMP | BB1PU800 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1BU500 | _DO_IF1 | BB1BU500_DO_IF1 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 1 | BURNER DIGITAL OUTPUT | INTERFACE 1 |  | BURNER DIGITAL OUTPUT INTERFACE 1 | BU | BURNER | DO | BURNER |  | BB1PU801 | CHEMICAL_PUMP | Chemical dosing pump 2 | CHEMICAL DOSING PUMP 2 |  |  | CHEMICAL DOSING PUMP 2 | PU | PUMP | BB1PU801 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1BU500 | _DO_IF2 | BB1BU500_DO_IF2 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 2 | BURNER DIGITAL OUTPUT | INTERFACE 2 |  | BURNER DIGITAL OUTPUT INTERFACE 2 | BU | BURNER | DO | BURNER |  | BB1EM402 | COMPR | Compressor 1 | COMPRESSOR 1 |  |  | COMPRESSOR 1 | EM | MOTOR | BB1EM402 | [7 empty] | 30kW, 400VAC | MOTOR 30kW | MOTOR 30kW, 3 PHASE | 30 | 30
BB1BU500 | _DO_IF3 | BB1BU500_DO_IF3 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 3 | BURNER DIGITAL OUTPUT | INTERFACE 3 |  | BURNER DIGITAL OUTPUT INTERFACE 3 | BU | BURNER | DO | BURNER |  | BB1EM403 | COMPR | Compressor 2 | COMPRESSOR 2 |  |  | COMPRESSOR 2 | EM | MOTOR | BB1EM403 | [7 empty] | 30kW, 400VAC | MOTOR 30kW | MOTOR 30kW, 3 PHASE | 30 | 30
BB1BU500 | _DO_IF4 | BB1BU500_DO_IF4 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 4 | BURNER DIGITAL OUTPUT | INTERFACE 4 |  | BURNER DIGITAL OUTPUT INTERFACE 4 | BU | BURNER | DO | BURNER |  | BB1PT200 | MEAS_ANA | Feed water tank pressure | FEED WATER TANK PRESSURE |  |  | FEED WATER TANK PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT200 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _DO_IF5 | BB1BU500_DO_IF5 | <IO NOT ASSIGNED> | BURNER DIGITAL OUTPUT INTERFACE 5 | BURNER DIGITAL OUTPUT | INTERFACE 5 |  | BURNER DIGITAL OUTPUT INTERFACE 5 | BU | BURNER | DO | BURNER |  | BB1LT001 | MEAS_ANA | Feed water tank level 1 | FEED WATER TANK LEVEL 1 |  |  | FEED WATER TANK LEVEL 1 | LT | LEVEL TRANSMITTER | BB1LT001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _DI_IF1 | BB1BU500_DI_IF1 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 1 | BURNER DIGITAL INPUT | INTERFACE 1 |  | BURNER DIGITAL INPUT INTERFACE 1 | BU | BURNER | DI | BURNER |  | BB1LT002 | MEAS_ANA | Feed water tank level 2 | FEED WATER TANK LEVEL 2 |  |  | FEED WATER TANK LEVEL 2 | LT | LEVEL TRANSMITTER | BB1LT002 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _DI_IF2 | BB1BU500_DI_IF2 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 2 | BURNER DIGITAL INPUT | INTERFACE 2 |  | BURNER DIGITAL INPUT INTERFACE 2 | BU | BURNER | DI | BURNER |  | BB1PT005 | MEAS_ANA | Feed water pressure after valve | FEED WATER PRESSURE | AFTER VALVE |  | FEED WATER PRESSURE AFTER VALVE | PT | PRESSURE TRANSMITTER | BB1PT005 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _DI_IF3 | BB1BU500_DI_IF3 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 3 | BURNER DIGITAL INPUT | INTERFACE 3 |  | BURNER DIGITAL INPUT INTERFACE 3 | BU | BURNER | DI | BURNER |  | BB1FT001 | MEAS_ANA | Feed water flow and control | FEED WATER FLOW | AND CONTROL |  | FEED WATER FLOW AND CONTROL | FT | FLOW TRANSMITTER | BB1FT001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _DI_IF4 | BB1BU500_DI_IF4 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 4 | BURNER DIGITAL INPUT | INTERFACE 4 |  | BURNER DIGITAL INPUT INTERFACE 4 | BU | BURNER | DI | BURNER |  | BB1TT001 | MEAS_ANA | Feed water temperature | FEED WATER TEMPERATURE |  |  | FEED WATER TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _DI_IF5 | BB1BU500_DI_IF5 | <IO NOT ASSIGNED> | BURNER DIGITAL INPUT INTERFACE 5 | BURNER DIGITAL INPUT | INTERFACE 5 |  | BURNER DIGITAL INPUT INTERFACE 5 | BU | BURNER | DI | BURNER |  | BB1TT002 | MEAS_ANA | Feed water pump 2 bearing temperature | FEED WATER PUMP 2 | BEARING TEMPERATURE |  | FEED WATER PUMP 2 BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT002 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _AO_IF1 | BB1BU500_AO_IF1 | <IO NOT ASSIGNED> | BURNER ANALOGUE OUTPUT INTERFACE 1 | BURNER ANALOGUE OUTPUT | INTERFACE 1 |  | BURNER ANALOGUE OUTPUT INTERFACE 1 | BU | BURNER | AO | BURNER |  | BB1PT004 | MEAS_ANA | Feed water pressure before valve | FEED WATER PRESSURE | BEFORE VALVE |  | FEED WATER PRESSURE BEFORE VALVE | PT | PRESSURE TRANSMITTER | BB1PT004 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _AO_IF2 | BB1BU500_AO_IF2 | <IO NOT ASSIGNED> | BURNER ANALOGUE OUTPUT INTERFACE 2 | BURNER ANALOGUE OUTPUT | INTERFACE 2 |  | BURNER ANALOGUE OUTPUT INTERFACE 2 | BU | BURNER | AO | BURNER |  | BB1PT002 | MEAS_ANA | Feed water pump 2 pressure side pressure | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  | FEED WATER PUMP 2 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT002 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _AI_IF1 | BB1BU500_AI_IF1 | <IO NOT ASSIGNED> | BURNER ANALOGUE INPUT INTERFACE 1 | BURNER ANALOGUE INPUT | INTERFACE 1 |  | BURNER ANALOGUE INPUT INTERFACE 1 | BU | BURNER | AI | BURNER |  | BB1PT006 | MEAS_ANA | FW suction line strainer pressure diff. | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | BB1PT006 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1BU500 | _AI_IF2 | BB1BU500_AI_IF2 | <IO NOT ASSIGNED> | BURNER ANALOGUE INPUT INTERFACE 2 | BURNER ANALOGUE INPUT | INTERFACE 2 |  | BURNER ANALOGUE INPUT INTERFACE 2 | BU | BURNER | AI | BURNER |  | BB1PT007 | MEAS_ANA | FW suction line strainer pressure diff. | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | BB1PT007 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PU800 |  | BB1PU800 | <IO NOT ASSIGNED> | Chemical dosing pump 1 | CHEMICAL DOSING PUMP 1 |  |  | CHEMICAL DOSING PUMP 1 | PU | PUMP | DO | CHEMICAL_PUMP |  | BB1TT005 | MEAS_ANA | FW pump 2 motor winding temperature | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  | FW PUMP 2 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT005 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PU801 |  | BB1PU801 | <IO NOT ASSIGNED> | Chemical dosing pump 2 | CHEMICAL DOSING PUMP 2 |  |  | CHEMICAL DOSING PUMP 2 | PU | PUMP | DO | CHEMICAL_PUMP |  | BB1PT001 | MEAS_ANA | Feed water pump 1 pressure side pressure | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  | FEED WATER PUMP 1 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM402 |  | BB1EM402 | <IO NOT ASSIGNED> | Compressor 1 | COMPRESSOR 1 |  |  | COMPRESSOR 1 | EM | MOTOR | DO | COMPR |  | BB1TT004 | MEAS_ANA | FW pump 1 motor winding temperature | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  | FW PUMP 1 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT004 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM402 | _FAULT_DI | BB1EM402_FAULT_DI | <IO NOT ASSIGNED> | Compressor 1 Fault | COMPRESSOR 1 | FAULT |  | COMPRESSOR 1 FAULT | EM | MOTOR | DO | COMPR |  | BB1TT003 | MEAS_ANA | FW pump 1 motor bearing temperature | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  | FW PUMP 1 MOTOR BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT003 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM402 | _RUNNING_DI | BB1EM402_RUNNING_DI | <IO NOT ASSIGNED> | Compressor 1 Running | COMPRESSOR 1 | RUNNING |  | COMPRESSOR 1 RUNNING | EM | MOTOR | DO | COMPR |  | BB1TT008 | MEAS_ANA | Temperature after economizer | TEMPERATURE AFTER | ECONOMIZER |  | TEMPERATURE AFTER ECONOMIZER | TT | TEMPERATURE TRANSMITTER | BB1TT008 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM402 | _RESERVE_DI | BB1EM402_RESERVE_DI | <IO NOT ASSIGNED> | Compressor 1 reserve | COMPRESSOR 1 | RESERVE |  | COMPRESSOR 1 RESERVE | EM | MOTOR | DO | COMPR |  | BB1FT200 | MEAS_ANA | Heating steam to feed water tank flow measurement | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT | HEATING STEAM TO FEED WATER TANK FLOW MEASUREMENT | FT | FLOW TRANSMITTER | BB1FT200 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM402 | _RUN_DO | BB1EM402_RUN_DO | <IO NOT ASSIGNED> | Compressor 1 remote run | COMPRESSOR 1 | REMOTE RUN |  | COMPRESSOR 1 REMOTE RUN | EM | MOTOR | DO | COMPR |  | BB1TT009 | MEAS_ANA | Temperature before economizer | TEMPERATURE BEFORE | ECONOMIZER |  | TEMPERATURE BEFORE ECONOMIZER | TT | TEMPERATURE TRANSMITTER | BB1TT009 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM402 | _FAULT_ACK_DO | BB1EM402_FAULT_ACK_DO | <IO NOT ASSIGNED> | Compressor 1 Fault Acknowledge | COMPRESSOR 1 | FAULT ACKNOWLEDGE |  | COMPRESSOR 1 FAULT ACKNOWLEDGE | EM | MOTOR | DO | COMPR |  | BB1TT200 | MEAS_ANA | Main steam temperature | MAIN STEAM TEMPERATURE |  |  | MAIN STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT200 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM403 |  | BB1EM403 | <IO NOT ASSIGNED> | Compressor 2 | COMPRESSOR 2 |  |  | COMPRESSOR 2 | EM | MOTOR | DO | COMPR |  | BB1FT202 | MEAS_ANA | Main steam flow | MAIN STEAM FLOW |  |  | MAIN STEAM FLOW | FT | FLOW TRANSMITTER | BB1FT202 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM403 | _FAULT_DI | BB1EM403_FAULT_DI | <IO NOT ASSIGNED> | Compressor 2 Fault | COMPRESSOR 2 | FAULT |  | COMPRESSOR 2 FAULT | EM | MOTOR | DO | COMPR |  | BB1FT201 | MEAS_ANA | Steam flow to sootblowing and air preheater | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  | STEAM FLOW TO SOOTBLOWING AND AIR PREHEATER | FT | FLOW TRANSMITTER | BB1FT201 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM403 | _RUNNING_DI | BB1EM403_RUNNING_DI | <IO NOT ASSIGNED> | Compressor 2 Running | COMPRESSOR 2 | RUNNING |  | COMPRESSOR 2 RUNNING | EM | MOTOR | DO | COMPR |  | BB1TT201 | MEAS_ANA | Sootblowing line temperature | SOOTBLOWING | LINE TEMPERATURE |  | SOOTBLOWING LINE TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT201 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1EM403 | _RESERVE_DI | BB1EM403_RESERVE_DI | <IO NOT ASSIGNED> | Compressor 2 reserve | COMPRESSOR 2 | RESERVE |  | COMPRESSOR 2 RESERVE | EM | MOTOR | DO | COMPR |  | <001> | #N/A | Electrical room temperature | ELECTRICAL ROOM | TEMPERATURE |  | ELECTRICAL ROOM TEMPERATURE | 1> | #N/A | <001> | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM403 | _RUN_DO | BB1EM403_RUN_DO | <IO NOT ASSIGNED> | Compressor 2 remote run | COMPRESSOR 2 | REMOTE RUN |  | COMPRESSOR 2 REMOTE RUN | EM | MOTOR | DO | COMPR |  | <002> | #N/A | PLC-cabinet temperature | PLC-CABINET | TEMPERATURE |  | PLC-CABINET TEMPERATURE | 2> | #N/A | <002> | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
BB1EM403 | _FAULT_ACK_DO | BB1EM403_FAULT_ACK_DO | <IO NOT ASSIGNED> | Compressor 2 Fault Acknowledge | COMPRESSOR 2 | FAULT ACKNOWLEDGE |  | COMPRESSOR 2 FAULT ACKNOWLEDGE | EM | MOTOR | DO | COMPR |  | BB1TT006 | MEAS_ANA | Blow down tank temperature and control | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  | BLOW DOWN TANK TEMPERATURE AND CONTROL | TT | TEMPERATURE TRANSMITTER | BB1TT006 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV200 | _SETPOINT | BB1CV200_SETPOINT | <IO NOT ASSIGNED> | Steam from drum control valve SETPOINT | STEAM FROM DRUM CONTROL | VALVE SETPOINT |  | STEAM FROM DRUM CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1TT202 | MEAS_ANA | Steam outlet temperature from accumulator | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  | STEAM OUTLET TEMPERATURE FROM ACCUMULATOR | TT | TEMPERATURE TRANSMITTER | BB1TT202 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV200 | _POSITION | BB1CV200_POSITION | <IO NOT ASSIGNED> | Steam from drum control valve POSITION | STEAM FROM DRUM CONTROL | VALVE POSITION |  | STEAM FROM DRUM CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1PT207 | MEAS_ANA | Accumulator pressure | ACCUMULATOR PRESSURE |  |  | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT207 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV001 | _SETPOINT | BB1CV001_SETPOINT | <IO NOT ASSIGNED> | Make-up water control valve SETPOINT | MAKE-UP WATER CONTROL | VALVE SETPOINT |  | MAKE-UP WATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1TT007 | MEAS_ANA | Accumulator temperature | ACCUMULATOR TEMPERATURE |  |  | ACCUMULATOR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT007 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV001 | _POSITION | BB1CV001_POSITION | <IO NOT ASSIGNED> | Make-up water control valve POSITION | MAKE-UP WATER CONTROL | VALVE POSITION |  | MAKE-UP WATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1TT203 | MEAS_ANA | 18bar(g) steam temperature | 18BAR(G) STEAM | TEMPERATURE |  | 18BAR(G) STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT203 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV002 | _SETPOINT | BB1CV002_SETPOINT | <IO NOT ASSIGNED> | Feed water control valve SETPOINT | FEED WATER CONTROL VALVE | SETPOINT |  | FEED WATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1PT204 | MEAS_ANA | Main steam pressure | MAIN STEAM PRESSURE |  |  | MAIN STEAM PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT204 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV002 | _POSITION | BB1CV002_POSITION | <IO NOT ASSIGNED> | Feed water control valve POSITION | FEED WATER CONTROL VALVE | POSITION |  | FEED WATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1LT004 | MEAS_ANA | Steam accumulator level 2 | STEAM ACCUMULATOR LEVEL 2 |  |  | STEAM ACCUMULATOR LEVEL 2 | LT | LEVEL TRANSMITTER | BB1LT004 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM300 | _SETPOINT | BB1DM300_SETPOINT | <IO NOT ASSIGNED> | Tertiary air damper 1 SETPOINT | TERTIARY AIR DAMPER 1 | SETPOINT |  | TERTIARY AIR DAMPER 1 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1PT208 | MEAS_ANA | Accumulator pressure | ACCUMULATOR PRESSURE |  |  | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT208 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM300 | _POSITION | BB1DM300_POSITION | <IO NOT ASSIGNED> | Tertiary air damper 1 POSITION | TERTIARY AIR DAMPER 1 | POSITION |  | TERTIARY AIR DAMPER 1 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1FT203 | MEAS_ANA | Steam to existing header flow measurement | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  | STEAM TO EXISTING HEADER FLOW MEASUREMENT | FT | FLOW TRANSMITTER | BB1FT203 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM400 | _SETPOINT | BB1DM400_SETPOINT | <IO NOT ASSIGNED> | Primary air damper SETPOINT | PRIMARY AIR DAMPER | SETPOINT |  | PRIMARY AIR DAMPER SETPOINT | DM | DAMPER | AO | CONT_VLV |  | <003> | #N/A | Steam to existing header energy calculator | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  | STEAM TO EXISTING HEADER ENERGY CALCULATOR | 3> | #N/A | <003> | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
BB1DM400 | _POSITION | BB1DM400_POSITION | <IO NOT ASSIGNED> | Primary air damper POSITION | PRIMARY AIR DAMPER | POSITION |  | PRIMARY AIR DAMPER POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1LT003 | MEAS_ANA | Steam accumulator level 1 | STEAM ACCUMULATOR LEVEL 1 |  |  | STEAM ACCUMULATOR LEVEL 1 | LT | LEVEL TRANSMITTER | BB1LT003 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM550 | _SETPOINT | BB1DM550_SETPOINT | <IO NOT ASSIGNED> | Recirculation gas damper SETPOINT | RECIRCULATION GAS DAMPER | SETPOINT |  | RECIRCULATION GAS DAMPER SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1QT002 | MEAS_ANA | pH measurement from feed water tank | PH MEASUREMENT FROM FEED | WATER TANK |  | PH MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT002 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM550 | _POSITION | BB1DM550_POSITION | <IO NOT ASSIGNED> | Recirculation gas damper POSITION | RECIRCULATION GAS DAMPER | POSITION |  | RECIRCULATION GAS DAMPER POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1QT006 | MEAS_ANA | Conductivity measurement from main steam | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  | CONDUCTIVITY MEASUREMENT FROM MAIN STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT006 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM301 | _SETPOINT | BB1DM301_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 4 SETPOINT | SECONDARY AIR DAMPER 4 | SETPOINT |  | SECONDARY AIR DAMPER 4 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1QT005 | MEAS_ANA | Conductivity measurement from saturated steam | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  | CONDUCTIVITY MEASUREMENT FROM SATURATED STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT005 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM301 | _POSITION | BB1DM301_POSITION | <IO NOT ASSIGNED> | Secondary air damper 4 POSITION | SECONDARY AIR DAMPER 4 | POSITION |  | SECONDARY AIR DAMPER 4 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1QT003 | MEAS_ANA | Conductivity measurement from condensate | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  | CONDUCTIVITY MEASUREMENT FROM CONDENSATE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT003 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM302 | _SETPOINT | BB1DM302_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 3 SETPOINT | SECONDARY AIR DAMPER 3 | SETPOINT |  | SECONDARY AIR DAMPER 3 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1QT007 | MEAS_ANA | Conductivity measurement from feed water line | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  | CONDUCTIVITY MEASUREMENT FROM FEED WATER LINE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT007 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM302 | _POSITION | BB1DM302_POSITION | <IO NOT ASSIGNED> | Secondary air damper 3 POSITION | SECONDARY AIR DAMPER 3 | POSITION |  | SECONDARY AIR DAMPER 3 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1QT001 | MEAS_ANA | Conductivity measurement from feed water tank | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  | CONDUCTIVITY MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM304 | _SETPOINT | BB1DM304_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 1 SETPOINT | SECONDARY AIR DAMPER 1 | SETPOINT |  | SECONDARY AIR DAMPER 1 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1QT004 | MEAS_ANA | Conductivity measurement from boiler water | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  | CONDUCTIVITY MEASUREMENT FROM BOILER WATER | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT004 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM304 | _POSITION | BB1DM304_POSITION | <IO NOT ASSIGNED> | Secondary air damper 1 POSITION | SECONDARY AIR DAMPER 1 | POSITION |  | SECONDARY AIR DAMPER 1 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1PT410 | MEAS_ANA | Secondary air pressure inner front wall | SECONDARY AIR PRESSURE | INNER FRONT WALL |  | SECONDARY AIR PRESSURE INNER FRONT WALL | PT | PRESSURE TRANSMITTER | BB1PT410 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM303 | _SETPOINT | BB1DM303_SETPOINT | <IO NOT ASSIGNED> | Secondary air damper 2 SETPOINT | SECONDARY AIR DAMPER 2 | SETPOINT |  | SECONDARY AIR DAMPER 2 SETPOINT | DM | DAMPER | AO | CONT_VLV |  | BB1TT551 | MEAS_ANA | Flue gas temperature 2 | FLUE GAS TEMPERATURE 2 |  |  | FLUE GAS TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | BB1TT551 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1DM303 | _POSITION | BB1DM303_POSITION | <IO NOT ASSIGNED> | Secondary air damper 2 POSITION | SECONDARY AIR DAMPER 2 | POSITION |  | SECONDARY AIR DAMPER 2 POSITION | DM | DAMPER | AI | CONT_VLV |  | BB1TT400 | MEAS_ANA | Primary air temperature before preheater | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  | PRIMARY AIR TEMPERATURE BEFORE PREHEATER | TT | TEMPERATURE TRANSMITTER | BB1TT400 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV004 | _SETPOINT | BB1CV004_SETPOINT | <IO NOT ASSIGNED> | Primary air preheater control valve SETPOINT | PRIMARY AIR PREHEATER | CONTROL VALVE SETPOINT |  | PRIMARY AIR PREHEATER CONTROL VALVE SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1PT403 | MEAS_ANA | Secondary air pressure inner back wall | SECONDARY AIR PRESSURE | INNER BACK WALL |  | SECONDARY AIR PRESSURE INNER BACK WALL | PT | PRESSURE TRANSMITTER | BB1PT403 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV004 | _POSITION | BB1CV004_POSITION | <IO NOT ASSIGNED> | Primary air preheater control valve POSITION | PRIMARY AIR PREHEATER | CONTROL VALVE POSITION |  | PRIMARY AIR PREHEATER CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1PT550 | MEAS_ANA | Flue gas pressure at the outlet of the boiler | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  | FLUE GAS PRESSURE AT THE OUTLET OF THE BOILER | PT | PRESSURE TRANSMITTER | BB1PT550 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV402 | _SETPOINT | BB1CV402_SETPOINT | <IO NOT ASSIGNED> | Fuel chute B carrying air control valve 2 SETPOINT | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | SETPOINT | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1TT012 | MEAS_ANA | Condensate temperature from primary air preheater | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R | CONDENSATE TEMPERATURE FROM PRIMARY AIR PREHEATE R | TT | TEMPERATURE TRANSMITTER | BB1TT012 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV402 | _POSITION | BB1CV402_POSITION | <IO NOT ASSIGNED> | Fuel chute B carrying air control valve 2 POSITION | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | POSITION | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1TT550 | MEAS_ANA | Flue gas temperature 1 | FLUE GAS TEMPERATURE 1 |  |  | FLUE GAS TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | BB1TT550 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV403 | _SETPOINT | BB1CV403_SETPOINT | <IO NOT ASSIGNED> | Fuel chute A carrying air control valve 1 SETPOINT | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | SETPOINT | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 SETPOINT | CV | CONTROL VALVE | AO | CONT_VLV |  | BB1TT412 | MEAS_ANA | Boiler temperature after empty draft 2 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  | BOILER TEMPERATURE AFTER EMPTY DRAFT 2 | TT | TEMPERATURE TRANSMITTER | BB1TT412 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1CV403 | _POSITION | BB1CV403_POSITION | <IO NOT ASSIGNED> | Fuel chute A carrying air control valve 1 POSITION | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | POSITION | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 POSITION | CV | CONTROL VALVE | AI | CONT_VLV |  | BB1TT411 | MEAS_ANA | Boiler temperature after empty draft 1 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  | BOILER TEMPERATURE AFTER EMPTY DRAFT 1 | TT | TEMPERATURE TRANSMITTER | BB1TT411 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT200 |  | BB1PT200 | <IO NOT ASSIGNED> | Feed water tank pressure | FEED WATER TANK PRESSURE |  |  | FEED WATER TANK PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1QT552 | MEAS_ANA | Fluegas CO measurement | FLUEGAS CO MEASUREMENT |  |  | FLUEGAS CO MEASUREMENT | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT552 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT001 |  | BB1LT001 | <IO NOT ASSIGNED> | Feed water tank level 1 | FEED WATER TANK LEVEL 1 |  |  | FEED WATER TANK LEVEL 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1TT405 | MEAS_ANA | Primary air temperature | PRIMARY AIR TEMPERATURE |  |  | PRIMARY AIR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT405 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT002 |  | BB1LT002 | <IO NOT ASSIGNED> | Feed water tank level 2 | FEED WATER TANK LEVEL 2 |  |  | FEED WATER TANK LEVEL 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1TT415 | MEAS_ANA | Boiler bed temperature middle level | BOILER BED TEMPERATURE | MIDDLE LEVEL |  | BOILER BED TEMPERATURE MIDDLE LEVEL | TT | TEMPERATURE TRANSMITTER | BB1TT415 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT005 |  | BB1PT005 | <IO NOT ASSIGNED> | Feed water pressure after valve | FEED WATER PRESSURE | AFTER VALVE |  | FEED WATER PRESSURE AFTER VALVE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT416 | MEAS_ANA | Boiler bed temperature lower level | BOILER BED TEMPERATURE | LOWER LEVEL |  | BOILER BED TEMPERATURE LOWER LEVEL | TT | TEMPERATURE TRANSMITTER | BB1TT416 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1FT001 |  | BB1FT001 | <IO NOT ASSIGNED> | Feed water flow and control | FEED WATER FLOW | AND CONTROL |  | FEED WATER FLOW AND CONTROL | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1TT410 | MEAS_ANA | Boiler 1st draft temperature | BOILER 1ST DRAFT | TEMPERATURE |  | BOILER 1ST DRAFT TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT410 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT001 |  | BB1TT001 | <IO NOT ASSIGNED> | Feed water temperature | FEED WATER TEMPERATURE |  |  | FEED WATER TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT116 | MEAS_ANA | Steam temperature to air preheater | STEAM TEMPERATURE TO | AIR PREHEATER |  | STEAM TEMPERATURE TO AIR PREHEATER | TT | TEMPERATURE TRANSMITTER | BB1TT116 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT002 |  | BB1TT002 | <IO NOT ASSIGNED> | Feed water pump 2 bearing temperature | FEED WATER PUMP 2 | BEARING TEMPERATURE |  | FEED WATER PUMP 2 BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT308 | MEAS_ANA | Furnace temperature connection | FURNACE TEMPERATURE | CONNECTION |  | FURNACE TEMPERATURE CONNECTION | TT | TEMPERATURE TRANSMITTER | BB1TT308 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT004 |  | BB1PT004 | <IO NOT ASSIGNED> | Feed water pressure before valve | FEED WATER PRESSURE | BEFORE VALVE |  | FEED WATER PRESSURE BEFORE VALVE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1QT553 | MEAS_ANA | Boiler room gas detector | BOILER ROOM GAS DETECTOR |  |  | BOILER ROOM GAS DETECTOR | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT553 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT002 |  | BB1PT002 | <IO NOT ASSIGNED> | Feed water pump 2 pressure side pressure | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  | FEED WATER PUMP 2 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT408 | MEAS_ANA | Secondary air fan motor bearing temperature 1 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | BB1TT408 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT006 |  | BB1PT006 | <IO NOT ASSIGNED> | FW suction line strainer pressure diff. | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT423 | MEAS_ANA | Secondary air fan motor bearing temperature 2 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | BB1TT423 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT007 |  | BB1PT007 | <IO NOT ASSIGNED> | FW suction line strainer pressure diff. | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  | FW SUCTION LINE STRAINER PRESSURE DIFF. | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT406 | MEAS_ANA | Secondary air fan motor winding temperature 1 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | BB1TT406 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT005 |  | BB1TT005 | <IO NOT ASSIGNED> | FW pump 2 motor winding temperature | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  | FW PUMP 2 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT404 | MEAS_ANA | Primary air fan motor bearing temperature 1 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | BB1TT404 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT001 |  | BB1PT001 | <IO NOT ASSIGNED> | Feed water pump 1 pressure side pressure | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  | FEED WATER PUMP 1 PRESSURE SIDE PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT409 | MEAS_ANA | Primary air fan motor bearing temperature 2 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | BB1TT409 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT004 |  | BB1TT004 | <IO NOT ASSIGNED> | FW pump 1 motor winding temperature | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  | FW PUMP 1 MOTOR WINDING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT402 | MEAS_ANA | Primary air fan motor winding temperature 1 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | BB1TT402 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT003 |  | BB1TT003 | <IO NOT ASSIGNED> | FW pump 1 motor bearing temperature | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  | FW PUMP 1 MOTOR BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT403 | MEAS_ANA | Primary air fan motor winding temperature 2 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | BB1TT403 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT008 |  | BB1TT008 | <IO NOT ASSIGNED> | Temperature after economizer | TEMPERATURE AFTER | ECONOMIZER |  | TEMPERATURE AFTER ECONOMIZER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT421 | MEAS_ANA | Primary air fan motor winding temperature 3 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | BB1TT421 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1FT200 |  | BB1FT200 | <IO NOT ASSIGNED> | Heating steam to feed water tank flow measurement | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT | HEATING STEAM TO FEED WATER TANK FLOW MEASUREMENT | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1TT407 | MEAS_ANA | Secondary air fan motor winding temperature 2 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | BB1TT407 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT009 |  | BB1TT009 | <IO NOT ASSIGNED> | Temperature before economizer | TEMPERATURE BEFORE | ECONOMIZER |  | TEMPERATURE BEFORE ECONOMIZER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT422 | MEAS_ANA | Secondary air fan motor winding temperature 3 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | BB1TT422 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT200 |  | BB1TT200 | <IO NOT ASSIGNED> | Main steam temperature | MAIN STEAM TEMPERATURE |  |  | MAIN STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT409 | MEAS_ANA | Secondary air pressure outer front wall | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  | SECONDARY AIR PRESSURE OUTER FRONT WALL | PT | PRESSURE TRANSMITTER | BB1PT409 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1FT202 |  | BB1FT202 | <IO NOT ASSIGNED> | Main steam flow | MAIN STEAM FLOW |  |  | MAIN STEAM FLOW | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1PT411 | MEAS_ANA | Secondary air pressure outer back wall | SECONDARY AIR PRESSURE | OUTER BACK WALL |  | SECONDARY AIR PRESSURE OUTER BACK WALL | PT | PRESSURE TRANSMITTER | BB1PT411 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1FT201 |  | BB1FT201 | <IO NOT ASSIGNED> | Steam flow to sootblowing and air preheater | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  | STEAM FLOW TO SOOTBLOWING AND AIR PREHEATER | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1PT407 | MEAS_ANA | Tertiary air pressure right wall | TERTIARY AIR PRESSURE | RIGHT WALL |  | TERTIARY AIR PRESSURE RIGHT WALL | PT | PRESSURE TRANSMITTER | BB1PT407 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT201 |  | BB1TT201 | <IO NOT ASSIGNED> | Sootblowing line temperature | SOOTBLOWING | LINE TEMPERATURE |  | SOOTBLOWING LINE TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT408 | MEAS_ANA | Tertiary air pressure left wall | TERTIARY AIR PRESSURE | LEFT WALL |  | TERTIARY AIR PRESSURE LEFT WALL | PT | PRESSURE TRANSMITTER | BB1PT408 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
<001> |  | <001> | <IO NOT ASSIGNED> | Electrical room temperature | ELECTRICAL ROOM | TEMPERATURE |  | ELECTRICAL ROOM TEMPERATURE | 1> | #N/A | AI | #N/A |  | BB1TT650 | MEAS_ANA | Scraper conveyor 1 temperature measurement | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  | SCRAPER CONVEYOR 1 TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | BB1TT650 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
<002> |  | <002> | <IO NOT ASSIGNED> | PLC-cabinet temperature | PLC-CABINET | TEMPERATURE |  | PLC-CABINET TEMPERATURE | 2> | #N/A | AI | #N/A |  | BB1LT611 | MEAS_ANA | Unloading station 1 level | UNLOADING STATION 1 LEVEL |  |  | UNLOADING STATION 1 LEVEL | LT | LEVEL TRANSMITTER | BB1LT611 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT006 |  | BB1TT006 | <IO NOT ASSIGNED> | Blow down tank temperature and control | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  | BLOW DOWN TANK TEMPERATURE AND CONTROL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT612 | MEAS_ANA | Unloading station 3 level | UNLOADING STATION 3 LEVEL |  |  | UNLOADING STATION 3 LEVEL | LT | LEVEL TRANSMITTER | BB1LT612 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT202 |  | BB1TT202 | <IO NOT ASSIGNED> | Steam outlet temperature from accumulator | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  | STEAM OUTLET TEMPERATURE FROM ACCUMULATOR | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT613 | MEAS_ANA | Unloading station 2 level | UNLOADING STATION 2 LEVEL |  |  | UNLOADING STATION 2 LEVEL | LT | LEVEL TRANSMITTER | BB1LT613 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT207 |  | BB1PT207 | <IO NOT ASSIGNED> | Accumulator pressure | ACCUMULATOR PRESSURE |  |  | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT650 | MEAS_ANA | Fuel silo level radar 1 | FUEL SILO LEVEL RADAR 1 |  |  | FUEL SILO LEVEL RADAR 1 | LT | LEVEL TRANSMITTER | BB1LT650 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT007 |  | BB1TT007 | <IO NOT ASSIGNED> | Accumulator temperature | ACCUMULATOR TEMPERATURE |  |  | ACCUMULATOR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT651 | MEAS_ANA | Fuel silo level radar 2 | FUEL SILO LEVEL RADAR 2 |  |  | FUEL SILO LEVEL RADAR 2 | LT | LEVEL TRANSMITTER | BB1LT651 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT203 |  | BB1TT203 | <IO NOT ASSIGNED> | 18bar(g) steam temperature | 18BAR(G) STEAM | TEMPERATURE |  | 18BAR(G) STEAM TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT652 | MEAS_ANA | Fuel pocket level | FUEL POCKET LEVEL |  |  | FUEL POCKET LEVEL | LT | LEVEL TRANSMITTER | BB1LT652 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT204 |  | BB1PT204 | <IO NOT ASSIGNED> | Main steam pressure | MAIN STEAM PRESSURE |  |  | MAIN STEAM PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT652 | MEAS_ANA | Fuel silo temperature measurement | FUEL SILO TEMPERATURE | MEASUREMENT |  | FUEL SILO TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | BB1TT652 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT004 |  | BB1LT004 | <IO NOT ASSIGNED> | Steam accumulator level 2 | STEAM ACCUMULATOR LEVEL 2 |  |  | STEAM ACCUMULATOR LEVEL 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1TT653 | MEAS_ANA | Fuel pocket temperature | FUEL POCKET TEMPERATURE |  |  | FUEL POCKET TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT653 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT208 |  | BB1PT208 | <IO NOT ASSIGNED> | Accumulator pressure | ACCUMULATOR PRESSURE |  |  | ACCUMULATOR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT552 | MEAS_ANA | ESP inlet pressure transmitter | ESP INLET PRESSURE | TRANSMITTER |  | ESP INLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | BB1PT552 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1FT203 |  | BB1FT203 | <IO NOT ASSIGNED> | Steam to existing header flow measurement | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  | STEAM TO EXISTING HEADER FLOW MEASUREMENT | FT | FLOW TRANSMITTER | AI | MEAS_ANA |  | BB1PT553 | MEAS_ANA | ESP outlet pressure transmitter | ESP OUTLET PRESSURE | TRANSMITTER |  | ESP OUTLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | BB1PT553 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
<003> |  | <003> | <IO NOT ASSIGNED> | Steam to existing header energy calculator | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  | STEAM TO EXISTING HEADER ENERGY CALCULATOR | 3> | #N/A | AI | #N/A |  | BB1QT554 | MEAS_ANA | Opacity after ESP | OPACITY AFTER ESP |  |  | OPACITY AFTER ESP | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT554 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT003 |  | BB1LT003 | <IO NOT ASSIGNED> | Steam accumulator level 1 | STEAM ACCUMULATOR LEVEL 1 |  |  | STEAM ACCUMULATOR LEVEL 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1TT553 | MEAS_ANA | Flue gas fan motor winding temperature 1 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | BB1TT553 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT002 |  | BB1QT002 | <IO NOT ASSIGNED> | pH measurement from feed water tank | PH MEASUREMENT FROM FEED | WATER TANK |  | PH MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT557 | MEAS_ANA | Flue gas fan motor winding temperature 2 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | BB1TT557 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT006 |  | BB1QT006 | <IO NOT ASSIGNED> | Conductivity measurement from main steam | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  | CONDUCTIVITY MEASUREMENT FROM MAIN STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT558 | MEAS_ANA | Flue gas fan motor winding temperature 3 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | BB1TT558 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT005 |  | BB1QT005 | <IO NOT ASSIGNED> | Conductivity measurement from saturated steam | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  | CONDUCTIVITY MEASUREMENT FROM SATURATED STEAM | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT554 | MEAS_ANA | Flue gas fan bearing temperature | FLUE GAS FAN BEARING | TEMPERATURE |  | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT554 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT003 |  | BB1QT003 | <IO NOT ASSIGNED> | Conductivity measurement from condensate | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  | CONDUCTIVITY MEASUREMENT FROM CONDENSATE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT555 | MEAS_ANA | Flue gas fan bearing temperature | FLUE GAS FAN BEARING | TEMPERATURE |  | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT555 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT007 |  | BB1QT007 | <IO NOT ASSIGNED> | Conductivity measurement from feed water line | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  | CONDUCTIVITY MEASUREMENT FROM FEED WATER LINE | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT556 | MEAS_ANA | Flue gas temperature before stack | FLUE GAS TEMPERATURE | BEFORE STACK |  | FLUE GAS TEMPERATURE BEFORE STACK | TT | TEMPERATURE TRANSMITTER | BB1TT556 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT001 |  | BB1QT001 | <IO NOT ASSIGNED> | Conductivity measurement from feed water tank | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  | CONDUCTIVITY MEASUREMENT FROM FEED WATER TANK | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT850 | MEAS_ANA | ESP Ash hopper 1 temperature | ESP ASH HOPPER 1 | TEMPERATURE |  | ESP ASH HOPPER 1 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT850 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT004 |  | BB1QT004 | <IO NOT ASSIGNED> | Conductivity measurement from boiler water | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  | CONDUCTIVITY MEASUREMENT FROM BOILER WATER | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT851 | MEAS_ANA | ESP Ash hopper 2 temperature | ESP ASH HOPPER 2 | TEMPERATURE |  | ESP ASH HOPPER 2 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT851 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT410 |  | BB1PT410 | <IO NOT ASSIGNED> | Secondary air pressure inner front wall | SECONDARY AIR PRESSURE | INNER FRONT WALL |  | SECONDARY AIR PRESSURE INNER FRONT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1TS501 | MEAS_ANA | ESP Insulator 1 temperature | ESP INSULATOR 1 | TEMPERATURE |  | ESP INSULATOR 1 TEMPERATURE | TS | TEMPERATURE SWITCH | BB1TS501 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT551 |  | BB1TT551 | <IO NOT ASSIGNED> | Flue gas temperature 2 | FLUE GAS TEMPERATURE 2 |  |  | FLUE GAS TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TS508 | MEAS_ANA | ESP Insulator 2 temperature | ESP INSULATOR 2 | TEMPERATURE |  | ESP INSULATOR 2 TEMPERATURE | TS | TEMPERATURE SWITCH | BB1TS508 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT400 |  | BB1TT400 | <IO NOT ASSIGNED> | Primary air temperature before preheater | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  | PRIMARY AIR TEMPERATURE BEFORE PREHEATER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT552 | MEAS_ANA | Flue gas temperature before ESP | FLUE GAS TEMPERATURE | BEFORE ESP |  | FLUE GAS TEMPERATURE BEFORE ESP | TT | TEMPERATURE TRANSMITTER | BB1TT552 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT403 |  | BB1PT403 | <IO NOT ASSIGNED> | Secondary air pressure inner back wall | SECONDARY AIR PRESSURE | INNER BACK WALL |  | SECONDARY AIR PRESSURE INNER BACK WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT800 | MEAS_ANA | Recycled bed material hopper level switch | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  | RECYCLED BED MATERIAL HOPPER LEVEL SWITCH | LT | LEVEL TRANSMITTER | BB1LT800 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT550 |  | BB1PT550 | <IO NOT ASSIGNED> | Flue gas pressure at the outlet of the boiler | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  | FLUE GAS PRESSURE AT THE OUTLET OF THE BOILER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT802 | MEAS_ANA | Sand silo level measurement | SAND SILO LEVEL | MEASUREMENT |  | SAND SILO LEVEL MEASUREMENT | LT | LEVEL TRANSMITTER | BB1LT802 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT012 |  | BB1TT012 | <IO NOT ASSIGNED> | Condensate temperature from primary air preheater | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R | CONDENSATE TEMPERATURE FROM PRIMARY AIR PREHEATE R | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT009 | MEAS_ANA | Cooling water pressure before pump | COOLING WATER PRESSURE | BEFORE PUMP |  | COOLING WATER PRESSURE BEFORE PUMP | PT | PRESSURE TRANSMITTER | BB1PT009 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT550 |  | BB1TT550 | <IO NOT ASSIGNED> | Flue gas temperature 1 | FLUE GAS TEMPERATURE 1 |  |  | FLUE GAS TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT031 | MEAS_ANA | Cooling water temperatureafter bottom ash conveyor | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  | COOLING WATER TEMPERATURE AFTER BOTTOM ASH CONVEYOR | TT | TEMPERATURE TRANSMITTER | BB1TT031 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT412 |  | BB1TT412 | <IO NOT ASSIGNED> | Boiler temperature after empty draft 2 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  | BOILER TEMPERATURE AFTER EMPTY DRAFT 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT478 | MEAS_ANA | Instrument air pressure | INSTRUMENT AIR PRESSURE |  |  | INSTRUMENT AIR PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT478 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT411 |  | BB1TT411 | <IO NOT ASSIGNED> | Boiler temperature after empty draft 1 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  | BOILER TEMPERATURE AFTER EMPTY DRAFT 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT402 | MEAS_ANA | Instrument air pressure after dryer | INSTRUMENT AIR PRESSURE | AFTER DRYER |  | INSTRUMENT AIR PRESSURE AFTER DRYER | PT | PRESSURE TRANSMITTER | BB1PT402 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT552 |  | BB1QT552 | <IO NOT ASSIGNED> | Fluegas CO measurement | FLUEGAS CO MEASUREMENT |  |  | FLUEGAS CO MEASUREMENT | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1TT430 | MEAS_ANA | Instrument air tank temperature | INSTRUMENT AIR TANK | TEMPERATURE |  | INSTRUMENT AIR TANK TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT430 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT405 |  | BB1TT405 | <IO NOT ASSIGNED> | Primary air temperature | PRIMARY AIR TEMPERATURE |  |  | PRIMARY AIR TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT401 | MEAS_ANA | Boiler room upper part temperature | BOILER ROOM UPPER PART | TEMPERATURE |  | BOILER ROOM UPPER PART TEMPERATURE | TT | TEMPERATURE TRANSMITTER | BB1TT401 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT415 |  | BB1TT415 | <IO NOT ASSIGNED> | Boiler bed temperature middle level | BOILER BED TEMPERATURE | MIDDLE LEVEL |  | BOILER BED TEMPERATURE MIDDLE LEVEL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT101 | MEAS_ANA_SRS | Steam drum level 1 | STEAM DRUM LEVEL 1 |  |  | STEAM DRUM LEVEL 1 | LT | LEVEL TRANSMITTER | BB1LT101 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT416 |  | BB1TT416 | <IO NOT ASSIGNED> | Boiler bed temperature lower level | BOILER BED TEMPERATURE | LOWER LEVEL |  | BOILER BED TEMPERATURE LOWER LEVEL | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT203 | MEAS_ANA_SRS | Steam drum pressure 2 | STEAM DRUM PRESSURE 2 |  |  | STEAM DRUM PRESSURE 2 | PT | PRESSURE TRANSMITTER | BB1PT203 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT410 |  | BB1TT410 | <IO NOT ASSIGNED> | Boiler 1st draft temperature | BOILER 1ST DRAFT | TEMPERATURE |  | BOILER 1ST DRAFT TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT102 | MEAS_ANA_SRS | Steam drum level 2 | STEAM DRUM LEVEL 2 |  |  | STEAM DRUM LEVEL 2 | LT | LEVEL TRANSMITTER | BB1LT102 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT116 |  | BB1TT116 | <IO NOT ASSIGNED> | Steam temperature to air preheater | STEAM TEMPERATURE TO | AIR PREHEATER |  | STEAM TEMPERATURE TO AIR PREHEATER | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT201 | MEAS_ANA_SRS | Steam drum pressure 1 | STEAM DRUM PRESSURE 1 |  |  | STEAM DRUM PRESSURE 1 | PT | PRESSURE TRANSMITTER | BB1PT201 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT308 |  | BB1TT308 | <IO NOT ASSIGNED> | Furnace temperature connection | FURNACE TEMPERATURE | CONNECTION |  | FURNACE TEMPERATURE CONNECTION | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LT103 | MEAS_ANA_SRS | Steam drum level 3 | STEAM DRUM LEVEL 3 |  |  | STEAM DRUM LEVEL 3 | LT | LEVEL TRANSMITTER | BB1LT103 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT553 |  | BB1QT553 | <IO NOT ASSIGNED> | Boiler room gas detector | BOILER ROOM GAS DETECTOR |  |  | BOILER ROOM GAS DETECTOR | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1PT205 | MEAS_ANA_SRS | Steam outlet pressure from accumulator | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  | STEAM OUTLET PRESSURE FROM ACCUMULATOR | PT | PRESSURE TRANSMITTER | BB1PT205 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT408 |  | BB1TT408 | <IO NOT ASSIGNED> | Secondary air fan motor bearing temperature 1 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT400 | MEAS_ANA_SRS | Primary air pressure | PRIMARY AIR PRESSURE |  |  | PRIMARY AIR PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT400 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT423 |  | BB1TT423 | <IO NOT ASSIGNED> | Secondary air fan motor bearing temperature 2 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT418 | MEAS_ANA_SRS | Bed temperature 4 | BED TEMPERATURE 4 |  |  | BED TEMPERATURE 4 | TT | TEMPERATURE TRANSMITTER | BB1TT418 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT406 |  | BB1TT406 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 1 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT404 | MEAS_ANA_SRS | Boiler upper part pressure 1 | BOILER UPPER PART | PRESSURE 1 |  | BOILER UPPER PART PRESSURE 1 | PT | PRESSURE TRANSMITTER | BB1PT404 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT404 |  | BB1TT404 | <IO NOT ASSIGNED> | Primary air fan motor bearing temperature 1 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1FT400 | MEAS_ANA_SRS | Primary air flow | PRIMARY AIR FLOW |  |  | PRIMARY AIR FLOW | FT | FLOW TRANSMITTER | BB1FT400 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT409 |  | BB1TT409 | <IO NOT ASSIGNED> | Primary air fan motor bearing temperature 2 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT401 | MEAS_ANA_SRS | Secondary air pressure | SECONDARY AIR PRESSURE |  |  | SECONDARY AIR PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT401 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT402 |  | BB1TT402 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 1 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1FT401 | MEAS_ANA_SRS | Secondary air flow | SECONDARY AIR FLOW |  |  | SECONDARY AIR FLOW | FT | FLOW TRANSMITTER | BB1FT401 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT403 |  | BB1TT403 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 2 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT417 | MEAS_ANA_SRS | Bed temperature 3 | BED TEMPERATURE 3 |  |  | BED TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | BB1TT417 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT421 |  | BB1TT421 | <IO NOT ASSIGNED> | Primary air fan motor winding temperature 3 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT413 | MEAS_ANA_SRS | Bed temperature 1 | BED TEMPERATURE 1 |  |  | BED TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | BB1TT413 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT407 |  | BB1TT407 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 2 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1TT414 | MEAS_ANA_SRS | Bed temperature 2 | BED TEMPERATURE 2 |  |  | BED TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | BB1TT414 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT422 |  | BB1TT422 | <IO NOT ASSIGNED> | Secondary air fan motor winding temperature 3 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT405 | MEAS_ANA_SRS | Boiler upper part pressure 2 | BOILER UPPER PART | PRESSURE 2 |  | BOILER UPPER PART PRESSURE 2 | PT | PRESSURE TRANSMITTER | BB1PT405 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT409 |  | BB1PT409 | <IO NOT ASSIGNED> | Secondary air pressure outer front wall | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  | SECONDARY AIR PRESSURE OUTER FRONT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1QT550 | MEAS_ANA_SRS | Fluegas oxygen measurement 1 | FLUEGAS OXYGEN | MEASUREMENT 1 |  | FLUEGAS OXYGEN MEASUREMENT 1 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT550 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT411 |  | BB1PT411 | <IO NOT ASSIGNED> | Secondary air pressure outer back wall | SECONDARY AIR PRESSURE | OUTER BACK WALL |  | SECONDARY AIR PRESSURE OUTER BACK WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1FT550 | MEAS_ANA_SRS | Recirculation gas flow | RECIRCULATION GAS FLOW |  |  | RECIRCULATION GAS FLOW | FT | FLOW TRANSMITTER | BB1FT550 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT407 |  | BB1PT407 | <IO NOT ASSIGNED> | Tertiary air pressure right wall | TERTIARY AIR PRESSURE | RIGHT WALL |  | TERTIARY AIR PRESSURE RIGHT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1QT551 | MEAS_ANA_SRS | Fluegas oxygen measurement 2 | FLUEGAS OXYGEN | MEASUREMENT 2 |  | FLUEGAS OXYGEN MEASUREMENT 2 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | BB1QT551 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT408 |  | BB1PT408 | <IO NOT ASSIGNED> | Tertiary air pressure left wall | TERTIARY AIR PRESSURE | LEFT WALL |  | TERTIARY AIR PRESSURE LEFT WALL | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1PT406 | MEAS_ANA_SRS | Boiler upper part pressure | BOILER UPPER PART | PRESSURE |  | BOILER UPPER PART PRESSURE | PT | PRESSURE TRANSMITTER | BB1PT406 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT650 |  | BB1TT650 | <IO NOT ASSIGNED> | Scraper conveyor 1 temperature measurement | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  | SCRAPER CONVEYOR 1 TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1LS700 | MEAS_BIN | Chemical tank 1 level switch | CHEMICAL TANK 1 | LEVEL SWITCH |  | CHEMICAL TANK 1 LEVEL SWITCH | LS | LEVEL SWITCH | BB1LS700 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT611 |  | BB1LT611 | <IO NOT ASSIGNED> | Unloading station 1 level | UNLOADING STATION 1 LEVEL |  |  | UNLOADING STATION 1 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1LS701 | MEAS_BIN | Chemical tank 2 level switch | CHEMICAL TANK 2 | LEVEL SWITCH |  | CHEMICAL TANK 2 LEVEL SWITCH | LS | LEVEL SWITCH | BB1LS701 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT612 |  | BB1LT612 | <IO NOT ASSIGNED> | Unloading station 3 level | UNLOADING STATION 3 LEVEL |  |  | UNLOADING STATION 3 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS004 | MEAS_BIN | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | BB1GS004 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT613 |  | BB1LT613 | <IO NOT ASSIGNED> | Unloading station 2 level | UNLOADING STATION 2 LEVEL |  |  | UNLOADING STATION 2 LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS003 | MEAS_BIN | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | BB1GS003 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT650 |  | BB1LT650 | <IO NOT ASSIGNED> | Fuel silo level radar 1 | FUEL SILO LEVEL RADAR 1 |  |  | FUEL SILO LEVEL RADAR 1 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS001 | MEAS_BIN | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | BB1GS001 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT651 |  | BB1LT651 | <IO NOT ASSIGNED> | Fuel silo level radar 2 | FUEL SILO LEVEL RADAR 2 |  |  | FUEL SILO LEVEL RADAR 2 | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS002 | MEAS_BIN | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | BB1GS002 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT652 |  | BB1LT652 | <IO NOT ASSIGNED> | Fuel pocket level | FUEL POCKET LEVEL |  |  | FUEL POCKET LEVEL | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS005 | MEAS_BIN | FW tank overflow On-Off valve position | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | BB1GS005 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT652 |  | BB1TT652 | <IO NOT ASSIGNED> | Fuel silo temperature measurement | FUEL SILO TEMPERATURE | MEASUREMENT |  | FUEL SILO TEMPERATURE MEASUREMENT | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS006 | MEAS_BIN | FW tank overflow On-Off valve position | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | BB1GS006 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT653 |  | BB1TT653 | <IO NOT ASSIGNED> | Fuel pocket temperature | FUEL POCKET TEMPERATURE |  |  | FUEL POCKET TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS007 | MEAS_BIN | Feedwater pump 1 on-off valve limit switch open | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | BB1GS007 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT552 |  | BB1PT552 | <IO NOT ASSIGNED> | ESP inlet pressure transmitter | ESP INLET PRESSURE | TRANSMITTER |  | ESP INLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS008 | MEAS_BIN | Feedwater pump 1 on-off valve limit switch close | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | BB1GS008 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT553 |  | BB1PT553 | <IO NOT ASSIGNED> | ESP outlet pressure transmitter | ESP OUTLET PRESSURE | TRANSMITTER |  | ESP OUTLET PRESSURE TRANSMITTER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS009 | MEAS_BIN | Feed water pump 2 on-off valve limit switch open | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | BB1GS009 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT554 |  | BB1QT554 | <IO NOT ASSIGNED> | Opacity after ESP | OPACITY AFTER ESP |  |  | OPACITY AFTER ESP | QT | GAS/pH/CONDUCTIVITY TRANSMITTER | AI | MEAS_ANA |  | BB1GS010 | MEAS_BIN | Feed water pump 2 on-off valve limit switch close | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | BB1GS010 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT553 |  | BB1TT553 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 1 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS011 | MEAS_BIN | Boiler bottom blow down on-off valve limit switch open | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | BB1GS011 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT557 |  | BB1TT557 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 2 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS012 | MEAS_BIN | Boiler bottom blow down on-off valve limit switch close | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | BB1GS012 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT558 |  | BB1TT558 | <IO NOT ASSIGNED> | Flue gas fan motor winding temperature 3 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  | FLUE GAS FAN MOTOR WINDING TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS221 | MEAS_BIN | Main steam valve by-pass open limit switch | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | MAIN STEAM VALVE BY-PASS OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS221 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT554 |  | BB1TT554 | <IO NOT ASSIGNED> | Flue gas fan bearing temperature | FLUE GAS FAN BEARING | TEMPERATURE |  | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS222 | MEAS_BIN | Main steam valve by-pass close limit switch | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | MAIN STEAM VALVE BY-PASS CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS222 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT555 |  | BB1TT555 | <IO NOT ASSIGNED> | Flue gas fan bearing temperature | FLUE GAS FAN BEARING | TEMPERATURE |  | FLUE GAS FAN BEARING TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS223 | MEAS_BIN | Main steam line valve open limit switch | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | MAIN STEAM LINE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS223 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT556 |  | BB1TT556 | <IO NOT ASSIGNED> | Flue gas temperature before stack | FLUE GAS TEMPERATURE | BEFORE STACK |  | FLUE GAS TEMPERATURE BEFORE STACK | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS224 | MEAS_BIN | Main steam line valve close limit switch | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | MAIN STEAM LINE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS224 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT850 |  | BB1TT850 | <IO NOT ASSIGNED> | ESP Ash hopper 1 temperature | ESP ASH HOPPER 1 | TEMPERATURE |  | ESP ASH HOPPER 1 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS225 | MEAS_BIN | Start-up line ON-OFF valve open limit switch | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | START-UP LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS225 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT851 |  | BB1TT851 | <IO NOT ASSIGNED> | ESP Ash hopper 2 temperature | ESP ASH HOPPER 2 | TEMPERATURE |  | ESP ASH HOPPER 2 TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS226 | MEAS_BIN | Start-up line ON-OFF valve close limit switch | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | START-UP LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS226 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TS501 |  | BB1TS501 | <IO NOT ASSIGNED> | ESP Insulator 1 temperature | ESP INSULATOR 1 | TEMPERATURE |  | ESP INSULATOR 1 TEMPERATURE | TS | TEMPERATURE SWITCH | AI | MEAS_ANA |  | BB1GS200 | MEAS_BIN | Sootblower 1 IN limit switch | SOOTBLOWER 1 IN | LIMIT SWITCH |  | SOOTBLOWER 1 IN LIMIT SWITCH | GS | GATE SWITCH | BB1GS200 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TS508 |  | BB1TS508 | <IO NOT ASSIGNED> | ESP Insulator 2 temperature | ESP INSULATOR 2 | TEMPERATURE |  | ESP INSULATOR 2 TEMPERATURE | TS | TEMPERATURE SWITCH | AI | MEAS_ANA |  | BB1GS201 | MEAS_BIN | Sootblower 1 OUT limit switch | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | SOOTBLOWER 1 OUT LIMIT SWITCH | GS | GATE SWITCH | BB1GS201 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT552 |  | BB1TT552 | <IO NOT ASSIGNED> | Flue gas temperature before ESP | FLUE GAS TEMPERATURE | BEFORE ESP |  | FLUE GAS TEMPERATURE BEFORE ESP | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS203 | MEAS_BIN | Sootblower 2 OUT limit switch | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | SOOTBLOWER 2 OUT LIMIT SWITCH | GS | GATE SWITCH | BB1GS203 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT800 |  | BB1LT800 | <IO NOT ASSIGNED> | Recycled bed material hopper level switch | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  | RECYCLED BED MATERIAL HOPPER LEVEL SWITCH | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS204 | MEAS_BIN | Sootblower 2 IN limit switch | SOOTBLOWER 2 IN | LIMIT SWITCH |  | SOOTBLOWER 2 IN LIMIT SWITCH | GS | GATE SWITCH | BB1GS204 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT802 |  | BB1LT802 | <IO NOT ASSIGNED> | Sand silo level measurement | SAND SILO LEVEL | MEASUREMENT |  | SAND SILO LEVEL MEASUREMENT | LT | LEVEL TRANSMITTER | AI | MEAS_ANA |  | BB1GS205 | MEAS_BIN | Sootblower 3 OUT limit switch | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | SOOTBLOWER 3 OUT LIMIT SWITCH | GS | GATE SWITCH | BB1GS205 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT009 |  | BB1PT009 | <IO NOT ASSIGNED> | Cooling water pressure before pump | COOLING WATER PRESSURE | BEFORE PUMP |  | COOLING WATER PRESSURE BEFORE PUMP | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS206 | MEAS_BIN | Sootblower 3 IN limit switch | SOOTBLOWER 3 IN | LIMIT SWITCH |  | SOOTBLOWER 3 IN LIMIT SWITCH | GS | GATE SWITCH | BB1GS206 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT031 |  | BB1TT031 | <IO NOT ASSIGNED> | Cooling water temperatureafter bottom ash conveyor | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  | COOLING WATER TEMPERATURE AFTER BOTTOM ASH CONVEYOR | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS207 | MEAS_BIN | Sootblower 5 OUT limit switch | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | SOOTBLOWER 5 OUT LIMIT SWITCH | GS | GATE SWITCH | BB1GS207 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT478 |  | BB1PT478 | <IO NOT ASSIGNED> | Instrument air pressure | INSTRUMENT AIR PRESSURE |  |  | INSTRUMENT AIR PRESSURE | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS208 | MEAS_BIN | Sootblower 5 IN limit switch | SOOTBLOWER 5 IN | LIMIT SWITCH |  | SOOTBLOWER 5 IN LIMIT SWITCH | GS | GATE SWITCH | BB1GS208 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT402 |  | BB1PT402 | <IO NOT ASSIGNED> | Instrument air pressure after dryer | INSTRUMENT AIR PRESSURE | AFTER DRYER |  | INSTRUMENT AIR PRESSURE AFTER DRYER | PT | PRESSURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS209 | MEAS_BIN | Sootblower 6 OUT limit switch | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | SOOTBLOWER 6 OUT LIMIT SWITCH | GS | GATE SWITCH | BB1GS209 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT430 |  | BB1TT430 | <IO NOT ASSIGNED> | Instrument air tank temperature | INSTRUMENT AIR TANK | TEMPERATURE |  | INSTRUMENT AIR TANK TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS210 | MEAS_BIN | Sootblower 6 IN limit switch | SOOTBLOWER 6 IN | LIMIT SWITCH |  | SOOTBLOWER 6 IN LIMIT SWITCH | GS | GATE SWITCH | BB1GS210 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT401 |  | BB1TT401 | <IO NOT ASSIGNED> | Boiler room upper part temperature | BOILER ROOM UPPER PART | TEMPERATURE |  | BOILER ROOM UPPER PART TEMPERATURE | TT | TEMPERATURE TRANSMITTER | AI | MEAS_ANA |  | BB1GS211 | MEAS_BIN | Sootblower 7 OUT limit switch | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | SOOTBLOWER 7 OUT LIMIT SWITCH | GS | GATE SWITCH | BB1GS211 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT101 |  | BB1LT101 | <IO NOT ASSIGNED> | Steam drum level 1 | STEAM DRUM LEVEL 1 |  |  | STEAM DRUM LEVEL 1 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS212 | MEAS_BIN | Sootblower 7 IN limit switch | SOOTBLOWER 7 IN | LIMIT SWITCH |  | SOOTBLOWER 7 IN LIMIT SWITCH | GS | GATE SWITCH | BB1GS212 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT203 |  | BB1PT203 | <IO NOT ASSIGNED> | Steam drum pressure 2 | STEAM DRUM PRESSURE 2 |  |  | STEAM DRUM PRESSURE 2 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS213 | MEAS_BIN | Sootblower 8 OUT limit switch | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | SOOTBLOWER 8 OUT LIMIT SWITCH | GS | GATE SWITCH | BB1GS213 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT102 |  | BB1LT102 | <IO NOT ASSIGNED> | Steam drum level 2 | STEAM DRUM LEVEL 2 |  |  | STEAM DRUM LEVEL 2 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS214 | MEAS_BIN | Sootblower 8 IN limit switch | SOOTBLOWER 8 IN | LIMIT SWITCH |  | SOOTBLOWER 8 IN LIMIT SWITCH | GS | GATE SWITCH | BB1GS214 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT201 |  | BB1PT201 | <IO NOT ASSIGNED> | Steam drum pressure 1 | STEAM DRUM PRESSURE 1 |  |  | STEAM DRUM PRESSURE 1 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS227 | MEAS_BIN | Sootblowing line on-off valve open limit switch | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | SOOTBLOWING LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS227 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LT103 |  | BB1LT103 | <IO NOT ASSIGNED> | Steam drum level 3 | STEAM DRUM LEVEL 3 |  |  | STEAM DRUM LEVEL 3 | LT | LEVEL TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS228 | MEAS_BIN | Sootblowing line on-off valve close limit switch | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | SOOTBLOWING LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS228 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT205 |  | BB1PT205 | <IO NOT ASSIGNED> | Steam outlet pressure from accumulator | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  | STEAM OUTLET PRESSURE FROM ACCUMULATOR | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS231 | MEAS_BIN | Steam accumulator pressure control valve open limit switch | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS231 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT400 |  | BB1PT400 | <IO NOT ASSIGNED> | Primary air pressure | PRIMARY AIR PRESSURE |  |  | PRIMARY AIR PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS230 | MEAS_BIN | Steam accumulator pressure control valve close limit switch | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS230 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT418 |  | BB1TT418 | <IO NOT ASSIGNED> | Bed temperature 4 | BED TEMPERATURE 4 |  |  | BED TEMPERATURE 4 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS233 | MEAS_BIN | Steam pressure reduction valve open limit switch | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | STEAM PRESSURE REDUCTION VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS233 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT404 |  | BB1PT404 | <IO NOT ASSIGNED> | Boiler upper part pressure 1 | BOILER UPPER PART | PRESSURE 1 |  | BOILER UPPER PART PRESSURE 1 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS232 | MEAS_BIN | Steam pressure reduction valve close limit switch | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | STEAM PRESSURE REDUCTION VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS232 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1FT400 |  | BB1FT400 | <IO NOT ASSIGNED> | Primary air flow | PRIMARY AIR FLOW |  |  | PRIMARY AIR FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS217 | MEAS_BIN | Main steam line accumulator bypass on-offvalve open limit switch | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS217 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT401 |  | BB1PT401 | <IO NOT ASSIGNED> | Secondary air pressure | SECONDARY AIR PRESSURE |  |  | SECONDARY AIR PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS218 | MEAS_BIN | Main steam line accumulator bypass on-offvalve close limit switch | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS218 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1FT401 |  | BB1FT401 | <IO NOT ASSIGNED> | Secondary air flow | SECONDARY AIR FLOW |  |  | SECONDARY AIR FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS219 | MEAS_BIN | Steam accumulator ON-OFF isolating valve open limit switch | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS219 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT417 |  | BB1TT417 | <IO NOT ASSIGNED> | Bed temperature 3 | BED TEMPERATURE 3 |  |  | BED TEMPERATURE 3 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS220 | MEAS_BIN | Steam accumulator ON-OFF isolating valve close limit switch | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS220 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT413 |  | BB1TT413 | <IO NOT ASSIGNED> | Bed temperature 1 | BED TEMPERATURE 1 |  |  | BED TEMPERATURE 1 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS217 | MEAS_BIN | Steam accumulator by-passvalve open limit switch | STEAM ACCUMULATOR BY-PASS | VALVE OPEN LIMIT SWITCH |  | STEAM ACCUMULATOR BY-PASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS217 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TT414 |  | BB1TT414 | <IO NOT ASSIGNED> | Bed temperature 2 | BED TEMPERATURE 2 |  |  | BED TEMPERATURE 2 | TT | TEMPERATURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS218 | MEAS_BIN | Steam accumulator by-passvalve close limit switch | STEAM ACCUMULATOR BY-PASS | VALVE CLOSE LIMIT SWITCH |  | STEAM ACCUMULATOR BY-PASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS218 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT405 |  | BB1PT405 | <IO NOT ASSIGNED> | Boiler upper part pressure 2 | BOILER UPPER PART | PRESSURE 2 |  | BOILER UPPER PART PRESSURE 2 | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS220 | MEAS_BIN | Steam accumulator ON-OFF valve close limit switch | STEAM ACCUMULATOR ON-OFF | VALVE CLOSE LIMIT SWITCH |  | STEAM ACCUMULATOR ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS220 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT550 |  | BB1QT550 | <IO NOT ASSIGNED> | Fluegas oxygen measurement 1 | FLUEGAS OXYGEN | MEASUREMENT 1 |  | FLUEGAS OXYGEN MEASUREMENT 1 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS219 | MEAS_BIN | Steam accumulator ON-OFF valve open limit switch | STEAM ACCUMULATOR ON-OFF | VALVE OPEN LIMIT SWITCH |  | STEAM ACCUMULATOR ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS219 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1FT550 |  | BB1FT550 | <IO NOT ASSIGNED> | Recirculation gas flow | RECIRCULATION GAS FLOW |  |  | RECIRCULATION GAS FLOW | FT | FLOW TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS215 | MEAS_BIN | Primary air preheater on-off valve open limit switch | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS215 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1QT551 |  | BB1QT551 | <IO NOT ASSIGNED> | Fluegas oxygen measurement 2 | FLUEGAS OXYGEN | MEASUREMENT 2 |  | FLUEGAS OXYGEN MEASUREMENT 2 | QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS216 | MEAS_BIN | Primary air preheater on-off valve close limit switch | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS216 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT406 |  | BB1PT406 | <IO NOT ASSIGNED> | Boiler upper part pressure | BOILER UPPER PART | PRESSURE |  | BOILER UPPER PART PRESSURE | PT | PRESSURE TRANSMITTER |  | MEAS_ANA_SRS |  | BB1GS621 | MEAS_BIN | Unloading station 3, block 3, feeder 3, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 3, OUT | GS | GATE SWITCH | BB1GS621 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS700 |  | BB1LS700 | <IO NOT ASSIGNED> | Chemical tank 1 level switch | CHEMICAL TANK 1 | LEVEL SWITCH |  | CHEMICAL TANK 1 LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS611 | MEAS_BIN | Unloading station 2, block 2, feeder 2, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 2, OUT | GS | GATE SWITCH | BB1GS611 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS701 |  | BB1LS701 | <IO NOT ASSIGNED> | Chemical tank 2 level switch | CHEMICAL TANK 2 | LEVEL SWITCH |  | CHEMICAL TANK 2 LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS606 | MEAS_BIN | Unloading station 1, block 1, feeder 4, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 4, IN | GS | GATE SWITCH | BB1GS606 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS004 |  | BB1GS004 | <IO NOT ASSIGNED> | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS614 | MEAS_BIN | Unloading station 2, block 2, feeder 4, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 4, IN | GS | GATE SWITCH | BB1GS614 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS003 |  | BB1GS003 | <IO NOT ASSIGNED> | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS619 | MEAS_BIN | Unloading station 3, block 3, feeder 2, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 2, OUT | GS | GATE SWITCH | BB1GS619 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS001 |  | BB1GS001 | <IO NOT ASSIGNED> | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS651 | MEAS_BIN | Disc screen by-pass damper limit switch to screen | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH TO SCREEN | GS | GATE SWITCH | BB1GS651 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS002 |  | BB1GS002 | <IO NOT ASSIGNED> | Feed water pump suction side shut-off valve limit switch | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS602 | MEAS_BIN | Hydraulics unit 1, block 3, pressure switch | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 3, PRESSURE SWITCH | PS | PRESSURE SWITCH | BB1PS602 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS005 |  | BB1GS005 | <IO NOT ASSIGNED> | FW tank overflow On-Off valve position | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS615 | MEAS_BIN | Unloading station 2, block 2, feeder 4, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 4, OUT | GS | GATE SWITCH | BB1GS615 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS006 |  | BB1GS006 | <IO NOT ASSIGNED> | FW tank overflow On-Off valve position | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | FW TANK OVERFLOW ON-OFF VALVE POSITION | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS623 | MEAS_BIN | Unloading station 3, block 3, feeder 4, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 4, OUT | GS | GATE SWITCH | BB1GS623 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS007 |  | BB1GS007 | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve limit switch open | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST651 | MEAS_BIN | Scraper conveyor 2, rotation guard | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | SCRAPER CONVEYOR 2, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST651 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS008 |  | BB1GS008 | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve limit switch close | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS603 | MEAS_BIN | Unloading station 1, block 1, feeder 2, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 2, OUT | GS | GATE SWITCH | BB1GS603 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS009 |  | BB1GS009 | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve limit switch open | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS601 | MEAS_BIN | Hydraulics unit 1, block 2, pressure switch | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 2, PRESSURE SWITCH | PS | PRESSURE SWITCH | BB1PS601 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS010 |  | BB1GS010 | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve limit switch close | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS650 | MEAS_BIN | Disc screen by-pass damper limit switch by-pass pos. | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH BY-PASS POS. | GS | GATE SWITCH | BB1GS650 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS011 |  | BB1GS011 | <IO NOT ASSIGNED> | Boiler bottom blow down on-off valve limit switch open | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH OPEN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS622 | MEAS_BIN | Unloading station 3, block 3, feeder 4, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 4, IN | GS | GATE SWITCH | BB1GS622 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS012 |  | BB1GS012 | <IO NOT ASSIGNED> | Boiler bottom blow down on-off valve limit switch close | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH CLOSE | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS602 | MEAS_BIN | Unloading station 1, block 1, feeder 2, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 2, IN | GS | GATE SWITCH | BB1GS602 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS221 |  | BB1GS221 | <IO NOT ASSIGNED> | Main steam valve by-pass open limit switch | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | MAIN STEAM VALVE BY-PASS OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS655 | MEAS_BIN | Scraper conveyor 2, turning point blockage guard | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | SCRAPER CONVEYOR 2, TURNING POINT BLOCKAGE GU ARD | LS | LEVEL SWITCH | BB1LS655 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS222 |  | BB1GS222 | <IO NOT ASSIGNED> | Main steam valve by-pass close limit switch | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | MAIN STEAM VALVE BY-PASS CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS607 | MEAS_BIN | Unloading station 1, block 1, feeder 4, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 4, OUT | GS | GATE SWITCH | BB1GS607 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS223 |  | BB1GS223 | <IO NOT ASSIGNED> | Main steam line valve open limit switch | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | MAIN STEAM LINE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS605 | MEAS_BIN | Unloading station 1, block 1, feeder 3, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 3, OUT | GS | GATE SWITCH | BB1GS605 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS224 |  | BB1GS224 | <IO NOT ASSIGNED> | Main steam line valve close limit switch | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | MAIN STEAM LINE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS652 | MEAS_BIN | Unloading station 2, block 2, blockage guard | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | UNLOADING STATION 2, BLOCK 2, BLOCKAGE GUARD | LS | LEVEL SWITCH | BB1LS652 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS225 |  | BB1GS225 | <IO NOT ASSIGNED> | Start-up line ON-OFF valve open limit switch | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | START-UP LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS601 | MEAS_BIN | Unloading station 1, block 1, feeder 1, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 1, OUT | GS | GATE SWITCH | BB1GS601 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS226 |  | BB1GS226 | <IO NOT ASSIGNED> | Start-up line ON-OFF valve close limit switch | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | START-UP LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS608 | MEAS_BIN | Hydraulics unit 1, low oil level alarm | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | HYDRAULICS UNIT 1, LOW OIL LEVEL ALARM | LS | LEVEL SWITCH | BB1LS608 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS200 |  | BB1GS200 | <IO NOT ASSIGNED> | Sootblower 1 IN limit switch | SOOTBLOWER 1 IN | LIMIT SWITCH |  | SOOTBLOWER 1 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS656 | MEAS_BIN | Scraper conveyor 2, fuel silo side blockage guard | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | SCRAPER CONVEYOR 2, FUEL SILO SIDE BLOCKAGE GUARD | LS | LEVEL SWITCH | BB1LS656 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS201 |  | BB1GS201 | <IO NOT ASSIGNED> | Sootblower 1 OUT limit switch | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | SOOTBLOWER 1 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS600 | MEAS_BIN | Hydraulics unit 1, leaking pool limit switch | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | HYDRAULICS UNIT 1, LEAKING POOL LIMIT SWITCH | LS | LEVEL SWITCH | BB1LS600 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS203 |  | BB1GS203 | <IO NOT ASSIGNED> | Sootblower 2 OUT limit switch | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | SOOTBLOWER 2 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS609 | MEAS_BIN | Unloading station 2, block 2, feeder 1, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 1, OUT | GS | GATE SWITCH | BB1GS609 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS204 |  | BB1GS204 | <IO NOT ASSIGNED> | Sootblower 2 IN limit switch | SOOTBLOWER 2 IN | LIMIT SWITCH |  | SOOTBLOWER 2 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS650 | MEAS_BIN | Scraper conveyor 1 bed height level switch | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | SCRAPER CONVEYOR 1 BED HEIGHT LEVEL SWITCH | LS | LEVEL SWITCH | BB1LS650 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS205 |  | BB1GS205 | <IO NOT ASSIGNED> | Sootblower 3 OUT limit switch | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | SOOTBLOWER 3 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS617 | MEAS_BIN | Unloading station 3, block 3, feeder 1, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 1, OUT | GS | GATE SWITCH | BB1GS617 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS206 |  | BB1GS206 | <IO NOT ASSIGNED> | Sootblower 3 IN limit switch | SOOTBLOWER 3 IN | LIMIT SWITCH |  | SOOTBLOWER 3 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS651 | MEAS_BIN | Unloading station 3, block 3, blockage guard | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | UNLOADING STATION 3, BLOCK 3, BLOCKAGE GUARD | LS | LEVEL SWITCH | BB1LS651 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS207 |  | BB1GS207 | <IO NOT ASSIGNED> | Sootblower 5 OUT limit switch | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | SOOTBLOWER 5 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS612 | MEAS_BIN | Unloading station 2, block 2, feeder 3, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 3, IN | GS | GATE SWITCH | BB1GS612 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS208 |  | BB1GS208 | <IO NOT ASSIGNED> | Sootblower 5 IN limit switch | SOOTBLOWER 5 IN | LIMIT SWITCH |  | SOOTBLOWER 5 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS654 | MEAS_BIN | Scraper conveyor 1, blockage guard | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | SCRAPER CONVEYOR 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | BB1LS654 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS209 |  | BB1GS209 | <IO NOT ASSIGNED> | Sootblower 6 OUT limit switch | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | SOOTBLOWER 6 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS613 | MEAS_BIN | Unloading station 2, block 2, feeder 3, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 3, OUT | GS | GATE SWITCH | BB1GS613 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS210 |  | BB1GS210 | <IO NOT ASSIGNED> | Sootblower 6 IN limit switch | SOOTBLOWER 6 IN | LIMIT SWITCH |  | SOOTBLOWER 6 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS620 | MEAS_BIN | Unloading station 3, block 3, feeder 3, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 3, IN | GS | GATE SWITCH | BB1GS620 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS211 |  | BB1GS211 | <IO NOT ASSIGNED> | Sootblower 7 OUT limit switch | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | SOOTBLOWER 7 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS618 | MEAS_BIN | Unloading station 3, block 3, feeder 2, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 2, IN | GS | GATE SWITCH | BB1GS618 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS212 |  | BB1GS212 | <IO NOT ASSIGNED> | Sootblower 7 IN limit switch | SOOTBLOWER 7 IN | LIMIT SWITCH |  | SOOTBLOWER 7 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS600 | MEAS_BIN | Hydraulics unit 1, block 1, pressure switch | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 1, PRESSURE SWITCH | PS | PRESSURE SWITCH | BB1PS600 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS213 |  | BB1GS213 | <IO NOT ASSIGNED> | Sootblower 8 OUT limit switch | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | SOOTBLOWER 8 OUT LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS608 | MEAS_BIN | Unloading station 2, block 2, feeder 1, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 1, IN | GS | GATE SWITCH | BB1GS608 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS214 |  | BB1GS214 | <IO NOT ASSIGNED> | Sootblower 8 IN limit switch | SOOTBLOWER 8 IN | LIMIT SWITCH |  | SOOTBLOWER 8 IN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS604 | MEAS_BIN | Unloading station 1, block 1, feeder 3, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 3, IN | GS | GATE SWITCH | BB1GS604 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS227 |  | BB1GS227 | <IO NOT ASSIGNED> | Sootblowing line on-off valve open limit switch | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | SOOTBLOWING LINE ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS653 | MEAS_BIN | Unloading station 1, block 1, blockage guard | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | UNLOADING STATION 1, BLOCK 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | BB1LS653 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS228 |  | BB1GS228 | <IO NOT ASSIGNED> | Sootblowing line on-off valve close limit switch | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | SOOTBLOWING LINE ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS616 | MEAS_BIN | Unloading station 3, block 3, feeder 1, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 1, IN | GS | GATE SWITCH | BB1GS616 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS231 |  | BB1GS231 | <IO NOT ASSIGNED> | Steam accumulator pressure control valve open limit switch | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS600 | MEAS_BIN | Unloading station 1, block 1, feeder 1, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 1, IN | GS | GATE SWITCH | BB1GS600 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS230 |  | BB1GS230 | <IO NOT ASSIGNED> | Steam accumulator pressure control valve close limit switch | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST650 | MEAS_BIN | Scraper conveyor 1, rotation guard | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | SCRAPER CONVEYOR 1, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST650 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS233 |  | BB1GS233 | <IO NOT ASSIGNED> | Steam pressure reduction valve open limit switch | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | STEAM PRESSURE REDUCTION VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS610 | MEAS_BIN | Unloading station 2, block 2, feeder 2, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 2, IN | GS | GATE SWITCH | BB1GS610 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS232 |  | BB1GS232 | <IO NOT ASSIGNED> | Steam pressure reduction valve close limit switch | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | STEAM PRESSURE REDUCTION VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST675 | MEAS_BIN | Leveling roller 3 speed switch | LEVELING ROLLER 3 | SPEED SWITCH |  | LEVELING ROLLER 3 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | BB1ST675 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS217 |  | BB1GS217 | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-offvalve open limit switch | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS608 | MEAS_BIN | High temperature switch hydraulic oil | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | HIGH TEMPERATURE SWITCH HYDRAULIC OIL | TS | TEMPERATURE SWITCH | BB1TS608 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS218 |  | BB1GS218 | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-offvalve close limit switch | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST673 | MEAS_BIN | Leveling roller 1 speed switch | LEVELING ROLLER 1 | SPEED SWITCH |  | LEVELING ROLLER 1 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | BB1ST673 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS219 |  | BB1GS219 | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve open limit switch | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS600 | MEAS_BIN | Hydraulics unit, thermostat for heater | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | HYDRAULICS UNIT, THERMOSTAT FOR HEATER | TS | TEMPERATURE SWITCH | BB1TS600 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS220 |  | BB1GS220 | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve close limit switch | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST674 | MEAS_BIN | Leveling roller 2 speed switch | LEVELING ROLLER 2 | SPEED SWITCH |  | LEVELING ROLLER 2 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | BB1ST674 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS217 |  | BB1GS217 | <IO NOT ASSIGNED> | Steam accumulator by-passvalve open limit switch | STEAM ACCUMULATOR BY-PASS | VALVE OPEN LIMIT SWITCH |  | STEAM ACCUMULATOR BY-PASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS605 | MEAS_BIN | Hydraulic oil return block 3 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 3 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | BB1PS605 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS218 |  | BB1GS218 | <IO NOT ASSIGNED> | Steam accumulator by-passvalve close limit switch | STEAM ACCUMULATOR BY-PASS | VALVE CLOSE LIMIT SWITCH |  | STEAM ACCUMULATOR BY-PASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS603 | MEAS_BIN | Hydraulic oil return block 1 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 1 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | BB1PS603 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS220 |  | BB1GS220 | <IO NOT ASSIGNED> | Steam accumulator ON-OFF valve close limit switch | STEAM ACCUMULATOR ON-OFF | VALVE CLOSE LIMIT SWITCH |  | STEAM ACCUMULATOR ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PS604 | MEAS_BIN | Hydraulic oil return block 2 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 2 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | BB1PS604 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS219 |  | BB1GS219 | <IO NOT ASSIGNED> | Steam accumulator ON-OFF valve open limit switch | STEAM ACCUMULATOR ON-OFF | VALVE OPEN LIMIT SWITCH |  | STEAM ACCUMULATOR ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST654 | MEAS_BIN | Belt magnet rotation guard | BELT MAGNET | ROTATION GUARD |  | BELT MAGNET ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST654 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS215 |  | BB1GS215 | <IO NOT ASSIGNED> | Primary air preheater on-off valve open limit switch | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS661 | MEAS_BIN | Belt magnet deviation detector 1 | BELT MAGNET | DEVIATION DETECTOR 1 |  | BELT MAGNET DEVIATION DETECTOR 1 | GS | GATE SWITCH | BB1GS661 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS216 |  | BB1GS216 | <IO NOT ASSIGNED> | Primary air preheater on-off valve close limit switch | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS662 | MEAS_BIN | Belt magnet deviation detector 2 | BELT MAGNET | DEVIATION DETECTOR 2 |  | BELT MAGNET DEVIATION DETECTOR 2 | GS | GATE SWITCH | BB1GS662 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS621 |  | BB1GS621 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 3, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST652 | MEAS_BIN | Belt conveyor rotation guard | BELT CONVEYOR | ROTATION GUARD |  | BELT CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST652 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS611 |  | BB1GS611 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 2, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS659 | MEAS_BIN | Belt conveyor deviation detector 1 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | BELT CONVEYOR DEVIATION DETECTOR 1 | GS | GATE SWITCH | BB1GS659 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS606 |  | BB1GS606 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 4, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS660 | MEAS_BIN | Belt conveyor deviation detector 2 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | BELT CONVEYOR DEVIATION DETECTOR 2 | GS | GATE SWITCH | BB1GS660 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS614 |  | BB1GS614 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 4, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS663 | MEAS_BIN | Belt conveyor oversize detector | BELT CONVEYOR | OVERSIZE DETECTOR |  | BELT CONVEYOR OVERSIZE DETECTOR | GS | GATE SWITCH | BB1GS663 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS619 |  | BB1GS619 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 2, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST656 | MEAS_BIN | Disc screen drive 1 rotation guard | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | DISC SCREEN DRIVE 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST656 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS651 |  | BB1GS651 | <IO NOT ASSIGNED> | Disc screen by-pass damper limit switch to screen | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH TO SCREEN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST657 | MEAS_BIN | Disc screen drive 2 rotation guard | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | DISC SCREEN DRIVE 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST657 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PS602 |  | BB1PS602 | <IO NOT ASSIGNED> | Hydraulics unit 1, block 3, pressure switch | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 3, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1GS652 | MEAS_BIN | Explosion hatch limit switch 1 | EXPLOSION HATCH | LIMIT SWITCH 1 |  | EXPLOSION HATCH LIMIT SWITCH 1 | GS | GATE SWITCH | BB1GS652 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS615 |  | BB1GS615 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 4, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS653 | MEAS_BIN | Explosion hatch limit switch 2 | EXPLOSION HATCH | LIMIT SWITCH 2 |  | EXPLOSION HATCH LIMIT SWITCH 2 | GS | GATE SWITCH | BB1GS653 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS623 |  | BB1GS623 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 4, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS654 | MEAS_BIN | Explosion hatch limit switch 3 | EXPLOSION HATCH | LIMIT SWITCH 3 |  | EXPLOSION HATCH LIMIT SWITCH 3 | GS | GATE SWITCH | BB1GS654 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST651 |  | BB1ST651 | <IO NOT ASSIGNED> | Scraper conveyor 2, rotation guard | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | SCRAPER CONVEYOR 2, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS655 | MEAS_BIN | Explosion hatch limit switch 4 | EXPLOSION HATCH | LIMIT SWITCH 4 |  | EXPLOSION HATCH LIMIT SWITCH 4 | GS | GATE SWITCH | BB1GS655 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS603 |  | BB1GS603 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 2, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 2, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS657 | MEAS_BIN | Fuel silo discharge screw blockage switch | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | FUEL SILO DISCHARGE SCREW BLOCKAGE SWITCH | LS | LEVEL SWITCH | BB1LS657 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PS601 |  | BB1PS601 | <IO NOT ASSIGNED> | Hydraulics unit 1, block 2, pressure switch | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 2, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1LS658 | MEAS_BIN | Fuel silo cross conveyor blockage switch | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | FUEL SILO CROSS CONVEYOR BLOCKAGE SWITCH | LS | LEVEL SWITCH | BB1LS658 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS650 |  | BB1GS650 | <IO NOT ASSIGNED> | Disc screen by-pass damper limit switch by-pass pos. | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH BY-PASS POS. | GS | GATE SWITCH | DI | MEAS_BIN |  | <004> | #N/A | Fuel silo cross conveyor explosion hatch limit switch | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | FUEL SILO CROSS CONVEYOR EXPLOSION HATCH LIMIT SWITCH | 4> | #N/A | <004> | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
BB1GS622 |  | BB1GS622 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 4, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 4, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS659 | MEAS_BIN | Fuel feeding screw 1 blockage switch | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | FUEL FEEDING SCREW 1 BLOCKAGE SWITCH | LS | LEVEL SWITCH | BB1LS659 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS602 |  | BB1GS602 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 2, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS660 | MEAS_BIN | Fuel feeding screw 2 blockage switch | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | FUEL FEEDING SCREW 2 BLOCKAGE SWITCH | LS | LEVEL SWITCH | BB1LS660 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS655 |  | BB1LS655 | <IO NOT ASSIGNED> | Scraper conveyor 2, turning point blockage guard | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | SCRAPER CONVEYOR 2, TURNING POINT BLOCKAGE GU ARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1ST649 | MEAS_BIN | Fuel silo cross conveyor rotation guard | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | FUEL SILO CROSS CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST649 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS607 |  | BB1GS607 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 4, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 4, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST652 | MEAS_BIN | Rotating fuel spreader rotation guard | ROTATING FUEL SPREADER | ROTATION GUARD |  | ROTATING FUEL SPREADER ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST652 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS605 |  | BB1GS605 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 3, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST653 | MEAS_BIN | Fuel feeding screw 2 rotation guard | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | FUEL FEEDING SCREW 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST653 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS652 |  | BB1LS652 | <IO NOT ASSIGNED> | Unloading station 2, block 2, blockage guard | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | UNLOADING STATION 2, BLOCK 2, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1ST654 | MEAS_BIN | Fuel feeding rotary feeder 1 rotation guard | FUEL FEEDING ROTARY | FEEDER 1 ROTATION GUARD |  | FUEL FEEDING ROTARY FEEDER 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST654 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS601 |  | BB1GS601 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 1, out | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | UNLOADING STATION 1, BLOCK 1, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST655 | MEAS_BIN | Fuel feeding rotary feeder 2 rotation guard | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | FUEL FEEDING ROTARY FEEDER 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST655 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS608 |  | BB1LS608 | <IO NOT ASSIGNED> | Hydraulics unit 1, low oil level alarm | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | HYDRAULICS UNIT 1, LOW OIL LEVEL ALARM | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1ST659 | MEAS_BIN | Fuel feeding screw 1 rotation guard | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | FUEL FEEDING SCREW 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST659 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS656 |  | BB1LS656 | <IO NOT ASSIGNED> | Scraper conveyor 2, fuel silo side blockage guard | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | SCRAPER CONVEYOR 2, FUEL SILO SIDE BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS655 | MEAS_BIN | Slide gate valve open limit switch | SLIDE GATE VALVE OPEN | LIMIT SWITCH |  | SLIDE GATE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS655 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS600 |  | BB1LS600 | <IO NOT ASSIGNED> | Hydraulics unit 1, leaking pool limit switch | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | HYDRAULICS UNIT 1, LEAKING POOL LIMIT SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS656 | MEAS_BIN | Slide gate valve close limit switch | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | SLIDE GATE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS656 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS609 |  | BB1GS609 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 1, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS661 | MEAS_BIN | Lubrication alarm screw discharger | LUBRICATION ALARM | SCREW DISCHARGER |  | LUBRICATION ALARM SCREW DISCHARGER | LS | LEVEL SWITCH | BB1LS661 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS650 |  | BB1LS650 | <IO NOT ASSIGNED> | Scraper conveyor 1 bed height level switch | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | SCRAPER CONVEYOR 1 BED HEIGHT LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS802 | MEAS_BIN | Bottom ash valve limit switch | BOTTOM ASH VALVE | LIMIT SWITCH |  | BOTTOM ASH VALVE LIMIT SWITCH | GS | GATE SWITCH | BB1GS802 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS617 |  | BB1GS617 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 1, out | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | UNLOADING STATION 3, BLOCK 3, FEEDER 1, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS803 | MEAS_BIN | Bottom ash dropping chuteclosing device limit switch | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | BB1GS803 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS651 |  | BB1LS651 | <IO NOT ASSIGNED> | Unloading station 3, block 3, blockage guard | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | UNLOADING STATION 3, BLOCK 3, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1LS852 | MEAS_BIN | Fly ash container level switch | FLY ASH CONTAINER | LEVEL SWITCH |  | FLY ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | BB1LS852 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS612 |  | BB1GS612 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 3, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST805 | MEAS_BIN | Heated ESP collection screw rotation guard | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  | HEATED ESP COLLECTION SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST805 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS654 |  | BB1LS654 | <IO NOT ASSIGNED> | Scraper conveyor 1, blockage guard | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | SCRAPER CONVEYOR 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1ST808 | MEAS_BIN | ESP hopper 2 screw rotation guard | ESP HOPPER 2 SCREW | ROTATION GUARD |  | ESP HOPPER 2 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST808 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS613 |  | BB1GS613 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 3, out | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | UNLOADING STATION 2, BLOCK 2, FEEDER 3, OUT | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST809 | MEAS_BIN | ESP hopper 1 screw rotation guard | ESP HOPPER 1 SCREW | ROTATION GUARD |  | ESP HOPPER 1 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST809 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS620 |  | BB1GS620 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 3, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST804 | MEAS_BIN | ESP Rotary valve rotation guard | ESP ROTARY VALVE | ROTATION GUARD |  | ESP ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST804 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS618 |  | BB1GS618 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 2, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS808 | MEAS_BIN | ESP Ash hopper 2 overheat thermostat | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  | ESP ASH HOPPER 2 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | BB1TS808 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PS600 |  | BB1PS600 | <IO NOT ASSIGNED> | Hydraulics unit 1, block 1, pressure switch | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | HYDRAULICS UNIT 1, BLOCK 1, PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1TS809 | MEAS_BIN | ESP Ash hopper 1 overheat thermostat | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  | ESP ASH HOPPER 1 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | BB1TS809 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS608 |  | BB1GS608 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 1, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS805 | MEAS_BIN | ESP collection screw heating thermostat | ESP COLLECTION SCREW | HEATING THERMOSTAT |  | ESP COLLECTION SCREW HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | BB1TS805 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS604 |  | BB1GS604 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 3, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 3, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1TS804 | MEAS_BIN | ESP Rotary valve heating thermostat | ESP ROTARY VALVE | HEATING THERMOSTAT |  | ESP ROTARY VALVE HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | BB1TS804 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS653 |  | BB1LS653 | <IO NOT ASSIGNED> | Unloading station 1, block 1, blockage guard | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | UNLOADING STATION 1, BLOCK 1, BLOCKAGE GUARD | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1GS855 | MEAS_BIN | Bottom ash valve solenoid valve open limit switch | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS855 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS616 |  | BB1GS616 | <IO NOT ASSIGNED> | Unloading station 3, block 3, feeder 1, in | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | UNLOADING STATION 3, BLOCK 3, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS856 | MEAS_BIN | Bottom ash valve solenoid valve close limit switch | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS856 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS600 |  | BB1GS600 | <IO NOT ASSIGNED> | Unloading station 1, block 1, feeder 1, in | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | UNLOADING STATION 1, BLOCK 1, FEEDER 1, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS857 | MEAS_BIN | Bottom ash valve solenoid valve open limit switch | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS857 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST650 |  | BB1ST650 | <IO NOT ASSIGNED> | Scraper conveyor 1, rotation guard | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | SCRAPER CONVEYOR 1, ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS858 | MEAS_BIN | Bottom ash valve solenoid valve close limit switch | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS858 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS610 |  | BB1GS610 | <IO NOT ASSIGNED> | Unloading station 2, block 2, feeder 2, in | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | UNLOADING STATION 2, BLOCK 2, FEEDER 2, IN | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS850 | MEAS_BIN | Bottom ash sieve bypass valve close limit switch | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH SIEVE BYPASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS850 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST675 |  | BB1ST675 | <IO NOT ASSIGNED> | Leveling roller 3 speed switch | LEVELING ROLLER 3 | SPEED SWITCH |  | LEVELING ROLLER 3 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS851 | MEAS_BIN | Bottom ash sieve bypass valve open limit switch | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH SIEVE BYPASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS851 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TS608 |  | BB1TS608 | <IO NOT ASSIGNED> | High temperature switch hydraulic oil | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | HIGH TEMPERATURE SWITCH HYDRAULIC OIL | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1FS003 | MEAS_BIN | Bottom ash cooling flow switch | BOTTOM ASH COOLING | FLOW SWITCH |  | BOTTOM ASH COOLING FLOW SWITCH | FS | FLOW SWITCH | BB1FS003 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST673 |  | BB1ST673 | <IO NOT ASSIGNED> | Leveling roller 1 speed switch | LEVELING ROLLER 1 | SPEED SWITCH |  | LEVELING ROLLER 1 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS801 | MEAS_BIN | Sand filling valve position open limit switch | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | SAND FILLING VALVE POSITION OPEN LIMIT SWITCH | GS | GATE SWITCH | BB1GS801 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TS600 |  | BB1TS600 | <IO NOT ASSIGNED> | Hydraulics unit, thermostat for heater | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | HYDRAULICS UNIT, THERMOSTAT FOR HEATER | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1GS800 | MEAS_BIN | Sand filling valve position close limit switch | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | SAND FILLING VALVE POSITION CLOSE LIMIT SWITCH | GS | GATE SWITCH | BB1GS800 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST674 |  | BB1ST674 | <IO NOT ASSIGNED> | Leveling roller 2 speed switch | LEVELING ROLLER 2 | SPEED SWITCH |  | LEVELING ROLLER 2 SPEED SWITCH | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS854 | MEAS_BIN | Bottom ash dropping chute limit switch | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | BOTTOM ASH DROPPING CHUTE LIMIT SWITCH | GS | GATE SWITCH | BB1GS854 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PS605 |  | BB1PS605 | <IO NOT ASSIGNED> | Hydraulic oil return block 3 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 3 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1GS853 | MEAS_BIN | Bottom ash dropping chute closing device limit switch | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | BB1GS853 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PS603 |  | BB1PS603 | <IO NOT ASSIGNED> | Hydraulic oil return block 1 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 1 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1GS859 | MEAS_BIN | Bottom ash to container in place | BOTTOM ASH TO CONTAINER | IN PLACE |  | BOTTOM ASH TO CONTAINER IN PLACE | GS | GATE SWITCH | BB1GS859 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PS604 |  | BB1PS604 | <IO NOT ASSIGNED> | Hydraulic oil return block 2 filter pressure switch | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | HYDRAULIC OIL RETURN BLOCK 2 FILTER PRESSURE SWITCH | PS | PRESSURE SWITCH | DI | MEAS_BIN |  | BB1LS850 | MEAS_BIN | Bottom ash container level switch | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | BB1LS850 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST654 |  | BB1ST654 | <IO NOT ASSIGNED> | Belt magnet rotation guard | BELT MAGNET | ROTATION GUARD |  | BELT MAGNET ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1LS851 | MEAS_BIN | Bottom ash container level switch | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | BB1LS851 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS661 |  | BB1GS661 | <IO NOT ASSIGNED> | Belt magnet deviation detector 1 | BELT MAGNET | DEVIATION DETECTOR 1 |  | BELT MAGNET DEVIATION DETECTOR 1 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1PT800 | MEAS_BIN | Recycled bed material damper pressure switch | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  | RECYCLED BED MATERIAL DAMPER PRESSURE SWITCH | PT | PRESSURE TRANSMITTER | BB1PT800 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS662 |  | BB1GS662 | <IO NOT ASSIGNED> | Belt magnet deviation detector 2 | BELT MAGNET | DEVIATION DETECTOR 2 |  | BELT MAGNET DEVIATION DETECTOR 2 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST856 | MEAS_BIN | Purified sand screw conveyor rotation guard | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | PURIFIED SAND SCREW CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST856 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST652 |  | BB1ST652 | <IO NOT ASSIGNED> | Belt conveyor rotation guard | BELT CONVEYOR | ROTATION GUARD |  | BELT CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1ST850 | MEAS_BIN | Bottom ash conveyor rotation guard | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | BOTTOM ASH CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST850 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS659 |  | BB1GS659 | <IO NOT ASSIGNED> | Belt conveyor deviation detector 1 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | BELT CONVEYOR DEVIATION DETECTOR 1 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1GS852 | MEAS_BIN | Bottom ash conveyor blockage detector | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | BOTTOM ASH CONVEYOR BLOCKAGE DETECTOR | GS | GATE SWITCH | BB1GS852 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS660 |  | BB1GS660 | <IO NOT ASSIGNED> | Belt conveyor deviation detector 2 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | BELT CONVEYOR DEVIATION DETECTOR 2 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST852 | MEAS_BIN | 2nd pass fly ash rotary valve rotation guard | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 2ND PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST852 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS663 |  | BB1GS663 | <IO NOT ASSIGNED> | Belt conveyor oversize detector | BELT CONVEYOR | OVERSIZE DETECTOR |  | BELT CONVEYOR OVERSIZE DETECTOR | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1ST853 | MEAS_BIN | 3rd pass fly ash rotary valve rotation guard | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 3RD PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | BB1ST853 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST656 |  | BB1ST656 | <IO NOT ASSIGNED> | Disc screen drive 1 rotation guard | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | DISC SCREEN DRIVE 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1GS020 | MEAS_BIN | Emergency shower use switch | EMERGENCY SHOWER | USE SWITCH |  | EMERGENCY SHOWER USE SWITCH | GS | GATE SWITCH | BB1GS020 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST657 |  | BB1ST657 | <IO NOT ASSIGNED> | Disc screen drive 2 rotation guard | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | DISC SCREEN DRIVE 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1LS103 | MEAS_BIN_SRS | Steam drum level switch 1 | STEAM DRUM LEVEL SWITCH 1 |  |  | STEAM DRUM LEVEL SWITCH 1 | LS | LEVEL SWITCH | BB1LS103 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS652 |  | BB1GS652 | <IO NOT ASSIGNED> | Explosion hatch limit switch 1 | EXPLOSION HATCH | LIMIT SWITCH 1 |  | EXPLOSION HATCH LIMIT SWITCH 1 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1LS104 | MEAS_BIN_SRS | Steam drum level switch 2 | STEAM DRUM LEVEL SWITCH 2 |  |  | STEAM DRUM LEVEL SWITCH 2 | LS | LEVEL SWITCH | BB1LS104 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS653 |  | BB1GS653 | <IO NOT ASSIGNED> | Explosion hatch limit switch 2 | EXPLOSION HATCH | LIMIT SWITCH 2 |  | EXPLOSION HATCH LIMIT SWITCH 2 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS101 | MEAS_BIN_SRS | Boiler emergency shutdown switch 1 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  | BOILER EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP | BB1HS101 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS654 |  | BB1GS654 | <IO NOT ASSIGNED> | Explosion hatch limit switch 3 | EXPLOSION HATCH | LIMIT SWITCH 3 |  | EXPLOSION HATCH LIMIT SWITCH 3 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS103 | MEAS_BIN_SRS | Boiler emergency shutdown switch 3 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  | BOILER EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP | BB1HS103 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS655 |  | BB1GS655 | <IO NOT ASSIGNED> | Explosion hatch limit switch 4 | EXPLOSION HATCH | LIMIT SWITCH 4 |  | EXPLOSION HATCH LIMIT SWITCH 4 | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS104 | MEAS_BIN_SRS | Boiler emergency shutdown switch 4 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  | BOILER EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP | BB1HS104 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS657 |  | BB1LS657 | <IO NOT ASSIGNED> | Fuel silo discharge screw blockage switch | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | FUEL SILO DISCHARGE SCREW BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1HS102 | MEAS_BIN_SRS | Boiler emergency shutdown switch 2 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  | BOILER EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP | BB1HS102 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS658 |  | BB1LS658 | <IO NOT ASSIGNED> | Fuel silo cross conveyor blockage switch | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | FUEL SILO CROSS CONVEYOR BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1HS105 | MEAS_BIN_SRS | Boiler emergency shutdown switch 5 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  | BOILER EMERGENCY SHUTDOWN SWITCH 5 | HS | EMERGENCY STOP | BB1HS105 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
<004> |  | <004> | <IO NOT ASSIGNED> | Fuel silo cross conveyor explosion hatch limit switch | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | FUEL SILO CROSS CONVEYOR EXPLOSION HATCH LIMIT SWITCH | 4> | #N/A | DI | #N/A |  | BB1HS106 | MEAS_BIN_SRS | Boiler emergency shutdown switch 6 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  | BOILER EMERGENCY SHUTDOWN SWITCH 6 | HS | EMERGENCY STOP | BB1HS106 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS659 |  | BB1LS659 | <IO NOT ASSIGNED> | Fuel feeding screw 1 blockage switch | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | FUEL FEEDING SCREW 1 BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1HS107 | MEAS_BIN_SRS | Boiler emergency shutdown switch 7 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  | BOILER EMERGENCY SHUTDOWN SWITCH 7 | HS | EMERGENCY STOP | BB1HS107 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS660 |  | BB1LS660 | <IO NOT ASSIGNED> | Fuel feeding screw 2 blockage switch | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | FUEL FEEDING SCREW 2 BLOCKAGE SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1HS108 | MEAS_BIN_SRS | Boiler emergency shutdown switch 8 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  | BOILER EMERGENCY SHUTDOWN SWITCH 8 | HS | EMERGENCY STOP | BB1HS108 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST649 |  | BB1ST649 | <IO NOT ASSIGNED> | Fuel silo cross conveyor rotation guard | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | FUEL SILO CROSS CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS109 | MEAS_BIN_SRS | Boiler emergency shutdown switch 9 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  | BOILER EMERGENCY SHUTDOWN SWITCH 9 | HS | EMERGENCY STOP | BB1HS109 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST652 |  | BB1ST652 | <IO NOT ASSIGNED> | Rotating fuel spreader rotation guard | ROTATING FUEL SPREADER | ROTATION GUARD |  | ROTATING FUEL SPREADER ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS110 | MEAS_BIN_SRS | Boiler emergency shutdown switch 10 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  | BOILER EMERGENCY SHUTDOWN SWITCH 10 | HS | EMERGENCY STOP | BB1HS110 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST653 |  | BB1ST653 | <IO NOT ASSIGNED> | Fuel feeding screw 2 rotation guard | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | FUEL FEEDING SCREW 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS111 | MEAS_BIN_SRS | Boiler emergency shutdown switch 11 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  | BOILER EMERGENCY SHUTDOWN SWITCH 11 | HS | EMERGENCY STOP | BB1HS111 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST654 |  | BB1ST654 | <IO NOT ASSIGNED> | Fuel feeding rotary feeder 1 rotation guard | FUEL FEEDING ROTARY | FEEDER 1 ROTATION GUARD |  | FUEL FEEDING ROTARY FEEDER 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS112 | MEAS_BIN_SRS | Boiler emergency shutdown switch 12 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  | BOILER EMERGENCY SHUTDOWN SWITCH 12 | HS | EMERGENCY STOP | BB1HS112 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST655 |  | BB1ST655 | <IO NOT ASSIGNED> | Fuel feeding rotary feeder 2 rotation guard | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | FUEL FEEDING ROTARY FEEDER 2 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS601 | MEAS_BIN_SRS | Fuel system emergency shutdown switch 1 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP | BB1HS601 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST659 |  | BB1ST659 | <IO NOT ASSIGNED> | Fuel feeding screw 1 rotation guard | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | FUEL FEEDING SCREW 1 ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1HS602 | MEAS_BIN_SRS | Fuel system emergency shutdown switch 2 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP | BB1HS602 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS655 |  | BB1GS655 | <IO NOT ASSIGNED> | Slide gate valve open limit switch | SLIDE GATE VALVE OPEN | LIMIT SWITCH |  | SLIDE GATE VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS603 | MEAS_BIN_SRS | Fuel system emergency shutdown switch 3 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP | BB1HS603 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS656 |  | BB1GS656 | <IO NOT ASSIGNED> | Slide gate valve close limit switch | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | SLIDE GATE VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1HS604 | MEAS_BIN_SRS | Fuel system emergency shutdown switch 4 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP | BB1HS604 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS661 |  | BB1LS661 | <IO NOT ASSIGNED> | Lubrication alarm screw discharger | LUBRICATION ALARM | SCREW DISCHARGER |  | LUBRICATION ALARM SCREW DISCHARGER | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1IV002 | MTR_VLV | Feedwater pump 1 on-off valve | FEEDWATER PUMP 1 ON-OFF | VALVE |  | FEEDWATER PUMP 1 ON-OFF VALVE | IV | ISOLATING VALVE | BB1IV002 | [7 empty] | 0.25kW, 400VAC | MOTOR 0.25kW | MOTOR 0.25kW, 3 PHASE | 0.25 | 0.25
BB1GS802 |  | BB1GS802 | <IO NOT ASSIGNED> | Bottom ash valve limit switch | BOTTOM ASH VALVE | LIMIT SWITCH |  | BOTTOM ASH VALVE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1IV003 | MTR_VLV | Feed water pump 2 on-off valve | FEED WATER PUMP 2 ON-OFF | VALVE |  | FEED WATER PUMP 2 ON-OFF VALVE | IV | ISOLATING VALVE | BB1IV003 | [7 empty] | 0.25kW, 400VAC | MOTOR 0.25kW | MOTOR 0.25kW, 3 PHASE | 0.25 | 0.25
BB1GS803 |  | BB1GS803 | <IO NOT ASSIGNED> | Bottom ash dropping chuteclosing device limit switch | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1IV202 | MTR_VLV | Main steam valve by-pass valve | MAIN STEAM VALVE BY-PASS | VALVE |  | MAIN STEAM VALVE BY-PASS VALVE | IV | ISOLATING VALVE | BB1IV202 | [7 empty] | 0.12kW, 400VAC | MOTOR 0.12kW | MOTOR 0.12kW, 3 PHASE | 0.12 | 0.12
BB1LS852 |  | BB1LS852 | <IO NOT ASSIGNED> | Fly ash container level switch | FLY ASH CONTAINER | LEVEL SWITCH |  | FLY ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1CV201 | MTR_VLV | Start-up valve | START-UP VALVE |  |  | START-UP VALVE | CV | CONTROL VALVE | BB1CV201 | [7 empty] | 0.06kW, 400VAC | MOTOR 0.06kW | MOTOR 0.06kW, 3 PHASE | 0.06 | 0.06
BB1ST805 |  | BB1ST805 | <IO NOT ASSIGNED> | Heated ESP collection screw rotation guard | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  | HEATED ESP COLLECTION SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1IV201 | MTR_VLV | Main steam valve | MAIN STEAM VALVE |  |  | MAIN STEAM VALVE | IV | ISOLATING VALVE | BB1IV201 | [7 empty] | 0.45kW, 400VAC | MOTOR 0.45kW | MOTOR 0.45kW, 3 PHASE | 0.45 | 0.45
BB1ST808 |  | BB1ST808 | <IO NOT ASSIGNED> | ESP hopper 2 screw rotation guard | ESP HOPPER 2 SCREW | ROTATION GUARD |  | ESP HOPPER 2 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1IV200 | MTR_VLV | Start-up check valve | START-UP CHECK VALVE |  |  | START-UP CHECK VALVE | IV | ISOLATING VALVE | BB1IV200 | [7 empty] | 0.12kW, 400VAC | MOTOR 0.12kW | MOTOR 0.12kW, 3 PHASE | 0.12 | 0.12
BB1ST809 |  | BB1ST809 | <IO NOT ASSIGNED> | ESP hopper 1 screw rotation guard | ESP HOPPER 1 SCREW | ROTATION GUARD |  | ESP HOPPER 1 SCREW ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1IV203 | MTR_VLV | Sootblowing line on-off valve | SOOTBLOWING LINE ON-OFF | VALVE |  | SOOTBLOWING LINE ON-OFF VALVE | IV | ISOLATING VALVE | BB1IV203 | [7 empty] | 0.12kW, 400VAC | MOTOR 0.12kW | MOTOR 0.12kW, 3 PHASE | 0.12 | 0.12
BB1ST804 |  | BB1ST804 | <IO NOT ASSIGNED> | ESP Rotary valve rotation guard | ESP ROTARY VALVE | ROTATION GUARD |  | ESP ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1CV003 | MTR_VLV | Continuous blow down valve | CONTINUOUS BLOW DOWN | VALVE |  | CONTINUOUS BLOW DOWN VALVE | CV | CONTROL VALVE | BB1CV003 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1TS808 |  | BB1TS808 | <IO NOT ASSIGNED> | ESP Ash hopper 2 overheat thermostat | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  | ESP ASH HOPPER 2 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1CV203 | MTR_VLV | Steam accumulator pressure control valve | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE |  | STEAM ACCUMULATOR PRESSURE CONTROL VALVE | CV | CONTROL VALVE | BB1CV203 | [7 empty] | 0.25kW, 400VAC | MOTOR 0.25kW | MOTOR 0.25kW, 3 PHASE | 0.25 | 0.25
BB1TS809 |  | BB1TS809 | <IO NOT ASSIGNED> | ESP Ash hopper 1 overheat thermostat | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  | ESP ASH HOPPER 1 OVERHEAT THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1CV202 | MTR_VLV | Steam pressure reduction valve | STEAM PRESSURE REDUCTION | VALVE |  | STEAM PRESSURE REDUCTION VALVE | CV | CONTROL VALVE | BB1CV202 | [7 empty] | 0.25kW, 400VAC | MOTOR 0.25kW | MOTOR 0.25kW, 3 PHASE | 0.25 | 0.25
BB1TS805 |  | BB1TS805 | <IO NOT ASSIGNED> | ESP collection screw heating thermostat | ESP COLLECTION SCREW | HEATING THERMOSTAT |  | ESP COLLECTION SCREW HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1IV204 | MTR_VLV | Main steam line accumulator bypass on-off valve | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE | IV | ISOLATING VALVE | BB1IV204 | [7 empty] | 0.45kW, 400VAC | MOTOR 0.45kW | MOTOR 0.45kW, 3 PHASE | 0.45 | 0.45
BB1TS804 |  | BB1TS804 | <IO NOT ASSIGNED> | ESP Rotary valve heating thermostat | ESP ROTARY VALVE | HEATING THERMOSTAT |  | ESP ROTARY VALVE HEATING THERMOSTAT | TS | TEMPERATURE SWITCH | DI | MEAS_BIN |  | BB1IV205 | MTR_VLV | Steam accumulator ON-OFF isolating valve | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE | IV | ISOLATING VALVE | BB1IV205 | [7 empty] | 0.45kW, 400VAC | MOTOR 0.45kW | MOTOR 0.45kW, 3 PHASE | 0.45 | 0.45
BB1GS855 |  | BB1GS855 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve open limit switch | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1IV206 | MTR_VLV | Primary air preheater on-off valve | PRIMARY AIR PREHEATER | ON-OFF VALVE |  | PRIMARY AIR PREHEATER ON-OFF VALVE | IV | ISOLATING VALVE | BB1IV206 | [7 empty] | 0.12kW, 400VAC | MOTOR 0.12kW | MOTOR 0.12kW, 3 PHASE | 0.12 | 0.12
BB1GS856 |  | BB1GS856 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve close limit switch | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1FM001 | OESA_3ph | Bottom ash sieve feed | BOTTOM ASH SIEVE FEED |  |  | BOTTOM ASH SIEVE FEED | FM | MOTOR | BB1FM001 | [7 empty] | 1,4kW, 400VAC | MOTOR 1,4kW | MOTOR 1,4kW, 3 PHASE | 1,4 | 1,4
BB1GS857 |  | BB1GS857 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve open limit switch | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1FL650 | MCCB_1ph | Fuel silo dust filter control box feed | FUEL SILO DUST FILTER | CONTROL BOX FEED |  | FUEL SILO DUST FILTER CONTROL BOX FEED | FL | FILTER | BB1FL650 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS858 |  | BB1GS858 | <IO NOT ASSIGNED> | Bottom ash valve solenoid valve close limit switch | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1EH662 | MCCB_1ph | Heater for slipring unit | HEATER FOR SLIPRING UNIT |  |  | HEATER FOR SLIPRING UNIT | EH | HEATER | BB1EH662 | [7 empty] | 0.4kW, 400VAC | MOTOR 0.4kW | MOTOR 0.4kW, 3 PHASE | 0.4 | 0.4
BB1GS850 |  | BB1GS850 | <IO NOT ASSIGNED> | Bottom ash sieve bypass valve close limit switch | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | BOTTOM ASH SIEVE BYPASS VALVE CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | <005> | #N/A | Sand transmitter 230 Vac feed | SAND TRANSMITTER | 230 VAC FEED |  | SAND TRANSMITTER 230 VAC FEED | 5> | #N/A | <005> | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
BB1GS851 |  | BB1GS851 | <IO NOT ASSIGNED> | Bottom ash sieve bypass valve open limit switch | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | BOTTOM ASH SIEVE BYPASS VALVE OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1DR400 | MCCB_1ph | Compressor 1 dryer | COMPRESSOR 1 DRYER |  |  | COMPRESSOR 1 DRYER | DR | DRYER | BB1DR400 | [7 empty] | 4kW, 400VAC | MOTOR 4kW | MOTOR 4kW, 3 PHASE | 4 | 4
BB1FS003 |  | BB1FS003 | <IO NOT ASSIGNED> | Bottom ash cooling flow switch | BOTTOM ASH COOLING | FLOW SWITCH |  | BOTTOM ASH COOLING FLOW SWITCH | FS | FLOW SWITCH | DI | MEAS_BIN |  | BB1DR401 | MCCB_1ph | Compressor 2 dryer | COMPRESSOR 2 DRYER |  |  | COMPRESSOR 2 DRYER | DR | DRYER | BB1DR401 | [7 empty] | 4kW, 400VAC | MOTOR 4kW | MOTOR 4kW, 3 PHASE | 4 | 4
BB1GS801 |  | BB1GS801 | <IO NOT ASSIGNED> | Sand filling valve position open limit switch | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | SAND FILLING VALVE POSITION OPEN LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1CP002 | MCCB_1ph | Smoke Exhaust cabinet | SMOKE EXHAUST CABINET |  |  | SMOKE EXHAUST CABINET | CP | CONTROL PANEL? | BB1CP002 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS800 |  | BB1GS800 | <IO NOT ASSIGNED> | Sand filling valve position close limit switch | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | SAND FILLING VALVE POSITION CLOSE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1FG300 | ESP_DI_DO | ESP hardwired signals to/from Boiler PLC | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC |  | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC | FG | ESP | BB1FG300 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS854 |  | BB1GS854 | <IO NOT ASSIGNED> | Bottom ash dropping chute limit switch | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | BOTTOM ASH DROPPING CHUTE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SI400 | FAN_SRS_DO | Primary air fan safety interlock | PRIMARY AIR FAN | SAFETY INTERLOCK |  | PRIMARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI400 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS853 |  | BB1GS853 | <IO NOT ASSIGNED> | Bottom ash dropping chute closing device limit switch | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SI401 | FAN_SRS_DO | Secondary air fan safety interlock | SECONDARY AIR FAN | SAFETY INTERLOCK |  | SECONDARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI401 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS859 |  | BB1GS859 | <IO NOT ASSIGNED> | Bottom ash to container in place | BOTTOM ASH TO CONTAINER | IN PLACE |  | BOTTOM ASH TO CONTAINER IN PLACE | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SI603 | FAN_SRS_DO | Fuel reception hydraulic unit 1, pump 1 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI603 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS850 |  | BB1LS850 | <IO NOT ASSIGNED> | Bottom ash container level switch | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1SI604 | FAN_SRS_DO | Fuel reception hydraulic unit 1, pump 2 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI604 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS851 |  | BB1LS851 | <IO NOT ASSIGNED> | Bottom ash container level switch | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | BOTTOM ASH CONTAINER LEVEL SWITCH | LS | LEVEL SWITCH | DI | MEAS_BIN |  | BB1SI605 | FAN_SRS_DO | Fuel reception hydraulic unit 1, pump 3 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI605 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1PT800 |  | BB1PT800 | <IO NOT ASSIGNED> | Recycled bed material damper pressure switch | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  | RECYCLED BED MATERIAL DAMPER PRESSURE SWITCH | PT | PRESSURE TRANSMITTER | DI | MEAS_BIN |  | BB1SI658 | FAN_SRS_DO | Scraper Conveyor 1 safety interlock | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  | SCRAPER CONVEYOR 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI658 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST856 |  | BB1ST856 | <IO NOT ASSIGNED> | Purified sand screw conveyor rotation guard | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | PURIFIED SAND SCREW CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1SI659 | FAN_SRS_DO | Belt Conveyor safety interlock | BELT CONVEYOR | SAFETY INTERLOCK |  | BELT CONVEYOR SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI659 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST850 |  | BB1ST850 | <IO NOT ASSIGNED> | Bottom ash conveyor rotation guard | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | BOTTOM ASH CONVEYOR ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1SI675 | FAN_SRS_DO | Disc screen drive 1 safety interlock | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  | DISC SCREEN DRIVE 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI675 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS852 |  | BB1GS852 | <IO NOT ASSIGNED> | Bottom ash conveyor blockage detector | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | BOTTOM ASH CONVEYOR BLOCKAGE DETECTOR | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SI676 | FAN_SRS_DO | Disc screen drive 2 safety interlock | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  | DISC SCREEN DRIVE 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI676 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST852 |  | BB1ST852 | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve rotation guard | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 2ND PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1SI672 | FAN_SRS_DO | Scraper Conveyor 2 safety interlock | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  | SCRAPER CONVEYOR 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI672 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1ST853 |  | BB1ST853 | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve rotation guard | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 3RD PASS FLY ASH ROTARY VALVE ROTATION GUARD | ST | SPEED SWITCH/ROTATION GUARD | DI | MEAS_BIN |  | BB1SI550 | FAN_SRS_DO | Flue gas fan safety interlock | FLUE GAS FAN | SAFETY INTERLOCK |  | FLUE GAS FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK | BB1SI550 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1GS020 |  | BB1GS020 | <IO NOT ASSIGNED> | Emergency shower use switch | EMERGENCY SHOWER | USE SWITCH |  | EMERGENCY SHOWER USE SWITCH | GS | GATE SWITCH | DI | MEAS_BIN |  | BB1SV601 | PUSH_FEED | Control Valve push feeders unloading station 1 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 | SV | SOLENOID VALVE | BB1SV601 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS103 |  | BB1LS103 | <IO NOT ASSIGNED> | Steam drum level switch 1 | STEAM DRUM LEVEL SWITCH 1 |  |  | STEAM DRUM LEVEL SWITCH 1 | LS | LEVEL SWITCH |  | MEAS_BIN_SRS |  | BB1SV603 | PUSH_FEED | Control Valve push feeders unloading station 3 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 | SV | SOLENOID VALVE | BB1SV603 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1LS104 |  | BB1LS104 | <IO NOT ASSIGNED> | Steam drum level switch 2 | STEAM DRUM LEVEL SWITCH 2 |  |  | STEAM DRUM LEVEL SWITCH 2 | LS | LEVEL SWITCH |  | MEAS_BIN_SRS |  | BB1SV602 | PUSH_FEED | Control Valve push feeders unloading station 2 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 | SV | SOLENOID VALVE | BB1SV602 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1HS101 |  | BB1HS101 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 1 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  | BOILER EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM001 | FRQ_DIR | Feed water pump 1 | FEED WATER PUMP 1 |  |  | FEED WATER PUMP 1 | EM | MOTOR | BB1EM001_VSD | 20F11GC140AA0NNNNN | PowerFlex 753 Series VSD, 75kW, 400VAC |  |  |  | BB1EM001 |  | 75kW, 400VAC | MOTOR 75kW | MOTOR 75kW, 3 PHASE | 75 | 75
BB1HS103 |  | BB1HS103 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 3 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  | BOILER EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM002 | FRQ_DIR | Feed water pump 2 | FEED WATER PUMP 2 |  |  | FEED WATER PUMP 2 | EM | MOTOR | BB1EM002_VSD | 20F11GC140AA0NNNNN | PowerFlex 753 Series VSD, 75kW, 400VAC |  |  |  | BB1EM002 |  | 75kW, 400VAC | MOTOR 75kW | MOTOR 75kW, 3 PHASE | 75 | 75
BB1HS104 |  | BB1HS104 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 4 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  | BOILER EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM400 | FRQ_DIR | Primary air fan | PRIMARY AIR FAN |  |  | PRIMARY AIR FAN | EM | MOTOR | BB1EM400_VSD | 20F11GC260AA0NNNNN | PowerFlex 1323 Series VSD, 132kW, 400VAC |  |  |  | BB1EM400 |  | 132kW, 400VAC | MOTOR 132kW | MOTOR 132kW, 3 PHASE | 132 | 132
BB1HS102 |  | BB1HS102 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 2 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  | BOILER EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM401 | FRQ_DIR | Secondary air fan | SECONDARY AIR FAN |  |  | SECONDARY AIR FAN | EM | MOTOR | BB1EM401_VSD | 20F11GC085AA0NNNNN | PowerFlex 753 Series VSD, 45kW, 400VAC |  |  |  | BB1EM401 |  | 45kW, 400VAC | MOTOR 45kW | MOTOR 45kW, 3 PHASE | 45 | 45
BB1HS105 |  | BB1HS105 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 5 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  | BOILER EMERGENCY SHUTDOWN SWITCH 5 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM550 | FRQ_DIR | Flue gas fan | FLUE GAS FAN |  |  | FLUE GAS FAN | EM | MOTOR | BB1EM550_VSD | 20F11GC140AA0NNNNN | PowerFlex 753 Series VSD, 75kW, 400VAC |  |  |  | BB1EM550 |  | 75kW, 400VAC | MOTOR 75kW | MOTOR 75kW, 3 PHASE | 75 | 75
BB1HS106 |  | BB1HS106 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 6 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  | BOILER EMERGENCY SHUTDOWN SWITCH 6 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM603 | FRQ_DIRH | Fuel reception hydraulic unit 1, pump 1 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 | EM | MOTOR | BB1EM603_VSD | 20F11GC072AA0NNNNN | PowerFlex 753 Series VSD, 37kW, 400VAC |  |  |  | BB1EM603 |  | 37kW, 400VAC | MOTOR 37kW | MOTOR 37kW, 3 PHASE | 37 | 37
BB1HS107 |  | BB1HS107 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 7 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  | BOILER EMERGENCY SHUTDOWN SWITCH 7 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM604 | FRQ_DIRH | Fuel reception hydraulic unit 1, pump 2 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 | EM | MOTOR | BB1EM604_VSD | 20F11GC072AA0NNNNN | PowerFlex 753 Series VSD, 37kW, 400VAC |  |  |  | BB1EM604 |  | 37kW, 400VAC | MOTOR 37kW | MOTOR 37kW, 3 PHASE | 37 | 37
BB1HS108 |  | BB1HS108 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 8 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  | BOILER EMERGENCY SHUTDOWN SWITCH 8 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM605 | FRQ_DIRH | Fuel reception hydraulic unit 1, pump 3 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 | EM | MOTOR | BB1EM605_VSD | 20F11GC072AA0NNNNN | PowerFlex 753 Series VSD, 37kW, 400VAC |  |  |  | BB1EM605 |  | 37kW, 400VAC | MOTOR 37kW | MOTOR 37kW, 3 PHASE | 37 | 37
BB1HS109 |  | BB1HS109 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 9 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  | BOILER EMERGENCY SHUTDOWN SWITCH 9 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM658 | FRQ_REVH | SCRAPER CONVEYOR 1 | SCRAPER CONVEYOR 1 |  |  | SCRAPER CONVEYOR 1 | EM | MOTOR | BB1EM658_VSD | 20F11GC030AA0NNNNN | PowerFlex 753 Series VSD, 15kW, 400VAC | BB1EM658 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | BB1EM658 |  | 15kW, 400VAC | MOTOR 15kW | MOTOR 15kW, 3 PHASE | 15 | 15
BB1HS110 |  | BB1HS110 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 10 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  | BOILER EMERGENCY SHUTDOWN SWITCH 10 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM659 | FRQ_REVH | BELT CONVEYOR | BELT CONVEYOR |  |  | BELT CONVEYOR | EM | MOTOR | BB1EM659_VSD | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM659 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM659 |  | 4kW, 400VAC | MOTOR 4kW | MOTOR 4kW, 3 PHASE | 4 | 4
BB1HS111 |  | BB1HS111 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 11 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  | BOILER EMERGENCY SHUTDOWN SWITCH 11 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM675 | DOL_REVH_BUS | DISC SCREEN DRIVE 1 | DISC SCREEN DRIVE 1 |  |  | DISC SCREEN DRIVE 1 | EM | MOTOR | BB1EM675 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1HS112 |  | BB1HS112 | <IO NOT ASSIGNED> | Boiler emergency shutdown switch 12 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  | BOILER EMERGENCY SHUTDOWN SWITCH 12 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM676 | FRQ_REVH | DISC SCREEN DRIVE 2 | DISC SCREEN DRIVE 2 |  |  | DISC SCREEN DRIVE 2 | EM | MOTOR | BB1EM676_VSD | 20F11GC022AA0NNNNN | PowerFlex 753 Series VSD, 11kW, 400VAC | BB1EM676 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM676 |  | 7.5kW, 400VAC | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE | 11 | 7.5
BB1HS601 |  | BB1HS601 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 1 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 1 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM672 | FRQ_REVH | SCRAPER CONVEYOR 2 | SCRAPER CONVEYOR 2 |  |  | SCRAPER CONVEYOR 2 | EM | MOTOR | BB1EM672_VSD | 20F11GC043AA0NNNNN | PowerFlex 753 Series VSD, 22kW, 400VAC | BB1EM672 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | BB1EM672 |  | 18,5kW, 400VAC | MOTOR 18,5kW | MOTOR 18,5kW, 3 PHASE | 22 | 18,5
BB1HS602 |  | BB1HS602 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 2 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 2 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM662 | FRQ_REVH | FUEL SILO SCREW DISCHARGE | FUEL SILO SCREW DISCHARGE |  |  | FUEL SILO SCREW DISCHARGE | EM | MOTOR | BB1EM662_VSD | 20F11GC060AA0NNNNN | PowerFlex 753 Series VSD, 30kW, 400VAC | BB1EM662 | SEP2663 | VSD FIELD ISOLATOR WITH SOCKET: 15-30kW (52A), 3 Pole, 2 x N/O Aux | BB1EM662 |  | 22kW, 400VAC | MOTOR 22kW | MOTOR 22kW, 3 PHASE | 30 | 22
BB1HS603 |  | BB1HS603 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 3 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 3 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM650 | FRQ_REVH | SLEWING MOTOR FOR SCREW | SLEWING MOTOR FOR SCREW |  |  | SLEWING MOTOR FOR SCREW | EM | MOTOR | BB1EM650_VSD | 20F11GC5P7AA0NNNNN | PowerFlex 753 Series VSD, 2.2kW, 400VAC | BB1EM650 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM650 |  | 4kW, 400VAC | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | 2.2 | 2.2
BB1HS604 |  | BB1HS604 | <IO NOT ASSIGNED> | Fuel system emergency shutdown switch 4 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 4 | HS | EMERGENCY STOP |  | MEAS_BIN_SRS |  | BB1EM663 | FRQ_REVH | FUEL SILO CROSS CONVEYOR | FUEL SILO CROSS CONVEYOR |  |  | FUEL SILO CROSS CONVEYOR | EM | MOTOR | BB1EM663_VSD | 20F11GC8P7AA0NNNNN | PowerFlex 753 Series VSD, 4kW, 400VAC | BB1EM663 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM663 |  | 4kW, 400VAC | MOTOR 4kW | MOTOR 4kW, 3 PHASE | 4 | 4
BB1IV002 | _OPEN | BB1IV002_OPEN | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve OPEN | FEEDWATER PUMP 1 ON-OFF | VALVE OPEN |  | FEEDWATER PUMP 1 ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM664 | FRQ_REVH | FUEL FEEDING SCREW 1 | FUEL FEEDING SCREW 1 |  |  | FUEL FEEDING SCREW 1 | EM | MOTOR | BB1EM664_VSD | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | BB1EM664 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM664 |  | 5.5kW, 400VAC | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE | 5.5 | 5.5
BB1IV002 | _CLOSE | BB1IV002_CLOSE | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve CLOSE | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSE |  | FEEDWATER PUMP 1 ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM665 | FRQ_REVH | FUEL FEEDING SCREW 2 | FUEL FEEDING SCREW 2 |  |  | FUEL FEEDING SCREW 2 | EM | MOTOR | BB1EM665_VSD | 20F11GC011AA0NNNNN | PowerFlex 753 Series VSD, 5.5kW, 400VAC | BB1EM665 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM665 |  | 5.5kW, 400VAC | MOTOR 5.5kW | MOTOR 5.5kW, 3 PHASE | 5.5 | 5.5
BB1IV002 | _OPENED | BB1IV002_OPENED | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve OPENED | FEEDWATER PUMP 1 ON-OFF | VALVE OPENED |  | FEEDWATER PUMP 1 ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM852 | FRQ_REVH | BOTTOM ASH CONVEYOR | BOTTOM ASH CONVEYOR |  |  | BOTTOM ASH CONVEYOR | EM | MOTOR | BB1EM852_VSD | 20F11GC5P7AA0NNNNN | PowerFlex 753 Series VSD, 2.2kW, 400VAC | BB1EM852 | SEP2662 | VSD FIELD ISOLATOR: 0-15kW (26A), 3 Pole, 2 x N/O Aux | BB1EM852 |  | 4kW, 400VAC | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | 2.2 | 2.2
BB1IV002 | _CLOSED | BB1IV002_CLOSED | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve CLOSED | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSED |  | FEEDWATER PUMP 1 ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM660 | DOL_DIR_BUS | Cooling fan for slewing motor | COOLING FAN FOR | SLEWING MOTOR |  | COOLING FAN FOR SLEWING MOTOR | EM | MOTOR | BB1EM660 | [7 empty] | 0.09kW, 400VAC | MOTOR 0.09kW | MOTOR 0.09kW, 3 PHASE | 0.09 | 0.09
BB1IV002 | _FAULT | BB1IV002_FAULT | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve FAULT | FEEDWATER PUMP 1 ON-OFF | VALVE FAULT |  | FEEDWATER PUMP 1 ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM654 | DOL_DIR_BUS | Lubrication unit | LUBRICATION UNIT |  |  | LUBRICATION UNIT | EM | MOTOR | BB1EM654 | [7 empty] | 0.2kW, 400VAC | MOTOR 0.2kW | MOTOR 0.2kW, 3 PHASE | 0.2 | 0.2
BB1IV002 | _POSITION | BB1IV002_POSITION | <IO NOT ASSIGNED> | Feedwater pump 1 on-off valve POSITION | FEEDWATER PUMP 1 ON-OFF | VALVE POSITION |  | FEEDWATER PUMP 1 ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM653 | DOL_DIR_BUS | Cooling fan fuel feeding screw 1 | COOLING FAN FUEL | FEEDING SCREW 1 |  | COOLING FAN FUEL FEEDING SCREW 1 | EM | MOTOR | BB1EM653 | [7 empty] | 0.15kW, 400VAC | MOTOR 0.15kW | MOTOR 0.15kW, 3 PHASE | 0.15 | 0.15
BB1IV003 | _OPEN | BB1IV003_OPEN | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve OPEN | FEED WATER PUMP 2 ON-OFF | VALVE OPEN |  | FEED WATER PUMP 2 ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM655 | DOL_DIR_BUS | Cooling fan fuel feeding screw 2 | COOLING FAN FUEL | FEEDING SCREW 2 |  | COOLING FAN FUEL FEEDING SCREW 2 | EM | MOTOR | BB1EM655 | [7 empty] | 0.15kW, 400VAC | MOTOR 0.15kW | MOTOR 0.15kW, 3 PHASE | 0.15 | 0.15
BB1IV003 | _CLOSE | BB1IV003_CLOSE | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve CLOSE | FEED WATER PUMP 2 ON-OFF | VALVE CLOSE |  | FEED WATER PUMP 2 ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM606 | FRQ_DIR | Dust extraction fan | DUST EXTRACTION FAN |  |  | DUST EXTRACTION FAN | EM | MOTOR | BB1EM606_VSD | 20F11GC072AA0NNNNN | PowerFlex 753 Series VSD, 37kW, 400VAC |  |  |  | BB1EM606 |  | 30kW, 400VAC | MOTOR 30kW | MOTOR 30kW, 3 PHASE | 37 | 30
BB1IV003 | _OPENED | BB1IV003_OPENED | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve OPENED | FEED WATER PUMP 2 ON-OFF | VALVE OPENED |  | FEED WATER PUMP 2 ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EH600 | DOL_DIR_BUS | Electric heater hydraulic unit | ELECTRIC HEATER | HYDRAULIC UNIT |  | ELECTRIC HEATER HYDRAULIC UNIT | EH | HEATER | BB1EH600 | [7 empty] | 1,5kW, 400VAC | MOTOR 1,5kW | MOTOR 1,5kW, 3 PHASE | 1,5 | 1,5
BB1IV003 | _CLOSED | BB1IV003_CLOSED | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve CLOSED | FEED WATER PUMP 2 ON-OFF | VALVE CLOSED |  | FEED WATER PUMP 2 ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM651 | DOL_DIR_BUS | Fuel silo dust filter fan | FUEL SILO DUST FILTER FAN |  |  | FUEL SILO DUST FILTER FAN | EM | MOTOR | BB1EM651 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IV003 | _FAULT | BB1IV003_FAULT | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve FAULT | FEED WATER PUMP 2 ON-OFF | VALVE FAULT |  | FEED WATER PUMP 2 ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM008 | DOL_DIR_BUS | Conveyor cooling pump | CONVEYOR COOLING PUMP |  |  | CONVEYOR COOLING PUMP | EM | MOTOR | BB1EM008 | [7 empty] | 1,1kW, 400VAC | MOTOR 1,1kW | MOTOR 1,1kW, 3 PHASE | 1,1 | 1,1
BB1IV003 | _POSITION | BB1IV003_POSITION | <IO NOT ASSIGNED> | Feed water pump 2 on-off valve POSITION | FEED WATER PUMP 2 ON-OFF | VALVE POSITION |  | FEED WATER PUMP 2 ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM009 | DOL_DIR_BUS | Bottom ash conveyor heat exchanger fan | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN |  | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN | EM | MOTOR | BB1EM009 | [7 empty] | 7,5kW, 400VAC | MOTOR 7,5kW | MOTOR 7,5kW, 3 PHASE | 7,5 | 7,5
BB1IV202 | _OPEN | BB1IV202_OPEN | <IO NOT ASSIGNED> | Main steam valve by-pass valve OPEN | MAIN STEAM VALVE BY-PASS | VALVE OPEN |  | MAIN STEAM VALVE BY-PASS VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM408 | DOL_DIR_BUS | Boiler house heater 1 | BOILER HOUSE HEATER 1 |  |  | BOILER HOUSE HEATER 1 | EM | MOTOR | BB1EM408 | [7 empty] | 15kW, 400VAC | MOTOR 15kW | MOTOR 15kW, 3 PHASE | 15 | 15
BB1IV202 | _CLOSE | BB1IV202_CLOSE | <IO NOT ASSIGNED> | Main steam valve by-pass valve CLOSE | MAIN STEAM VALVE BY-PASS | VALVE CLOSE |  | MAIN STEAM VALVE BY-PASS VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM409 | DOL_DIR_BUS | Boiler house heater 2 | BOILER HOUSE HEATER 2 |  |  | BOILER HOUSE HEATER 2 | EM | MOTOR | BB1EM409 | [7 empty] | 15kW, 400VAC | MOTOR 15kW | MOTOR 15kW, 3 PHASE | 15 | 15
BB1IV202 | _OPENED | BB1IV202_OPENED | <IO NOT ASSIGNED> | Main steam valve by-pass valve OPENED | MAIN STEAM VALVE BY-PASS | VALVE OPENED |  | MAIN STEAM VALVE BY-PASS VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM703 | DOL_DIRH_BUS | Chemical filling pump 1 | CHEMICAL FILLING PUMP 1 |  |  | CHEMICAL FILLING PUMP 1 | EM | MOTOR | BB1EM703 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IV202 | _CLOSED | BB1IV202_CLOSED | <IO NOT ASSIGNED> | Main steam valve by-pass valve CLOSED | MAIN STEAM VALVE BY-PASS | VALVE CLOSED |  | MAIN STEAM VALVE BY-PASS VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM704 | DOL_DIRH_BUS | Chemical filling pump 2 | CHEMICAL FILLING PUMP 2 |  |  | CHEMICAL FILLING PUMP 2 | EM | MOTOR | BB1EM704 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IV202 | _FAULT | BB1IV202_FAULT | <IO NOT ASSIGNED> | Main steam valve by-pass valve FAULT | MAIN STEAM VALVE BY-PASS | VALVE FAULT |  | MAIN STEAM VALVE BY-PASS VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM670 | DOL_DIRH_BUS | Belt magnet | BELT MAGNET |  |  | BELT MAGNET | EM | MOTOR | BB1EM670 | [7 empty] | 2.2kW, 400VAC | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | 2.2 | 2.2
BB1IV202 | _POSITION | BB1IV202_POSITION | <IO NOT ASSIGNED> | Main steam valve by-pass valve POSITION | MAIN STEAM VALVE BY-PASS | VALVE POSITION |  | MAIN STEAM VALVE BY-PASS VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM652 | DOL_DIRH_BUS | Rotating fuel spreader | ROTATING FUEL SPREADER |  |  | ROTATING FUEL SPREADER | EM | MOTOR | BB1EM652 | [7 empty] | 0.75kW, 400VAC | MOTOR 0.75kW | MOTOR 0.75kW, 3 PHASE | 0.75 | 0.75
BB1CV201 | _OPEN | BB1CV201_OPEN | <IO NOT ASSIGNED> | Start-up valve OPEN | START-UP VALVE OPEN |  |  | START-UP VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV |  | BB1BL200 | DOL_REV_BUS | Sootblower 1 | SOOTBLOWER 1 |  |  | SOOTBLOWER 1 | BL | BLOWER | BB1BL200 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1CV201 | _CLOSE | BB1CV201_CLOSE | <IO NOT ASSIGNED> | Start-up valve CLOSE | START-UP VALVE CLOSE |  |  | START-UP VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV |  | BB1BL201 | DOL_REV_BUS | Sootblower 2 | SOOTBLOWER 2 |  |  | SOOTBLOWER 2 | BL | BLOWER | BB1BL201 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1CV201 | _OPENED | BB1CV201_OPENED | <IO NOT ASSIGNED> | Start-up valve OPENED | START-UP VALVE OPENED |  |  | START-UP VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV |  | BB1BL202 | DOL_REV_BUS | Sootblower 3 | SOOTBLOWER 3 |  |  | SOOTBLOWER 3 | BL | BLOWER | BB1BL202 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1CV201 | _CLOSED | BB1CV201_CLOSED | <IO NOT ASSIGNED> | Start-up valve CLOSED | START-UP VALVE CLOSED |  |  | START-UP VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV |  | BB1BL203 | DOL_REV_BUS | Sootblower 4 | SOOTBLOWER 4 |  |  | SOOTBLOWER 4 | BL | BLOWER | BB1BL203 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1CV201 | _FAULT | BB1CV201_FAULT | <IO NOT ASSIGNED> | Start-up valve FAULT | START-UP VALVE FAULT |  |  | START-UP VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV |  | BB1BL204 | DOL_REV_BUS | Sootblower 5 | SOOTBLOWER 5 |  |  | SOOTBLOWER 5 | BL | BLOWER | BB1BL204 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1CV201 | _POSITION | BB1CV201_POSITION | <IO NOT ASSIGNED> | Start-up valve POSITION | START-UP VALVE POSITION |  |  | START-UP VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV |  | BB1BL205 | DOL_REV_BUS | Sootblower 6 | SOOTBLOWER 6 |  |  | SOOTBLOWER 6 | BL | BLOWER | BB1BL205 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1IV201 | _OPEN | BB1IV201_OPEN | <IO NOT ASSIGNED> | Main steam valve OPEN | MAIN STEAM VALVE OPEN |  |  | MAIN STEAM VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1BL206 | DOL_REV_BUS | Sootblower 7 | SOOTBLOWER 7 |  |  | SOOTBLOWER 7 | BL | BLOWER | BB1BL206 | [7 empty] | 0,37kW, 400VAC | MOTOR 0,37kW | MOTOR 0,37kW, 3 PHASE | 0,37 | 0,37
BB1IV201 | _CLOSE | BB1IV201_CLOSE | <IO NOT ASSIGNED> | Main steam valve CLOSE | MAIN STEAM VALVE CLOSE |  |  | MAIN STEAM VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM815 | DOL_REV_BUS | Fly ash container screw | FLY ASH CONTAINER SCREW |  |  | FLY ASH CONTAINER SCREW | EM | MOTOR | BB1EM815 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IV201 | _OPENED | BB1IV201_OPENED | <IO NOT ASSIGNED> | Main steam valve OPENED | MAIN STEAM VALVE OPENED |  |  | MAIN STEAM VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM855 | DOL_REV_BUS | Ash container screw | ASH CONTAINER SCREW |  |  | ASH CONTAINER SCREW | EM | MOTOR | BB1EM855 | [7 empty] | 1,5kW, 400VAC | MOTOR 1,5kW | MOTOR 1,5kW, 3 PHASE | 1,5 | 1,5
BB1IV201 | _CLOSED | BB1IV201_CLOSED | <IO NOT ASSIGNED> | Main steam valve CLOSED | MAIN STEAM VALVE CLOSED |  |  | MAIN STEAM VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM411 | DOL_REV_BUS | Exhaust fan 1 | EXHAUST FAN 1 |  |  | EXHAUST FAN 1 | EM | MOTOR | BB1EM411_VSD | 20F11GC085AA0NNNNN | PowerFlex 753 Series VSD, 45kW, 400VAC |  |  |  | BB1EM411 |  | 1,9kW, 400VAC | MOTOR 1,9kW | MOTOR 1,9kW, 3 PHASE | 1,9 | 1,9
BB1IV201 | _FAULT | BB1IV201_FAULT | <IO NOT ASSIGNED> | Main steam valve FAULT | MAIN STEAM VALVE FAULT |  |  | MAIN STEAM VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM402 | COMPR | Exhaust fan 2 | EXHAUST FAN 2 |  |  | EXHAUST FAN 2 | EM | MOTOR | BB1EM402 | [7 empty] | 30kW, 400VAC | MOTOR 30kW | MOTOR 30kW, 3 PHASE | 30 | 30
BB1IV201 | _POSITION | BB1IV201_POSITION | <IO NOT ASSIGNED> | Main steam valve POSITION | MAIN STEAM VALVE POSITION |  |  | MAIN STEAM VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM403 | COMPR | Exhaust fan 3 | EXHAUST FAN 3 |  |  | EXHAUST FAN 3 | EM | MOTOR | BB1EM403 | [7 empty] | 30kW, 400VAC | MOTOR 30kW | MOTOR 30kW, 3 PHASE | 30 | 30
BB1IV200 | _OPEN | BB1IV200_OPEN | <IO NOT ASSIGNED> | Start-up check valve OPEN | START-UP CHECK VALVE | OPEN |  | START-UP CHECK VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  |  | #N/A | [6 empty] | 0 | 0 | [7 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
BB1IV200 | _CLOSE | BB1IV200_CLOSE | <IO NOT ASSIGNED> | Start-up check valve CLOSE | START-UP CHECK VALVE | CLOSE |  | START-UP CHECK VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM673 | DOL_REVH_BUS | Levelling roller 1 | LEVELLING ROLLER 1 |  |  | LEVELLING ROLLER 1 | EM | MOTOR | BB1EM673 | [7 empty] | 2,2kW, 400VAC | MOTOR 2,2kW | MOTOR 2,2kW, 3 PHASE | 2,2 | 2,2
BB1IV200 | _OPENED | BB1IV200_OPENED | <IO NOT ASSIGNED> | Start-up check valve OPENED | START-UP CHECK VALVE | OPENED |  | START-UP CHECK VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM674 | DOL_REVH_BUS | Levelling roller 2 | LEVELLING ROLLER 2 |  |  | LEVELLING ROLLER 2 | EM | MOTOR | BB1EM674 | [7 empty] | 3kW, 400VAC | MOTOR 3kW | MOTOR 3kW, 3 PHASE | 3 | 3
BB1IV200 | _CLOSED | BB1IV200_CLOSED | <IO NOT ASSIGNED> | Start-up check valve CLOSED | START-UP CHECK VALVE | CLOSED |  | START-UP CHECK VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM601 | DOL_REVH_BUS | Dust extraction rotary feeder | DUST EXTRACTION | ROTARY FEEDER |  | DUST EXTRACTION ROTARY FEEDER | EM | MOTOR | BB1EM601 | [7 empty] | 0,75kW, 400VAC | MOTOR 0,75kW | MOTOR 0,75kW, 3 PHASE | 0,75 | 0,75
BB1IV200 | _FAULT | BB1IV200_FAULT | <IO NOT ASSIGNED> | Start-up check valve FAULT | START-UP CHECK VALVE | FAULT |  | START-UP CHECK VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1IV650 | DOL_REVH_BUS | Slide gate valve | SLIDE GATE VALVE |  |  | SLIDE GATE VALVE | IV | ISOLATING VALVE | BB1IV650 | [7 empty] | 2.2kW, 400VAC | MOTOR 2.2kW | MOTOR 2.2kW, 3 PHASE | 2.2 | 2.2
BB1IV200 | _POSITION | BB1IV200_POSITION | <IO NOT ASSIGNED> | Start-up check valve POSITION | START-UP CHECK VALVE | POSITION |  | START-UP CHECK VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV |  | BB1EM657 | DOL_REVH_BUS | Fuel feeding rotary valve 1 | FUEL FEEDING | ROTARY VALVE 1 |  | FUEL FEEDING ROTARY VALVE 1 | EM | MOTOR | BB1EM657 | [7 empty] | 7.5kW, 400VAC | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE | 7.5 | 7.5
BB1IV203 | _OPEN | BB1IV203_OPEN | <IO NOT ASSIGNED> | Sootblowing line on-off valve OPEN | SOOTBLOWING LINE ON-OFF | VALVE OPEN |  | SOOTBLOWING LINE ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM656 | DOL_REVH_BUS | Fuel feeding rotary valve 2 | FUEL FEEDING | ROTARY VALVE 2 |  | FUEL FEEDING ROTARY VALVE 2 | EM | MOTOR | BB1EM656 | [7 empty] | 7.5kW, 400VAC | MOTOR 7.5kW | MOTOR 7.5kW, 3 PHASE | 7.5 | 7.5
BB1IV203 | _CLOSE | BB1IV203_CLOSE | <IO NOT ASSIGNED> | Sootblowing line on-off valve CLOSE | SOOTBLOWING LINE ON-OFF | VALVE CLOSE |  | SOOTBLOWING LINE ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV |  | BB1EM856 | DOL_REVH_BUS | Purified sand screw conveyor | PURIFIED SAND | SCREW CONVEYOR |  | PURIFIED SAND SCREW CONVEYOR | EM | MOTOR | BB1EM856 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IV203 | _OPENED | BB1IV203_OPENED | <IO NOT ASSIGNED> | Sootblowing line on-off valve OPENED | SOOTBLOWING LINE ON-OFF | VALVE OPENED |  | SOOTBLOWING LINE ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM850 | DOL_REVH_BUS | 2nd pass fly ash rotary valve | 2ND PASS FLY ASH | ROTARY VALVE |  | 2ND PASS FLY ASH ROTARY VALVE | EM | MOTOR | BB1EM850 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IV203 | _CLOSED | BB1IV203_CLOSED | <IO NOT ASSIGNED> | Sootblowing line on-off valve CLOSED | SOOTBLOWING LINE ON-OFF | VALVE CLOSED |  | SOOTBLOWING LINE ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV |  | BB1EM851 | DOL_REVH_BUS | 3rd pass fly ash rotary valve | 3RD PASS FLY ASH | ROTARY VALVE |  | 3RD PASS FLY ASH ROTARY VALVE | EM | MOTOR | BB1EM851 | [7 empty] | 0kW, 400VAC | MOTOR 0kW | MOTOR 0kW, 3 PHASE | 0 | 0
BB1IV203 | _FAULT | BB1IV203_FAULT | <IO NOT ASSIGNED> | Sootblowing line on-off valve FAULT | SOOTBLOWING LINE ON-OFF | VALVE FAULT |  | SOOTBLOWING LINE ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV203 | _POSITION | BB1IV203_POSITION | <IO NOT ASSIGNED> | Sootblowing line on-off valve POSITION | SOOTBLOWING LINE ON-OFF | VALVE POSITION |  | SOOTBLOWING LINE ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1CV003 | _OPEN | BB1CV003_OPEN | <IO NOT ASSIGNED> | Continuous blow down valve OPEN | CONTINUOUS BLOW DOWN | VALVE OPEN |  | CONTINUOUS BLOW DOWN VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV003 | _CLOSE | BB1CV003_CLOSE | <IO NOT ASSIGNED> | Continuous blow down valve CLOSE | CONTINUOUS BLOW DOWN | VALVE CLOSE |  | CONTINUOUS BLOW DOWN VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV003 | _OPENED | BB1CV003_OPENED | <IO NOT ASSIGNED> | Continuous blow down valve OPENED | CONTINUOUS BLOW DOWN | VALVE OPENED |  | CONTINUOUS BLOW DOWN VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _CLOSED | BB1CV003_CLOSED | <IO NOT ASSIGNED> | Continuous blow down valve CLOSED | CONTINUOUS BLOW DOWN | VALVE CLOSED |  | CONTINUOUS BLOW DOWN VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _FAULT | BB1CV003_FAULT | <IO NOT ASSIGNED> | Continuous blow down valve FAULT | CONTINUOUS BLOW DOWN | VALVE FAULT |  | CONTINUOUS BLOW DOWN VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV003 | _POSITION | BB1CV003_POSITION | <IO NOT ASSIGNED> | Continuous blow down valve POSITION | CONTINUOUS BLOW DOWN | VALVE POSITION |  | CONTINUOUS BLOW DOWN VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1CV203 | _OPEN | BB1CV203_OPEN | <IO NOT ASSIGNED> | Steam accumulator pressure control valve OPEN | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV203 | _CLOSE | BB1CV203_CLOSE | <IO NOT ASSIGNED> | Steam accumulator pressure control valve CLOSE | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV203 | _OPENED | BB1CV203_OPENED | <IO NOT ASSIGNED> | Steam accumulator pressure control valve OPENED | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPENED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _CLOSED | BB1CV203_CLOSED | <IO NOT ASSIGNED> | Steam accumulator pressure control valve CLOSED | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _FAULT | BB1CV203_FAULT | <IO NOT ASSIGNED> | Steam accumulator pressure control valve FAULT | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | FAULT | STEAM ACCUMULATOR PRESSURE CONTROL VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV203 | _POSITION | BB1CV203_POSITION | <IO NOT ASSIGNED> | Steam accumulator pressure control valve POSITION | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | POSITION | STEAM ACCUMULATOR PRESSURE CONTROL VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1CV202 | _OPEN | BB1CV202_OPEN | <IO NOT ASSIGNED> | Steam pressure reduction valve OPEN | STEAM PRESSURE REDUCTION | VALVE OPEN |  | STEAM PRESSURE REDUCTION VALVE OPEN | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV202 | _CLOSE | BB1CV202_CLOSE | <IO NOT ASSIGNED> | Steam pressure reduction valve CLOSE | STEAM PRESSURE REDUCTION | VALVE CLOSE |  | STEAM PRESSURE REDUCTION VALVE CLOSE | CV | CONTROL VALVE | DO | MTR_VLV
BB1CV202 | _OPENED | BB1CV202_OPENED | <IO NOT ASSIGNED> | Steam pressure reduction valve OPENED | STEAM PRESSURE REDUCTION | VALVE OPENED |  | STEAM PRESSURE REDUCTION VALVE OPENED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _CLOSED | BB1CV202_CLOSED | <IO NOT ASSIGNED> | Steam pressure reduction valve CLOSED | STEAM PRESSURE REDUCTION | VALVE CLOSED |  | STEAM PRESSURE REDUCTION VALVE CLOSED | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _FAULT | BB1CV202_FAULT | <IO NOT ASSIGNED> | Steam pressure reduction valve FAULT | STEAM PRESSURE REDUCTION | VALVE FAULT |  | STEAM PRESSURE REDUCTION VALVE FAULT | CV | CONTROL VALVE | DI | MTR_VLV
BB1CV202 | _POSITION | BB1CV202_POSITION | <IO NOT ASSIGNED> | Steam pressure reduction valve POSITION | STEAM PRESSURE REDUCTION | VALVE POSITION |  | STEAM PRESSURE REDUCTION VALVE POSITION | CV | CONTROL VALVE | AI | MTR_VLV
BB1IV204 | _OPEN | BB1IV204_OPEN | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve OPEN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV204 | _CLOSE | BB1IV204_CLOSE | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve CLOSE | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV204 | _OPENED | BB1IV204_OPENED | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve OPENED | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPENED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _CLOSED | BB1IV204_CLOSED | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve CLOSED | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _FAULT | BB1IV204_FAULT | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve FAULT | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE FAULT | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV204 | _POSITION | BB1IV204_POSITION | <IO NOT ASSIGNED> | Main steam line accumulator bypass on-off valve POSITION | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE POSITION | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV205 | _OPEN | BB1IV205_OPEN | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve OPEN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV205 | _CLOSE | BB1IV205_CLOSE | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve CLOSE | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV205 | _OPENED | BB1IV205_OPENED | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve OPENED | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPENED |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _CLOSED | BB1IV205_CLOSED | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve CLOSED | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSED |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _FAULT | BB1IV205_FAULT | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve FAULT | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE FAULT |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV205 | _POSITION | BB1IV205_POSITION | <IO NOT ASSIGNED> | Steam accumulator ON-OFF isolating valve POSITION | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE POSITION |  | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1IV206 | _OPEN | BB1IV206_OPEN | <IO NOT ASSIGNED> | Primary air preheater on-off valve OPEN | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN |  | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV206 | _CLOSE | BB1IV206_CLOSE | <IO NOT ASSIGNED> | Primary air preheater on-off valve CLOSE | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE |  | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE | IV | ISOLATING VALVE | DO | MTR_VLV
BB1IV206 | _OPENED | BB1IV206_OPENED | <IO NOT ASSIGNED> | Primary air preheater on-off valve OPENED | PRIMARY AIR PREHEATER | ON-OFF VALVE OPENED |  | PRIMARY AIR PREHEATER ON-OFF VALVE OPENED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _CLOSED | BB1IV206_CLOSED | <IO NOT ASSIGNED> | Primary air preheater on-off valve CLOSED | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSED |  | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSED | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _FAULT | BB1IV206_FAULT | <IO NOT ASSIGNED> | Primary air preheater on-off valve FAULT | PRIMARY AIR PREHEATER | ON-OFF VALVE FAULT |  | PRIMARY AIR PREHEATER ON-OFF VALVE FAULT | IV | ISOLATING VALVE | DI | MTR_VLV
BB1IV206 | _POSITION | BB1IV206_POSITION | <IO NOT ASSIGNED> | Primary air preheater on-off valve POSITION | PRIMARY AIR PREHEATER | ON-OFF VALVE POSITION |  | PRIMARY AIR PREHEATER ON-OFF VALVE POSITION | IV | ISOLATING VALVE | AI | MTR_VLV
BB1FM001 | _ESTOP | BB1FM001_ESTOP | <IO NOT ASSIGNED> | Bottom ash sieve feed ESTOP | BOTTOM ASH SIEVE FEED | ESTOP |  | BOTTOM ASH SIEVE FEED ESTOP | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _RUNNING | BB1FM001_RUNNING | <IO NOT ASSIGNED> | Bottom ash sieve feed RUNNING | BOTTOM ASH SIEVE FEED | RUNNING |  | BOTTOM ASH SIEVE FEED RUNNING | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _MAN_AUTO | BB1FM001_MAN_AUTO | <IO NOT ASSIGNED> | Bottom ash sieve feed MAN/AUTO | BOTTOM ASH SIEVE FEED | MAN/AUTO |  | BOTTOM ASH SIEVE FEED MAN/AUTO | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _FAULT | BB1FM001_FAULT | <IO NOT ASSIGNED> | Bottom ash sieve feed THERMAL FAULT | BOTTOM ASH SIEVE FEED | THERMAL FAULT |  | BOTTOM ASH SIEVE FEED THERMAL FAULT | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _VOLTAGE_OK | BB1FM001_VOLTAGE_OK | <IO NOT ASSIGNED> | Bottom ash sieve feed VOLTAGE OK | BOTTOM ASH SIEVE FEED | VOLTAGE OK |  | BOTTOM ASH SIEVE FEED VOLTAGE OK | FM | MOTOR | DI | OESA_3ph
BB1FM001 | _START_STOP | BB1FM001_START_STOP | <IO NOT ASSIGNED> | Bottom ash sieve feed START/STOP | BOTTOM ASH SIEVE FEED | START/STOP |  | BOTTOM ASH SIEVE FEED START/STOP | FM | MOTOR | DO | OESA_3ph
<005> |  | <005> | <IO NOT ASSIGNED> | Sand transmitter 230 Vac feed | SAND TRANSMITTER | 230 VAC FEED |  | SAND TRANSMITTER 230 VAC FEED | 5> | #N/A |  | #N/A
BB1FG300 | _ESP_COLLECTIVE_ALARM | BB1FG300_ESP_COLLECTIVE_ALARM | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_ALARM | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_COLLECTIVE_WARNING | BB1FG300_ESP_COLLECTIVE_WARNING | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_WARNING | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_IN_STANDBY | BB1FG300_ESP_IN_STANDBY | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_IN_STANDBY | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_IN_STANDBY | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_STANDBY | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_IN_OPERATION | BB1FG300_ESP_IN_OPERATION | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_IN_OPERATION | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_IN_OPERATION | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_OPERATION | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI1 | BB1FG300_ESP_SPARE_DI1 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI1 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI2 | BB1FG300_ESP_SPARE_DI2 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI2 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI3 | BB1FG300_ESP_SPARE_DI3 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI3 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DI4 | BB1FG300_ESP_SPARE_DI4 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI4 | FG | ESP | DI | ESP_DI_DO
BB1FG300 | _ESP_EXT_RELEASE_FILTER | BB1FG300_ESP_EXT_RELEASE_FILTER | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_EXT_RELEASE_FILTER | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO1 | BB1FG300_ESP_SPARE_DO1 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO1 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO2 | BB1FG300_ESP_SPARE_DO2 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO2 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO3 | BB1FG300_ESP_SPARE_DO3 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO3 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO4 | BB1FG300_ESP_SPARE_DO4 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO4 | FG | ESP | DO | ESP_DI_DO
BB1FG300 | _ESP_SPARE_DO5 | BB1FG300_ESP_SPARE_DO5 | <IO NOT ASSIGNED> | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO5 | FG | ESP | DO | ESP_DI_DO
BB1SI400 |  | BB1SI400 | <IO NOT ASSIGNED> | Primary air fan safety interlock | PRIMARY AIR FAN | SAFETY INTERLOCK |  | PRIMARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI401 |  | BB1SI401 | <IO NOT ASSIGNED> | Secondary air fan safety interlock | SECONDARY AIR FAN | SAFETY INTERLOCK |  | SECONDARY AIR FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI603 |  | BB1SI603 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI604 |  | BB1SI604 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI605 |  | BB1SI605 | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 safety interlock | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI658 |  | BB1SI658 | <IO NOT ASSIGNED> | Scraper Conveyor 1 safety interlock | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  | SCRAPER CONVEYOR 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI659 |  | BB1SI659 | <IO NOT ASSIGNED> | Belt Conveyor safety interlock | BELT CONVEYOR | SAFETY INTERLOCK |  | BELT CONVEYOR SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI675 |  | BB1SI675 | <IO NOT ASSIGNED> | Disc screen drive 1 safety interlock | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  | DISC SCREEN DRIVE 1 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI676 |  | BB1SI676 | <IO NOT ASSIGNED> | Disc screen drive 2 safety interlock | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  | DISC SCREEN DRIVE 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI672 |  | BB1SI672 | <IO NOT ASSIGNED> | Scraper Conveyor 2 safety interlock | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  | SCRAPER CONVEYOR 2 SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SI550 |  | BB1SI550 | <IO NOT ASSIGNED> | Flue gas fan safety interlock | FLUE GAS FAN | SAFETY INTERLOCK |  | FLUE GAS FAN SAFETY INTERLOCK | SI | SAFETY INTERLOCK |  | FAN_SRS_DO
BB1SV601 | _OUT | BB1SV601_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 1 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV601 | _IN | BB1SV601_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 1 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV603 | _OUT | BB1SV603_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 3 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV603 | _IN | BB1SV603_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 3 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV602 | _OUT | BB1SV602_OUT | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 2 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1SV602 | _IN | BB1SV602_IN | <IO NOT ASSIGNED> | Control Valve push feeders unloading station 2 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 | SV | SOLENOID VALVE | DO | PUSH_FEED
BB1EM603 | _LOCAL_MODE | BB1EM603_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM603 | _LOCAL_RUN | BB1EM603_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM603 | _ISOLATOR | BB1EM603_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 1 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _LOCAL_MODE | BB1EM604_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _LOCAL_RUN | BB1EM604_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM604 | _ISOLATOR | BB1EM604_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 2 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _LOCAL_MODE | BB1EM605_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_MODE | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _LOCAL_RUN | BB1EM605_LOCAL_RUN | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_RUN | EM | MOTOR | DI | FRQ_DIRH
BB1EM605 | _ISOLATOR | BB1EM605_ISOLATOR | <IO NOT ASSIGNED> | Fuel reception hydraulic unit 1, pump 3 ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 ISOLATOR | EM | MOTOR | DI | FRQ_DIRH
BB1EM658 | _LOCAL_MODE | BB1EM658_LOCAL_MODE | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  | SCRAPER CONVEYOR 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _LOCAL_RUN_FWD | BB1EM658_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _LOCAL_RUN_REV | BB1EM658_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 LOCAL_RUN_REV | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  | SCRAPER CONVEYOR 1 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM658 | _ISOLATOR | BB1EM658_ISOLATOR | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 1 ISOLATOR | SCRAPER CONVEYOR 1 | ISOLATOR |  | SCRAPER CONVEYOR 1 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_MODE | BB1EM659_LOCAL_MODE | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_MODE | BELT CONVEYOR | LOCAL_MODE |  | BELT CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_RUN_FWD | BB1EM659_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_RUN_FWD | BELT CONVEYOR | LOCAL_RUN_FWD |  | BELT CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _LOCAL_RUN_REV | BB1EM659_LOCAL_RUN_REV | <IO NOT ASSIGNED> | BELT CONVEYOR LOCAL_RUN_REV | BELT CONVEYOR | LOCAL_RUN_REV |  | BELT CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM659 | _ISOLATOR | BB1EM659_ISOLATOR | <IO NOT ASSIGNED> | BELT CONVEYOR ISOLATOR | BELT CONVEYOR | ISOLATOR |  | BELT CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM675 | _LOCAL_MODE | BB1EM675_LOCAL_MODE | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_MODE | DISC SCREEN DRIVE 1 | LOCAL_MODE |  | DISC SCREEN DRIVE 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _LOCAL_RUN_FWD | BB1EM675_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD | DISC SCREEN DRIVE 1 | LOCAL_RUN_FWD |  | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _LOCAL_RUN_REV | BB1EM675_LOCAL_RUN_REV | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 LOCAL_RUN_REV | DISC SCREEN DRIVE 1 | LOCAL_RUN_REV |  | DISC SCREEN DRIVE 1 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM675 | _ISOLATOR | BB1EM675_ISOLATOR | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 1 ISOLATOR | DISC SCREEN DRIVE 1 | ISOLATOR |  | DISC SCREEN DRIVE 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM676 | _LOCAL_MODE | BB1EM676_LOCAL_MODE | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_MODE | DISC SCREEN DRIVE 2 | LOCAL_MODE |  | DISC SCREEN DRIVE 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _LOCAL_RUN_FWD | BB1EM676_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _LOCAL_RUN_REV | BB1EM676_LOCAL_RUN_REV | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 LOCAL_RUN_REV | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  | DISC SCREEN DRIVE 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM676 | _ISOLATOR | BB1EM676_ISOLATOR | <IO NOT ASSIGNED> | DISC SCREEN DRIVE 2 ISOLATOR | DISC SCREEN DRIVE 2 | ISOLATOR |  | DISC SCREEN DRIVE 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_MODE | BB1EM672_LOCAL_MODE | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_MODE | SCRAPER CONVEYOR 2 | LOCAL_MODE |  | SCRAPER CONVEYOR 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_RUN_FWD | BB1EM672_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _LOCAL_RUN_REV | BB1EM672_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 LOCAL_RUN_REV | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  | SCRAPER CONVEYOR 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM672 | _ISOLATOR | BB1EM672_ISOLATOR | <IO NOT ASSIGNED> | SCRAPER CONVEYOR 2 ISOLATOR | SCRAPER CONVEYOR 2 | ISOLATOR |  | SCRAPER CONVEYOR 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_MODE | BB1EM662_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_MODE | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  | FUEL SILO SCREW DISCHARGE LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_RUN_FWD | BB1EM662_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  | FUEL SILO SCREW DISCHARGE LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _LOCAL_RUN_REV | BB1EM662_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGELOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  | FUEL SILO SCREW DISCHARGE LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM662 | _ISOLATOR | BB1EM662_ISOLATOR | <IO NOT ASSIGNED> | FUEL SILO SCREW DISCHARGEISOLATOR | FUEL SILO SCREW DISCHARGE | ISOLATOR |  | FUEL SILO SCREW DISCHARGE ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_MODE | BB1EM650_LOCAL_MODE | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_MODE | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  | SLEWING MOTOR FOR SCREW LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_RUN_FWD | BB1EM650_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _LOCAL_RUN_REV | BB1EM650_LOCAL_RUN_REV | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM650 | _ISOLATOR | BB1EM650_ISOLATOR | <IO NOT ASSIGNED> | SLEWING MOTOR FOR SCREW ISOLATOR | SLEWING MOTOR FOR SCREW | ISOLATOR |  | SLEWING MOTOR FOR SCREW ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_MODE | BB1EM663_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_MODE | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  | FUEL SILO CROSS CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_RUN_FWD | BB1EM663_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _LOCAL_RUN_REV | BB1EM663_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM663 | _ISOLATOR | BB1EM663_ISOLATOR | <IO NOT ASSIGNED> | FUEL SILO CROSS CONVEYOR ISOLATOR | FUEL SILO CROSS CONVEYOR | ISOLATOR |  | FUEL SILO CROSS CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_MODE | BB1EM664_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_MODE | FUEL FEEDING SCREW 1 | LOCAL_MODE |  | FUEL FEEDING SCREW 1 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_RUN_FWD | BB1EM664_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _LOCAL_RUN_REV | BB1EM664_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 LOCAL_RUN_REV | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  | FUEL FEEDING SCREW 1 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM664 | _ISOLATOR | BB1EM664_ISOLATOR | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 1 ISOLATOR | FUEL FEEDING SCREW 1 | ISOLATOR |  | FUEL FEEDING SCREW 1 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_MODE | BB1EM665_LOCAL_MODE | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_MODE | FUEL FEEDING SCREW 2 | LOCAL_MODE |  | FUEL FEEDING SCREW 2 LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_RUN_FWD | BB1EM665_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _LOCAL_RUN_REV | BB1EM665_LOCAL_RUN_REV | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 LOCAL_RUN_REV | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  | FUEL FEEDING SCREW 2 LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM665 | _ISOLATOR | BB1EM665_ISOLATOR | <IO NOT ASSIGNED> | FUEL FEEDING SCREW 2 ISOLATOR | FUEL FEEDING SCREW 2 | ISOLATOR |  | FUEL FEEDING SCREW 2 ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_MODE | BB1EM852_LOCAL_MODE | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_MODE | BOTTOM ASH CONVEYOR | LOCAL_MODE |  | BOTTOM ASH CONVEYOR LOCAL_MODE | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_RUN_FWD | BB1EM852_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _LOCAL_RUN_REV | BB1EM852_LOCAL_RUN_REV | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR LOCAL_RUN_REV | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  | BOTTOM ASH CONVEYOR LOCAL_RUN_REV | EM | MOTOR | DI | FRQ_REVH
BB1EM852 | _ISOLATOR | BB1EM852_ISOLATOR | <IO NOT ASSIGNED> | BOTTOM ASH CONVEYOR ISOLATOR | BOTTOM ASH CONVEYOR | ISOLATOR |  | BOTTOM ASH CONVEYOR ISOLATOR | EM | MOTOR | DI | FRQ_REVH
BB1EM660 | _RUNNING | BB1EM660_RUNNING | <IO NOT ASSIGNED> | Cooling fan for slewing motor RUNNING | COOLING FAN FOR | SLEWING MOTOR RUNNING |  | COOLING FAN FOR SLEWING MOTOR RUNNING | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM660 | _FAULT | BB1EM660_FAULT | <IO NOT ASSIGNED> | Cooling fan for slewing motor FAULT | COOLING FAN FOR | SLEWING MOTOR FAULT |  | COOLING FAN FOR SLEWING MOTOR FAULT | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM660 | _RUN | BB1EM660_RUN | <IO NOT ASSIGNED> | Cooling fan for slewing motor RUN | COOLING FAN FOR | SLEWING MOTOR RUN |  | COOLING FAN FOR SLEWING MOTOR RUN | EM | MOTOR | DO | DOL_DIR_BUS
BB1EM660 | _ISOLATOR | BB1EM660_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan for slewing motor ISOLATOR | COOLING FAN FOR | SLEWING MOTOR ISOLATOR |  | COOLING FAN FOR SLEWING MOTOR ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM654 | _RUNNING | BB1EM654_RUNNING | <IO NOT ASSIGNED> | Lubrication unit RUNNING | LUBRICATION UNIT RUNNING |  |  | LUBRICATION UNIT RUNNING | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM654 | _FAULT | BB1EM654_FAULT | <IO NOT ASSIGNED> | Lubrication unit FAULT | LUBRICATION UNIT FAULT |  |  | LUBRICATION UNIT FAULT | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM654 | _RUN | BB1EM654_RUN | <IO NOT ASSIGNED> | Lubrication unit RUN | LUBRICATION UNIT RUN |  |  | LUBRICATION UNIT RUN | EM | MOTOR | DO | DOL_DIR_BUS
BB1EM654 | _ISOLATOR | BB1EM654_ISOLATOR | <IO NOT ASSIGNED> | Lubrication unit ISOLATOR | LUBRICATION UNIT ISOLATOR |  |  | LUBRICATION UNIT ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM653 | _RUNNING | BB1EM653_RUNNING | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 RUNNING | COOLING FAN FUEL | FEEDING SCREW 1 RUNNING |  | COOLING FAN FUEL FEEDING SCREW 1 RUNNING | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM653 | _FAULT | BB1EM653_FAULT | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 FAULT | COOLING FAN FUEL | FEEDING SCREW 1 FAULT |  | COOLING FAN FUEL FEEDING SCREW 1 FAULT | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM653 | _RUN | BB1EM653_RUN | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 RUN | COOLING FAN FUEL | FEEDING SCREW 1 RUN |  | COOLING FAN FUEL FEEDING SCREW 1 RUN | EM | MOTOR | DO | DOL_DIR_BUS
BB1EM653 | _ISOLATOR | BB1EM653_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 1 ISOLATOR | COOLING FAN FUEL | FEEDING SCREW 1 ISOLATOR |  | COOLING FAN FUEL FEEDING SCREW 1 ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM655 | _RUNNING | BB1EM655_RUNNING | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 RUNNING | COOLING FAN FUEL | FEEDING SCREW 2 RUNNING |  | COOLING FAN FUEL FEEDING SCREW 2 RUNNING | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM655 | _FAULT | BB1EM655_FAULT | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 FAULT | COOLING FAN FUEL | FEEDING SCREW 2 FAULT |  | COOLING FAN FUEL FEEDING SCREW 2 FAULT | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM655 | _RUN | BB1EM655_RUN | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 RUN | COOLING FAN FUEL | FEEDING SCREW 2 RUN |  | COOLING FAN FUEL FEEDING SCREW 2 RUN | EM | MOTOR | DO | DOL_DIR_BUS
BB1EM655 | _ISOLATOR | BB1EM655_ISOLATOR | <IO NOT ASSIGNED> | Cooling fan fuel feeding screw 2 ISOLATOR | COOLING FAN FUEL | FEEDING SCREW 2 ISOLATOR |  | COOLING FAN FUEL FEEDING SCREW 2 ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM606 | _ISOLATOR | BB1EM606_ISOLATOR | <IO NOT ASSIGNED> | Dust extraction fan ISOLATOR | DUST EXTRACTION FAN | ISOLATOR |  | DUST EXTRACTION FAN ISOLATOR | EM | MOTOR | DI | FRQ_DIR
BB1EH600 | _ISOLATOR | BB1EH600_ISOLATOR | <IO NOT ASSIGNED> | Electric heater hydraulic unit ISOLATOR | ELECTRIC HEATER | HYDRAULIC UNIT ISOLATOR |  | ELECTRIC HEATER HYDRAULIC UNIT ISOLATOR | EH | HEATER | DI | DOL_DIR_BUS
BB1EM651 | _ISOLATOR | BB1EM651_ISOLATOR | <IO NOT ASSIGNED> | Fuel silo dust filter fanISOLATOR | FUEL SILO DUST FILTER FAN | ISOLATOR |  | FUEL SILO DUST FILTER FAN ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM008 | _ISOLATOR | BB1EM008_ISOLATOR | <IO NOT ASSIGNED> | Conveyor cooling pump ISOLATOR | CONVEYOR COOLING PUMP | ISOLATOR |  | CONVEYOR COOLING PUMP ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM009 | _ISOLATOR | BB1EM009_ISOLATOR | <IO NOT ASSIGNED> | Bottom ash conveyor heat exchanger fan ISOLATOR | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN ISOLAT | OR | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN ISOLAT OR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM408 | _ISOLATOR | BB1EM408_ISOLATOR | <IO NOT ASSIGNED> | Boiler house heater 1 ISOLATOR | BOILER HOUSE HEATER 1 | ISOLATOR |  | BOILER HOUSE HEATER 1 ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM409 | _ISOLATOR | BB1EM409_ISOLATOR | <IO NOT ASSIGNED> | Boiler house heater 2 ISOLATOR | BOILER HOUSE HEATER 2 | ISOLATOR |  | BOILER HOUSE HEATER 2 ISOLATOR | EM | MOTOR | DI | DOL_DIR_BUS
BB1EM703 | _RUNNING | BB1EM703_RUNNING | <IO NOT ASSIGNED> | Chemical filling pump 1 RUNNING | CHEMICAL FILLING PUMP 1 | RUNNING |  | CHEMICAL FILLING PUMP 1 RUNNING | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM703 | _FAULT | BB1EM703_FAULT | <IO NOT ASSIGNED> | Chemical filling pump 1 FAULT | CHEMICAL FILLING PUMP 1 | FAULT |  | CHEMICAL FILLING PUMP 1 FAULT | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM703 | _RUN | BB1EM703_RUN | <IO NOT ASSIGNED> | Chemical filling pump 1 RUN | CHEMICAL FILLING PUMP 1 | RUN |  | CHEMICAL FILLING PUMP 1 RUN | EM | MOTOR | DO | DOL_DIRH_BUS
BB1EM703 | _LOCAL_MODE | BB1EM703_LOCAL_MODE | <IO NOT ASSIGNED> | Chemical filling pump 1 LOCAL_MODE | CHEMICAL FILLING PUMP 1 | LOCAL_MODE |  | CHEMICAL FILLING PUMP 1 LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM703 | _LOCAL_RUN | BB1EM703_LOCAL_RUN | <IO NOT ASSIGNED> | Chemical filling pump 1 LOCAL_RUN | CHEMICAL FILLING PUMP 1 | LOCAL_RUN |  | CHEMICAL FILLING PUMP 1 LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM703 | _ISOLATOR | BB1EM703_ISOLATOR | <IO NOT ASSIGNED> | Chemical filling pump 1 ISOLATOR | CHEMICAL FILLING PUMP 1 | ISOLATOR |  | CHEMICAL FILLING PUMP 1 ISOLATOR | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM704 | _RUNNING | BB1EM704_RUNNING | <IO NOT ASSIGNED> | Chemical filling pump 2 RUNNING | CHEMICAL FILLING PUMP 2 | RUNNING |  | CHEMICAL FILLING PUMP 2 RUNNING | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM704 | _FAULT | BB1EM704_FAULT | <IO NOT ASSIGNED> | Chemical filling pump 2 FAULT | CHEMICAL FILLING PUMP 2 | FAULT |  | CHEMICAL FILLING PUMP 2 FAULT | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM704 | _RUN | BB1EM704_RUN | <IO NOT ASSIGNED> | Chemical filling pump 2 RUN | CHEMICAL FILLING PUMP 2 | RUN |  | CHEMICAL FILLING PUMP 2 RUN | EM | MOTOR | DO | DOL_DIRH_BUS
BB1EM704 | _LOCAL_MODE | BB1EM704_LOCAL_MODE | <IO NOT ASSIGNED> | Chemical filling pump 2 LOCAL_MODE | CHEMICAL FILLING PUMP 2 | LOCAL_MODE |  | CHEMICAL FILLING PUMP 2 LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM704 | _LOCAL_RUN | BB1EM704_LOCAL_RUN | <IO NOT ASSIGNED> | Chemical filling pump 2 LOCAL_RUN | CHEMICAL FILLING PUMP 2 | LOCAL_RUN |  | CHEMICAL FILLING PUMP 2 LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM704 | _ISOLATOR | BB1EM704_ISOLATOR | <IO NOT ASSIGNED> | Chemical filling pump 2 ISOLATOR | CHEMICAL FILLING PUMP 2 | ISOLATOR |  | CHEMICAL FILLING PUMP 2 ISOLATOR | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM670 | _LOCAL_MODE | BB1EM670_LOCAL_MODE | <IO NOT ASSIGNED> | Belt magnet LOCAL_MODE | BELT MAGNET LOCAL_MODE |  |  | BELT MAGNET LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM670 | _LOCAL_RUN | BB1EM670_LOCAL_RUN | <IO NOT ASSIGNED> | Belt magnet LOCAL_RUN | BELT MAGNET LOCAL_RUN |  |  | BELT MAGNET LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM670 | _ISOLATOR | BB1EM670_ISOLATOR | <IO NOT ASSIGNED> | Belt magnet ISOLATOR | BELT MAGNET ISOLATOR |  |  | BELT MAGNET ISOLATOR | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _LOCAL_MODE | BB1EM652_LOCAL_MODE | <IO NOT ASSIGNED> | Rotating fuel spreader LOCAL_MODE | ROTATING FUEL SPREADER | LOCAL_MODE |  | ROTATING FUEL SPREADER LOCAL_MODE | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _LOCAL_RUN | BB1EM652_LOCAL_RUN | <IO NOT ASSIGNED> | Rotating fuel spreader LOCAL_RUN | ROTATING FUEL SPREADER | LOCAL_RUN |  | ROTATING FUEL SPREADER LOCAL_RUN | EM | MOTOR | DI | DOL_DIRH_BUS
BB1EM652 | _ISOLATOR | BB1EM652_ISOLATOR | <IO NOT ASSIGNED> | Rotating fuel spreader ISOLATOR | ROTATING FUEL SPREADER | ISOLATOR |  | ROTATING FUEL SPREADER ISOLATOR | EM | MOTOR | DI | DOL_DIRH_BUS
BB1BL200 | _ISOLATOR | BB1BL200_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 1 ISOLATOR | SOOTBLOWER 1 ISOLATOR |  |  | SOOTBLOWER 1 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL201 | _ISOLATOR | BB1BL201_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 2 ISOLATOR | SOOTBLOWER 2 ISOLATOR |  |  | SOOTBLOWER 2 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL202 | _ISOLATOR | BB1BL202_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 3 ISOLATOR | SOOTBLOWER 3 ISOLATOR |  |  | SOOTBLOWER 3 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL203 | _ISOLATOR | BB1BL203_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 4 ISOLATOR | SOOTBLOWER 4 ISOLATOR |  |  | SOOTBLOWER 4 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL204 | _ISOLATOR | BB1BL204_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 5 ISOLATOR | SOOTBLOWER 5 ISOLATOR |  |  | SOOTBLOWER 5 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL205 | _ISOLATOR | BB1BL205_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 6 ISOLATOR | SOOTBLOWER 6 ISOLATOR |  |  | SOOTBLOWER 6 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1BL206 | _ISOLATOR | BB1BL206_ISOLATOR | <IO NOT ASSIGNED> | Sootblower 7 ISOLATOR | SOOTBLOWER 7 ISOLATOR |  |  | SOOTBLOWER 7 ISOLATOR | BL | BLOWER | DI | DOL_REV_BUS
BB1EM815 | _ISOLATOR | BB1EM815_ISOLATOR | <IO NOT ASSIGNED> | Fly ash container screw ISOLATOR | FLY ASH CONTAINER SCREW I | SOLATOR |  | FLY ASH CONTAINER SCREW I SOLATOR | EM | MOTOR | DI | DOL_REV_BUS
BB1EM855 | _ISOLATOR | BB1EM855_ISOLATOR | <IO NOT ASSIGNED> | Ash container screw ISOLATOR | ASH CONTAINER SCREW ISOLA | TOR |  | ASH CONTAINER SCREW ISOLA TOR | EM | MOTOR | DI | DOL_REV_BUS
BB1EM401 | _ISOLATOR | BB1EM401_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 1 ISOLATOR | EXHAUST FAN 1 ISOLATOR |  |  | EXHAUST FAN 1 ISOLATOR | EM | MOTOR | DI | FRQ_DIR
BB1EM402 |  | BB1EM402 | <IO NOT ASSIGNED> | Exhaust fan 2 | EXHAUST FAN 2 |  |  | EXHAUST FAN 2 | EM | MOTOR | DO | COMPR
BB1EM402 | _ISOLATOR | BB1EM402_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 2 ISOLATOR | EXHAUST FAN 2 ISOLATOR |  |  | EXHAUST FAN 2 ISOLATOR | EM | MOTOR | DO | COMPR
BB1EM403 |  | BB1EM403 | <IO NOT ASSIGNED> | Exhaust fan 3 | EXHAUST FAN 3 |  |  | EXHAUST FAN 3 | EM | MOTOR | DO | COMPR
BB1EM403 | _ISOLATOR | BB1EM403_ISOLATOR | <IO NOT ASSIGNED> | Exhaust fan 3 ISOLATOR | EXHAUST FAN 3 ISOLATOR |  |  | EXHAUST FAN 3 ISOLATOR | EM | MOTOR | DO | COMPR
BB1EM673 | _LOCAL_MODE | BB1EM673_LOCAL_MODE | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_MODE | LEVELLING ROLLER 1 | LOCAL_MODE |  | LEVELLING ROLLER 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _LOCAL_RUN_FWD | BB1EM673_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_RUN_FWD | LEVELLING ROLLER 1 | LOCAL_RUN_FWD |  | LEVELLING ROLLER 1 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _LOCAL_RUN_REV | BB1EM673_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Levelling roller 1 LOCAL_RUN_REV | LEVELLING ROLLER 1 | LOCAL_RUN_REV |  | LEVELLING ROLLER 1 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM673 | _ISOLATOR | BB1EM673_ISOLATOR | <IO NOT ASSIGNED> | Levelling roller 1 ISOLATOR | LEVELLING ROLLER 1 | ISOLATOR |  | LEVELLING ROLLER 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_MODE | BB1EM674_LOCAL_MODE | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_MODE | LEVELLING ROLLER 2 | LOCAL_MODE |  | LEVELLING ROLLER 2 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_RUN_FWD | BB1EM674_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_RUN_FWD | LEVELLING ROLLER 2 | LOCAL_RUN_FWD |  | LEVELLING ROLLER 2 LOCAL_RUN_FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _LOCAL_RUN_REV | BB1EM674_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Levelling roller 2 LOCAL_RUN_REV | LEVELLING ROLLER 2 | LOCAL_RUN_REV |  | LEVELLING ROLLER 2 LOCAL_RUN_REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM674 | _ISOLATOR | BB1EM674_ISOLATOR | <IO NOT ASSIGNED> | Levelling roller 2 ISOLATOR | LEVELLING ROLLER 2 | ISOLATOR |  | LEVELLING ROLLER 2 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_MODE | BB1EM601_LOCAL_MODE | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_MODE | DUST EXTRACTION | ROTARY FEEDER LOCAL_MODE |  | DUST EXTRACTION ROTARY FEEDER LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_RUN_FWD | BB1EM601_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_RUN_FWD | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_F | WD | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_F WD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _LOCAL_RUN_REV | BB1EM601_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Dust extraction rotary feeder LOCAL_RUN_REV | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_R | EV | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_R EV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM601 | _ISOLATOR | BB1EM601_ISOLATOR | <IO NOT ASSIGNED> | Dust extraction rotary feeder ISOLATOR | DUST EXTRACTION | ROTARY FEEDER ISOLATOR |  | DUST EXTRACTION ROTARY FEEDER ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_MODE | BB1IV650_LOCAL_MODE | <IO NOT ASSIGNED> | Slide gate valve LOCAL_MODE | SLIDE GATE VALVE | LOCAL_MODE |  | SLIDE GATE VALVE LOCAL_MODE | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_RUN_FWD | BB1IV650_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Slide gate valve LOCAL_RUN_FWD | SLIDE GATE VALVE | LOCAL_RUN_FWD |  | SLIDE GATE VALVE LOCAL_RUN_FWD | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _LOCAL_RUN_REV | BB1IV650_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Slide gate valve LOCAL_RUN_REV | SLIDE GATE VALVE | LOCAL_RUN_REV |  | SLIDE GATE VALVE LOCAL_RUN_REV | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1IV650 | _ISOLATOR | BB1IV650_ISOLATOR | <IO NOT ASSIGNED> | Slide gate valve ISOLATOR | SLIDE GATE VALVE | ISOLATOR |  | SLIDE GATE VALVE ISOLATOR | IV | ISOLATING VALVE | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_MODE | BB1EM657_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 1 LOCAL_MODE |  | FUEL FEEDING ROTARY VALVE 1 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_RUN_FWD | BB1EM657_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | FWD | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _LOCAL_RUN_REV | BB1EM657_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 LOCAL_RUN_REV | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | REV | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM657 | _ISOLATOR | BB1EM657_ISOLATOR | <IO NOT ASSIGNED> | Fuel feeding rotary valve 1 ISOLATOR | FUEL FEEDING | ROTARY VALVE 1 ISOLATOR |  | FUEL FEEDING ROTARY VALVE 1 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_MODE | BB1EM656_LOCAL_MODE | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 2 LOCAL_MODE |  | FUEL FEEDING ROTARY VALVE 2 LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_RUN_FWD | BB1EM656_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | FWD | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _LOCAL_RUN_REV | BB1EM656_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 LOCAL_RUN_REV | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | REV | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM656 | _ISOLATOR | BB1EM656_ISOLATOR | <IO NOT ASSIGNED> | Fuel feeding rotary valve 2 ISOLATOR | FUEL FEEDING | ROTARY VALVE 2 ISOLATOR |  | FUEL FEEDING ROTARY VALVE 2 ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_MODE | BB1EM856_LOCAL_MODE | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_MODE | PURIFIED SAND | SCREW CONVEYOR LOCAL_MODE |  | PURIFIED SAND SCREW CONVEYOR LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_RUN_FWD | BB1EM856_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_RUN_FWD | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | FWD | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _LOCAL_RUN_REV | BB1EM856_LOCAL_RUN_REV | <IO NOT ASSIGNED> | Purified sand screw conveyor LOCAL_RUN_REV | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | REV | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM856 | _ISOLATOR | BB1EM856_ISOLATOR | <IO NOT ASSIGNED> | Purified sand screw conveyor ISOLATOR | PURIFIED SAND | SCREW CONVEYOR ISOLATOR |  | PURIFIED SAND SCREW CONVEYOR ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_MODE | BB1EM850_LOCAL_MODE | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_MODE | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  | 2ND PASS FLY ASH ROTARY VALVE LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_RUN_FWD | BB1EM850_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_RUN_ FWD | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _LOCAL_RUN_REV | BB1EM850_LOCAL_RUN_REV | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve LOCAL_RUN_ REV | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | REV | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM850 | _ISOLATOR | BB1EM850_ISOLATOR | <IO NOT ASSIGNED> | 2nd pass fly ash rotary valve ISOLATOR | 2ND PASS FLY ASH | ROTARY VALVE ISOLATOR |  | 2ND PASS FLY ASH ROTARY VALVE ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_MODE | BB1EM851_LOCAL_MODE | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_MODE | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  | 3RD PASS FLY ASH ROTARY VALVE LOCAL_MODE | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_RUN_FWD | BB1EM851_LOCAL_RUN_FWD | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_RUN_ FWD | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _LOCAL_RUN_REV | BB1EM851_LOCAL_RUN_REV | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve LOCAL_RUN_ REV | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | REV | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV | EM | MOTOR | DI | DOL_REVH_BUS
BB1EM851 | _ISOLATOR | BB1EM851_ISOLATOR | <IO NOT ASSIGNED> | 3rd pass fly ash rotary valve ISOLATOR | 3RD PASS FLY ASH | ROTARY VALVE ISOLATOR |  | 3RD PASS FLY ASH ROTARY VALVE ISOLATOR | EM | MOTOR | DI | DOL_REVH_BUS
|  | <BB1TX001> | <IO NOT ASSIGNED> | BIOMASS BOILER SITE TRANSFORMER | BIOMASS BOILER | SITE TRANSFORMER |  | BIOMASS BOILER SITE TRANSFORMER |  | 0 |  | #N/A
|  | <BB1SA001> | <IO NOT ASSIGNED> | SUREGE ARRESTOR | SUREGE ARRESTOR |  |  | SUREGE ARRESTOR |  | 0 |  | #N/A

## C_CABLE
Cables
_Tag | _Drawing | _Typical | _Panel | _Tier | _Device1 | _Device2 | _Device3 | CableName1 | Cable1CatN | Cable1CatD | CableName2 | Cable2CatN | Cable2CatD | CableName3 | Cable3CatN | Cable3CatD | CableName4 | Cable4CatN | Cable4CatD
DETAIL | 01-100._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-101._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-102._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-103._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-104._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-105._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-106._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-107._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-108._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
DETAIL | 01-109._L0 |  | <KPA_MCC> | / | #N/A | #N/A | #N/A
BB1EM001 | 01-500._L0 |  | <KPA_MCC> | /T5R/2 | BB1EM001_VSD | 0 | BB1EM001 | <KPA_MCC>/T5R/2 BB1EM001 | 70-3C+E | 70mm^2 - 3C+E | <KPA_MCC>/T5R/2 BB1EM001_VSD/1 | 70-3C+E-V | 70mm^2 - 3C+E - VSD |  |  |  | BB1EM001/TH
BB1EM002 | 01-501._L0 |  | <KPA_MCC> | /T4F/4 | BB1EM002_VSD | 0 | BB1EM002 | <KPA_MCC>/T4F/4 BB1EM002 | 70-3C+E | 70mm^2 - 3C+E | <KPA_MCC>/T4F/4 BB1EM002_VSD/1 | 70-3C+E-V | 70mm^2 - 3C+E - VSD |  |  |  | BB1EM002/TH
BB1EM400 | 01-502._L0 |  | <KPA_MCC> | /T5R/1 | BB1EM400_VSD | 0 | BB1EM400 | <KPA_MCC>/T5R/1 BB1EM400 | 150-3C+E | 150mm^2 - 3C+E | <KPA_MCC>/T5R/1 BB1EM400_VSD/1 | 150-3C+E-V | 150mm^2 - 3C+E - VSD |  |  |  | BB1EM400/TH
BB1EM401 | 01-503._L0 |  | <KPA_MCC> | /T5R/3 | BB1EM401_VSD | 0 | BB1EM401 | <KPA_MCC>/T5R/3 BB1EM401 | 25-3C+E | 25mm^2 - 3C+E | <KPA_MCC>/T5R/3 BB1EM401_VSD/1 | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | BB1EM401/TH
BB1EM550 | 01-504._L0 |  | <KPA_MCC> | /T1F/2 | BB1EM550_VSD | 0 | BB1EM550 | <KPA_MCC>/T1F/2 BB1EM550 | 70-3C+E | 70mm^2 - 3C+E | <KPA_MCC>/T1F/2 BB1EM550_VSD/1 | 70-3C+E-V | 70mm^2 - 3C+E - VSD |  |  |  | BB1EM550/TH
BB1EM603 | 01-505._L0 |  | <KPA_MCC> | /T1F/3 | BB1EM603_VSD | 0 | BB1EM603 | <KPA_MCC>/T1F/3 BB1EM603 | 25-3C+E | 25mm^2 - 3C+E | <KPA_MCC>/T1F/3 BB1EM603_VSD/1 | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | BB1EM603/TH
BB1EM604 | 01-506._L0 |  | <KPA_MCC> | /T1F/4 | BB1EM604_VSD | 0 | BB1EM604 | <KPA_MCC>/T1F/4 BB1EM604 | 25-3C+E | 25mm^2 - 3C+E | <KPA_MCC>/T1F/4 BB1EM604_VSD/1 | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | BB1EM604/TH
BB1EM605 | 01-507._L0 |  | <KPA_MCC> | /T1F/5 | BB1EM605_VSD | 0 | BB1EM605 | <KPA_MCC>/T1F/5 BB1EM605 | 25-3C+E | 25mm^2 - 3C+E | <KPA_MCC>/T1F/5 BB1EM605_VSD/1 | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | BB1EM605/TH
BB1EM658 | 01-508._L0 |  | <KPA_MCC> | /T4F/5 | BB1EM658_VSD | BB1EM658 | BB1EM658 | <KPA_MCC>/T4F/5 BB1EM658 | 10-3C+E | 10mm^2 - 3C+E | <KPA_MCC>/T4F/5 BB1EM658_VSD/1 | 10-3C+E-V | 10mm^2 - 3C+E - VSD | <KPA_MCC>/T4F/5 BB1EM658_VSD/2 | 10-3C+E-V | 10mm^2 - 3C+E - VSD | BB1EM658/TH
BB1EM659 | 01-509._L0 |  | <KPA_MCC> | /T1R | BB1EM659_VSD | BB1EM659 | BB1EM659 | <KPA_MCC>/T1R BB1EM659 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T1R BB1EM659_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T1R BB1EM659_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM659/TH
BB1EM676 | 01-510._L0 |  | <KPA_MCC> | /T1R | BB1EM676_VSD | BB1EM676 | BB1EM676 | <KPA_MCC>/T1R BB1EM676 | 4-3C+E | 4mm^2 - 3C+E | <KPA_MCC>/T1R BB1EM676_VSD/1 | 4-3C+E-V | 4mm^2 - 3C+E - VSD | <KPA_MCC>/T1R BB1EM676_VSD/2 | 4-3C+E-V | 4mm^2 - 3C+E - VSD | BB1EM676/TH
BB1EM672 | 01-511._L0 |  | <KPA_MCC> | /T4F/6 | BB1EM672_VSD | BB1EM672 | BB1EM672 | <KPA_MCC>/T4F/6 BB1EM672 | 10-3C+E | 10mm^2 - 3C+E | <KPA_MCC>/T4F/6 BB1EM672_VSD/1 | 10-3C+E-V | 10mm^2 - 3C+E - VSD | <KPA_MCC>/T4F/6 BB1EM672_VSD/2 | 10-3C+E-V | 10mm^2 - 3C+E - VSD | BB1EM672/TH
BB1EM662 | 01-512._L0 |  | <KPA_MCC> | /T4F/7 | BB1EM662_VSD | BB1EM662 | BB1EM662 | <KPA_MCC>/T4F/7 BB1EM662 | 16-3C+E | 16mm^2 - 3C+E | <KPA_MCC>/T4F/7 BB1EM662_VSD/1 | 16-3C+E-V | 16mm^2 - 3C+E - VSD | <KPA_MCC>/T4F/7 BB1EM662_VSD/2 | 16-3C+E-V | 16mm^2 - 3C+E - VSD | BB1EM662/TH
BB1EM650 | 01-513._L0 |  | <KPA_MCC> | /T1R | BB1EM650_VSD | BB1EM650 | BB1EM650 | <KPA_MCC>/T1R BB1EM650 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T1R BB1EM650_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T1R BB1EM650_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM650/TH
BB1EM663 | 01-514._L0 |  | <KPA_MCC> | /T4R | BB1EM663_VSD | BB1EM663 | BB1EM663 | <KPA_MCC>/T4R BB1EM663 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T4R BB1EM663_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T4R BB1EM663_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM663/TH
BB1EM664 | 01-515._L0 |  | <KPA_MCC> | /T4R | BB1EM664_VSD | BB1EM664 | BB1EM664 | <KPA_MCC>/T4R BB1EM664 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T4R BB1EM664_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T4R BB1EM664_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM664/TH
BB1EM665 | 01-516._L0 |  | <KPA_MCC> | /T4R | BB1EM665_VSD | BB1EM665 | BB1EM665 | <KPA_MCC>/T4R BB1EM665 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T4R BB1EM665_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T4R BB1EM665_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM665/TH
BB1EM852 | 01-517._L0 |  | <KPA_MCC> | /T4R | BB1EM852_VSD | BB1EM852 | BB1EM852 | <KPA_MCC>/T4R BB1EM852 | 2.5-3C+E | 2.5mm^2 - 3C+E | <KPA_MCC>/T4R BB1EM852_VSD/1 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | <KPA_MCC>/T4R BB1EM852_VSD/2 | 2.5-3C+E-V | 2.5mm^2 - 3C+E - VSD | BB1EM852/TH
BB1EM606 | 01-518._L0 |  | <KPA_MCC> | /T5R/4 | BB1EM606_VSD | 0 | BB1EM606 | <KPA_MCC>/T5R/4 BB1EM606 | 16-3C+E | 16mm^2 - 3C+E | <KPA_MCC>/T5R/4 BB1EM606_VSD/1 | 16-3C+E-V | 16mm^2 - 3C+E - VSD |  |  |  | BB1EM606/TH
0 | 01-519._L0 |  | #REF! | #REF! | #N/A | #N/A | #N/A | #REF! | 25-3C+E | 25mm^2 - 3C+E | #REF! | 25-3C+E-V | 25mm^2 - 3C+E - VSD |  |  |  | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A |  | X-3C+E | XXXmm^2 - 3C+E |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD |  | X-3C+E-V | XXXmm^2 - 3C+E - VSD
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
0 | 01-._L0 |  | KPA_FLOORX_IO | / | #N/A | #N/A | #N/A
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | KPA_FLOORX_IO | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!
#VALUE! | #VALUE! |  | 0 | / | #VALUE! | #VALUE! | #VALUE!

## _LookupTables
Code | Type
IL | ALARM |  | Channel | IOTerminal | Type | CatN | CatD2 | CatD | ChannelIndex | LoopNameA | LoopTerminalA | LoopNameB | LoopTerminalB | GndName | GndTerminal | MaxIndex | T1 | T2 | T3 | T1Type | T2Type | T3Type
IJ | ALARM |  | 0 | 0 | DI | 1734-IB4D*M1 | Digital Input 1 (00,01) | 1734-IB4D | 0 | V+ | 1 | [5 empty] | V+ | 0 |  | 24VDC | DI
EM | MOTOR |  | 1 | 2 | DI | 1734-IB4D*M2 | Digital Input 2 (02,03) | 1734-IB4D | 1 | V+ | 3 | [5 empty] | V+ | 1 |  | 24VDC | DI
GS | GATE SWITCH |  | 2 | 4 | DI | 1734-IB4D*M3 | Digital Input 3 (04,05) | 1734-IB4D | 2 | V+ | 5 | [5 empty] | V+ | 2 |  | 24VDC | DI
SV | SOLENOID VALVE |  | 3 | 6 | DI | 1734-IB4D*M4 | Digital Input 4 (06,07) | 1734-IB4D | 3 | V+ | 7 |  |  |  |  | TRUE | V+ | 3 |  | 24VDC | DI
IV | ISOLATING VALVE |  | 0 | 0 | DO | 1734-OB4E*M1 | Digital Output 1 (00,06) | 1734-OB4E | 0 | V- | 4 | [5 empty] | 0 | V- |  | DO | 0VDC
CV | CONTROL VALVE |  | 1 | 1 | DO | 1734-OB4E*M2 | Digital Output 2 (01,07) | 1734-OB4E | 1 | V- | 5 | [5 empty] | 1 | V- |  | DO | 0VDC
BU | BURNER |  | 2 | 2 | DO | 1734-OB4E*M3 | Digital Output 3 (02,04) | 1734-OB4E | 2 | V- | 6 | [5 empty] | 2 | V- |  | DO | 0VDC
PU | PUMP |  | 3 | 3 | DO | 1734-OB4E*M4 | Digital Output 4 (03,05) | 1734-OB4E | 3 | V- | 7 |  |  |  |  | TRUE | 3 | V- |  | DO | 0VDC
DM | DAMPER |  | 0 | 0 | AI | 1734-IE8C#MOP-8AI*M1 | Analog Input 1 (0.24,I0,0.SHD) | 1734-IE8C | 0 | [7 empty] | 0 |  |  | AI
PT | PRESSURE TRANSMITTER |  | 1 | 1 | AI | 1734-IE8C#MOP-8AI*M2 | Analog Input 2 (1.24,I1,1.SHD) | 1734-IE8C | 1 | [7 empty] | 1 |  |  | AI
LT | LEVEL TRANSMITTER |  | 2 | 2 | AI | 1734-IE8C#MOP-8AI*M3 | Analog Input 3 (2.24,I2,2.SHD) | 1734-IE8C | 2 | [7 empty] | 2 |  |  | AI
FT | FLOW TRANSMITTER |  | 3 | 3 | AI | 1734-IE8C#MOP-8AI*M4 | Analog Input 4 (3.24,I3,3.SHD) | 1734-IE8C | 3 | [7 empty] | 3 |  |  | AI
TT | TEMPERATURE TRANSMITTER |  | 4 | 4 | AI | 1734-IE8C#MOP-8AI*M5 | Analog Input 5 (4.24,I4,4.SHD) | 1734-IE8C | 4 | [7 empty] | 4 |  |  | AI
QT | GAS/pH/CONDUCTIVITY TRANSMITTER |  | 5 | 5 | AI | 1734-IE8C#MOP-8AI*M6 | Analog Input 6 (5.24,I5,5.SHD) | 1734-IE8C | 5 | [7 empty] | 5 |  |  | AI
TS | TEMPERATURE SWITCH |  | 6 | 6 | AI | 1734-IE8C#MOP-8AI*M7 | Analog Input 7 (6.24,I6,6.0) | 1734-IE8C | 6 | [7 empty] | 6 |  |  | AI
LS | LEVEL SWITCH |  | 7 | 7 | AI | 1734-IE8C#MOP-8AI*M8 | Analog Input 8 (7.24,I7,7.SHD) | 1734-IE8C | 7 | [6 empty] | TRUE | 7 |  |  | AI
PS | PRESSURE SWITCH |  | 0 | 0 | AO | 1734-OE2C*M1 | Analog Output 1 (00,04,02) | 1734-OE2C | 0 | V- | 4 | V+ | 6 | SH | 2 |  | 0 | V- | V+ | AO | 0VDC | 24VDC
ST | SPEED SWITCH/ROTATION GUARD |  | 1 | 1 | AO | 1734-OE2C*M2 | Analog Output 2 (01,05,03) | 1734-OE2C | 1 | V- | 5 | V+ | 7 | SH | 3 | TRUE | 1 | V- | V+ | AO | 0VDC | 24VDC
FS | FLOW SWITCH
HS | EMERGENCY STOP
FM | MOTOR
FL | FILTER
EH | HEATER
DR | DRYER
CP | CONTROL PANEL?
FG | ESP
SI | SAFETY INTERLOCK
BL | BLOWER
Type | CatD | ShortCat
DI | 1734-IB4D | IB4D
DO | 1734-OB4E | OB4E
AI | 1734-IE8C | IE8C
AO | 1734-OE2C | OE2C

## prototype V6 spec
Object Name
objPrefix | objIndex | Column1 | objDesc |  | prefix | index | seperator | attribute | suffix | delimiter | result
P | 0 |  | numbered PLC IO block placeholder |  | P | 1 | _ | NAME |  |  | P1_NAME
D | 0 |  | numbered Device block placeholder |  | D | 1
C | 0 |  | numbered Cable block placeholder |  | C | 1
X | 0 |  | numbered PANEL block place holder |  | X | 1 |  | XIO | TI | _
VS | 0 |  | numbered VSD block placeholder |  | VS | 1
SS | 0 |  | numbered Soft Starter block placeholder |  | SS | 1
IS | 0 |  | numbered ISOLATOR block placeholder |  | IS | 1
Q | 0 |  | numbered PROTECTION block placeholder |  | Q | 1
W |  |  | WIRE
M | 0 |  | numbered MOTOR block placeholder |  | M | 1
Object Attribute |  |  |  | len
Column1 | Column2 | Column3 | Column4 | 4
NAME |  | NAME |  | 4
SLOT |  | SLOT |  | 4 | DRAWING
CHAN |  | CHAN |  | 3 | PROTOTYPE
TAG |  | TAG |  | 5 | X1_PNL
DESC2 |  | DESC2 |  | 5 | X1_PDESC
DESC3 |  | DESC3 |  | 5 | X1_24DC
DESC4 |  | DESC4 |  | 3 | X1_0DC
TAG |  | TAG | 0 | 3 | X1_24ACL
PNL |  | PNL |  | 3 | X1_24ACN
MFG |  | MFG |  | 4 | X1_230ACL1
CATN |  | CATN |  | 4 | X1_230ACN
CATD |  | CATD |  | 3 | X1_XIO
XIO |  | XIO | 0 | 6 | X1_XIO_TI
XIO | TI | XIO_TI |  | 6 | X1_XIO_FI
XIO | FI | XIO_FI |  | 6 | X1_XIO_KI
XIO | KI | XIO_KI |  | 3 | X1_XDB
XDB |  | XDB |  | 6 | X1_XDB_TI
XDB | TI | XDB_TI |  | 6 | X1_XDB_FI
XDB | FI | XDB_FI |  | 6 | X1_XDB_KI
XDB | KI | XDB_KI |  | 6 | X2_PNL
XDB | QI | XDB_QI |  | 5 | X2_PDESC
24VDC |  | 24VDC |  | 4 | X2_24DC
0VDC |  | 0VDC |  | 5 | X2_0DC
24VAC |  | 24VAC |  | 7 | X2_24ACL
24VAC | N | 24VAC_N |  | 7 | X2_24ACN
230V | L1 | 230V_L1 |  | 7 | X2_230ACL1
230V | L2 | 230V_L2 |  | 7 | X2_230ACN
230V | L3 | 230V_L3 |  | 6 | X2_XIO
230V | N | 230V_N |  | #REF! | X2_XIO_TI
TYPE |  | TYPE |  | 4 | X2_XIO_FI
|  |  |  | 0 | X2_XIO_KI
|  |  |  | 0 | X2_XDB
DWG | PREFIX | DWG_PREFIX |  | 10 | X2_XDB_TI
DWG | NUMBER | DWG_NUMBER |  | 10 | X2_XDB_FI
DRAWING |  | DRAWING |  | 7 | X2_XDB_KI
PROTOTYPE |  | PROTOTYPE |  | 9 | P1_NAME
CABLE | TYPE | CABLE_TYPE |  | 10 | P1_RACK
CABLE | DESC | CABLE_DESC |  | 10 | P1_SLOT
|  | 0 |  | 1 | P1_CHAN
|  | 0 |  | 1 | P1_MFG
SET_TO |  | SET_TO |  | 6 | P1_CATN
KW |  | KW |  | 2 | P1_CATD
AMPS |  | AMPS |  | 4 | P1_TAG
VOLTS |  | VOLTS |  | 5 | P1_DESC2
|  |  |  | 0 | P1_DESC3
P1_DESC4
Generic Power Cable Spec |  |  |  |  | P1_T1
VoltageRating | insulation | Cores | Size | Column1 | P1_T2
300/500 | PVC | 1 | 1.5 | Neutral-Screen | P2_NAME
0.6/1kV | XPLE | 36 |  | VSD | P2_RACK
|  |  |  | SWA | P2_SLOT
|  |  |  | FLEX | P2_CHAN
P2_MFG
P2_CATN
P2_CATD
P2_TAG
PVC | P |  |  |  | P2_DESC2
XPLE | X |  |  |  | P2_DESC3
Neutral Screen | NS |  |  |  | P2_DESC4
Steel-Wire-Armour | S |  |  |  | P2_T1
Flex | F |  |  |  | D1_TAG
Marine | M |  |  |  | D1_DESC2
D1_DESC3
Seperator: | - |  |  |  | D1_DESC4
D1_VDESC
VoltageRating | Examples | Description | NOTES |  | D1_TYPE
0 | 120V RMS | Instrumentation/Comms cables. Use for Extra Low Voltage Only |  |  | D1_T1
1 | 300/500 0.6/1kV | Suitible for general 230/400V applications |  |  | D1_T2
2 | >1kV | MV,HV Cables |  |  | D2_TAG
D2_DESC2
Insulation | Examples | Description | NOTES |  | D2_DESC3
P | TPS, R75 | General purpose cable. 75deg max |  |  | D2_DESC4
X | XPLE, R90 | Suitible for general 230/400V applications |  |  | D2_VDESC
X+ |  | Hi temp cable suitible for eg. 120, 150 degrees |  |  | D2_TYPE
D2_T1
D2_T2
Cores | Examples | Description | NOTES |  | C1_MFG
[n]C |  | Number of cores |  |  | C1_CATN
[n]PR |  | Number of Pairs |  |  | C1_CATD
+E |  | plus earth |  |  | C1_TAG
C1_COR1
Properties | Examples | Description | NOTES |  | C1_COR2
V |  | VSD Cable | Can include any number of entries. Can be ommited if not applicible |  | C2_MFG
N |  | Neutral-Screen |  |  | C2_CATN
A |  | Steel-Wire Armour |  |  | C2_CATD
F |  | Flexible |  |  | C2_TAG
M |  | Marine Rated |  |  | C2_COR1
T |  | Twisted-Pair? |  |  | C2_COR2
S |  | Shielded?
Examples
| 0P-3PR-S-1.5 | Instrumentation PVC 3 Pair shielded cable, 1.5mm^2
| 2X-3C+E-VF-35 | Power XPLE 3C+E Flexible VSD cable, 35mm

## MSIO
[10 empty] | MSIO-list | [26 empty] | Date |  | Name |  |  |  | Remarks | [23 empty] | New data with green | Changes with yellow |  | Revision
Revision 3
| Basic information | [8 empty] | Motor | [8 empty] | Supply | [7 empty] | I/O | [9 empty] | Scale |  |  | PLC I/O ( Process) |  |  |  | SIS I/O (Safety) |  |  |  | Bus I/O - Register |  |  |  | Alarm threshold |  |  |  | Instrument |  |  |  | Device |  |  | Supplier | Documentation |  |  | Location |  | Revision
Adresses
Row index | Area | Process | Device | Equipment | TAG | Description | Description 2. language | Short Description (n char) | Column1 | Power (kW) | Current (A) | Speed (rpm) | Voltage (V) | Cos φ | Thermistor | ATEX | Column2 | Column3 | Electrical center | Cubicle | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Signal suffix | W | Signal TAG | Column10 | Column11 | Rack | Slot | Chan. | Addr. | Term. | Min | Max | Unit | DI | DO | AI | AO | SDI | SDO | SAI | SAO | BDI | BDO | BAI | BAO | LL | L | H | HH | Transmitter type | Type of signal | Switch state | Voltage | Manufacturer | Model | Connection | Name | P&ID | Typical | Hook-up | Electrical room | Cabinet | Remarks | Issue
0 |  | BB1 | EM | 001 | BB1EM001 | Feed water pump 1 |  |  |  | 75 |  | 3000 | 415 | [26 empty] | 1 | [7 empty] | 3 | 1 | 4 | 1 | [11 empty] | Sulzer/ABB | 4001 | FRQ_DIR |  |  |  | Tag changed | 3
1 | [26 empty] | _R | Running | BB1PU001 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
2 | [26 empty] | _FAULT | MCC Fault | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
3 | [26 empty] | _SS | Load isolator (Safety switch) | BB1PU001 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIR |  |  |  | Hardwired DI | 4
4 | [26 empty] | _VSD_F | VFD Alarm | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
5 | [26 empty] | _CTRL | Run command | BB1PU001 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
6 | [26 empty] | _CUR | Current | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
7 | [26 empty] | _SR | Speed reference | BB1PU001 | [21 empty] | X | [13 empty] | FRQ_DIR
8 | [26 empty] | _AS | Actual speed | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
9 | [26 empty] | _TORQ | Torque | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
10 | [26 empty] | _RPM | RPM | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
11 |  | BB1 | XT | 003 | BB1XT003 | Feed water pump 1 pump vibration sensor | [30 empty] | 0 | 25 | mm/s |  |  | 1 | [17 empty] | IFM | VTV122 + EVC527 | 2-wire |  | 4001 | MEAS_ANA |  | Field IO |  | Instrument added | 4
12 | [26 empty] | _PV | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
13 |  | BB1 | XT | 001 | BB1XT001 | Feed water pump 1 motor vibration sensor 1 | [30 empty] | 0 | 25 | mm/s |  |  | 1 | [17 empty] | IFM | VTV122 + EVC527 | 2-wire |  | 4001 | MEAS_ANA |  | Field IO |  | Instrument added | 4
14 | [26 empty] | _PV | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
15 |  | BB1 | XT | 002 | BB1XT002 | Feed water pump 1 motor vibration sensor 2 | [30 empty] | 0 | 25 | mm/s |  |  | 1 | [17 empty] | IFM | VTV122 + EVC527 | 2-wire |  | 4001 | MEAS_ANA |  | Field IO |  | Instrument added | 4
16 | [26 empty] | _PV | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
17 |  | BB1 | EM | 002 | BB1EM002 | Feed water pump 2 |  |  |  | 75 |  | 3000 | 415 | [26 empty] | 1 | [7 empty] | 3 | 1 | 4 | 1 | [11 empty] | Sulzer/ABB | 4001 | FRQ_DIR |  |  |  | Tag changed | 3
18 | [26 empty] | _R | Running | BB1PU002 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
19 | [26 empty] | _FAULT | MCC Fault | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
20 | [26 empty] | _SS | Load isolator (Safety switch) | BB1PU002 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIR |  |  |  | Hardwired DI | 4
21 | [26 empty] | _VSD_F | VFD Alarm | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
22 | [26 empty] | _CTRL | Run command | BB1PU002 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
23 | [26 empty] | _CUR | Current | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
24 | [26 empty] | _SR | Speed reference | BB1PU002 | [21 empty] | X | [13 empty] | FRQ_DIR
25 | [26 empty] | _AS | Actual speed | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
26 | [26 empty] | _TORQ | Torque | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
27 | [26 empty] | _RPM | RPM | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
28 |  | BB1 | XT | 006 | BB1XT006 | Feed water pump 2 pump vibration sensor | [30 empty] | 0 | 25 | mm/s |  |  | 1 | [17 empty] | IFM | VTV122 + EVC527 | 2-wire |  | 4001 | MEAS_ANA |  | Field IO |  | Instrument added | 4
29 | [26 empty] | _PV | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
30 |  | BB1 | XT | 004 | BB1XT004 | Feed water pump 2 motor vibration sensor 1 | [30 empty] | 0 | 25 | mm/s |  |  | 1 | [17 empty] | IFM | VTV122 + EVC527 | 2-wire |  | 4001 | MEAS_ANA |  | Field IO |  | Instrument added | 4
31 | [26 empty] | _PV | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
32 |  | BB1 | XT | 005 | BB1XT005 | Feed water pump 2 motor vibration sensor 2 | [30 empty] | 0 | 25 | mm/s |  |  | 1 | [17 empty] | IFM | VTV122 + EVC527 | 2-wire |  | 4001 | MEAS_ANA |  | Field IO |  | Instrument added | 4
33 | [26 empty] | _PV | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
34 |  | BB1 | EM | 703 | BB1EM703 | Chemical filling pump 1 |  | Best guess < 1kW |  |  |  |  | 240 | [26 empty] | 3 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4001 | DOL_DIRH_BUS |  |  |  | Motor typical changed | 4
35 | [26 empty] | _R | Running | BB1SD650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
36 | [26 empty] | _FAULT | MCC Fault | BB1SD650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
37 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS |  |  |  | Added signal | 4
38 | [26 empty] | _L_RUN | Local run command | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
39 | [26 empty] | _L/R | Local mode switch | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
40 | [26 empty] | _CTRL | Run command | BB1SD650 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
41 | [26 empty] | _CUR | Current | BB1SD650 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
42 |  | BB1 | EM | 704 | BB1EM704 | Chemical filling pump 2 |  | Best guess < 1kW |  |  |  |  | 240 | [26 empty] | 3 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4001 | DOL_DIRH_BUS |  |  |  | Motor typical changed | 4
43 | [26 empty] | _R | Running | BB1SD650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
44 | [26 empty] | _FAULT | MCC Fault | BB1SD650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
45 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS |  |  |  | Added signal | 4
46 | [26 empty] | _L_RUN | Local run command | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
47 | [26 empty] | _L/R | Local mode switch | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
48 | [26 empty] | _CTRL | Run command | BB1SD650 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
49 | [26 empty] | _CUR | Current | BB1SD650 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
50 |  | BB1 | PU | 800 | BB1PU800 | Chemical dosing pump 1 |  |  |  | 0,37 |  |  | 230 | [29 empty] | 1 | [20 empty] | 4001 | CHEMICAL_PUMP |  | Field IO |  | Motor details | 1
51 | [26 empty] | _CTLR | Control signal | BB1PU800 | [13 empty] | X | [21 empty] | CHEMICAL_PUMP |  | Field IO
52 |  | BB1 | LS | 700 | BB1LS700 | Chemical tank 1 level switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | LS001 | Field IO |  | Instrument added | 1
53 | [26 empty] | _DI | Binary State | BB1LT001 | [10 empty] | X | [24 empty] | MEAS_BIN |  | Field IO
54 |  | BB1 | PU | 801 | BB1PU801 | Chemical dosing pump 2 |  |  |  | 0,37 |  |  | 230 | [29 empty] | 1 | [20 empty] | 4001 | CHEMICAL_PUMP |  | Field IO |  | Motor details | 1
55 | [26 empty] | _CTLR | Control signal | BB1PU801 | [13 empty] | X | [21 empty] | CHEMICAL_PUMP |  | Field IO
56 |  | BB1 | LS | 701 | BB1LS701 | Chemical tank 2 level switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | LS001 | Field IO |  | Instrument added | 1
57 | [26 empty] | _DI | Binary State | BB1LT001 | [10 empty] | X | [24 empty] | MEAS_BIN |  | Field IO
58 |  | BB1 | PT | 200 | BB1PT200 | Feed water tank pressure | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [13 empty] | Pressure |  |  |  | E+H | PMP51-AA22IA1PGBGCJA1+JAZ1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
59 | [26 empty] | _PV | Measurement | BB1PT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
60 |  | BB1 | LT | 001 | BB1LT001 | Feed water tank level 1 | [30 empty] | 0 | 1800 | mm |  |  | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+JAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | LT001 | Field IO
61 | [26 empty] | _PV | Measurement | BB1LT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
62 |  | BB1 | LT | 002 | BB1LT002 | Feed water tank level 2 | [30 empty] | 0 | 1800 | mm |  |  | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+JAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | LT001 | Field IO
63 | [26 empty] | _PV | Measurement | BB1LT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
64 |  | BB1 | PT | 005 | BB1PT005 | Feed water pressure after valve | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+JAZ1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
65 | [26 empty] | _PV | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
66 |  | BB1 | FT | 001 | BB1FT001 | Feed water flow and control | [35 empty] | 1 | [17 empty] | E+H | PMD75-ACA7FG1DAEA+N3PJZ1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | FT002 | Field IO
67 | [26 empty] | _PV | Measurement | BB1FT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
68 |  | BB1 | CV | 200 | BB1CV200 | Steam from drum control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
69 | [26 empty] | _SP | Setpoint position | BB1CV200 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
70 | [26 empty] | _POS | Position feedback | BB1CV200 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
71 |  | BB1 | TT | 001 | BB1TT001 | Feed water temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4001 | MEAS_ANA | TT001 | Field IO
72 | [26 empty] | _PV | Measurement | BB1TT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
73 |  | BB1 | IV | 002 | BB1IV002 | Feedwater pump 1 on-off valve |  |  |  | 0.25 | 1.9 |  | 415 | [26 empty] | 4 | 2 | 1 | [17 empty] | AUMA | SA10.2-22 + RWG |  | Konwell/Auma | 4001 | MTR_VLV |  |  |  | Changed to motor valve | 1
74 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
75 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
76 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
77 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
78 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
79 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
80 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
81 |  | BB1 | TT | 002 | BB1TT002 | Feed water pump 2 bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4001 | MEAS_ANA | TT005 | Field IO
82 | [26 empty] | _PV | Measurement | BB1TT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
83 |  | BB1 | GS | 004 | BB1GS004 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
84 | [26 empty] | _DI | Binary state | BB1GS004 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
85 |  | BB1 | PT | 004 | BB1PT004 | Feed water pressure before valve | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+JAZ1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
86 | [26 empty] | _PV | Measurement | BB1PT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
87 |  | BB1 | GS | 003 | BB1GS003 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
88 | [26 empty] | _DI | Binary state | BB1GS003 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
89 |  | BB1 | IV | 003 | BB1IV003 | Feed water pump 2 on-off valve |  |  |  | 0.25 | 1.9 |  | 415 | [26 empty] | 4 | 2 | 1 | [17 empty] | AUMA | SA10.2-22 + RWG |  | Konwell/Auma | 4001 | MTR_VLV |  |  |  | Changed to motor valve | 1
90 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
91 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
92 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
93 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
94 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
95 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
96 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
97 |  | BB1 | PT | 002 | BB1PT002 | Feed water pump 2 pressure side pressure | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+JAZ1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
98 | [26 empty] | _PV | Measurement | BB1PT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
99 |  | BB1 | CV | 001 | BB1CV001 | Make-up water control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
100 | [26 empty] | _SP | Setpoint position | BB1CV001 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
101 | [26 empty] | _POS | Position feedback | BB1CV001 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
102 |  | BB1 | PT | 006 | BB1PT006 | FW suction line strainer pressure diff. | [30 empty] | 0 | 5 | bar(g) |  |  | 1 | [17 empty] | E+H | PMD55-AA22AB67LGJHAJA1A+JAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | PT005 | Field IO
103 | [26 empty] | _PV | Measurement | BB1PT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
104 |  | BB1 | GS | 001 | BB1GS001 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
105 | [26 empty] | _DI | Binary state | BB1GS001 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
106 |  | BB1 | PT | 007 | BB1PT007 | FW suction line strainer pressure diff. | [30 empty] | 0 | 5 | bar(g) |  |  | 1 | [17 empty] | E+H | PMD55-AA22AB67LGJHAJA1A+JAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | PT005 | Field IO
107 | [26 empty] | _PV | Measurement | BB1PT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
108 |  | BB1 | TT | 005 | BB1TT005 | FW pump 2 motor winding temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4001 | MEAS_ANA | TT005 | Field IO
109 | [26 empty] | _PV | Measurement | BB1TT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
110 |  | BB1 | PT | 001 | BB1PT001 | Feed water pump 1 pressure side pressure | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+JAZ1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
111 | [26 empty] | _PV | Measurement | BB1PT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
112 |  | BB1 | GS | 002 | BB1GS002 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
113 | [26 empty] | _DI | Binary state | BB1GS002 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
114 |  | BB1 | CV | 002 | BB1CV002 | Feed water control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
115 | [26 empty] | _SP | Setpoint position | BB1CV002 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
116 | [26 empty] | _POS | Position feedback | BB1CV002 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
117 |  | BB1 | TT | 004 | BB1TT004 | FW pump 1 motor winding temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4001 | MEAS_ANA | TT005 | Field IO
118 | [26 empty] | _PV | Measurement | BB1TT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
119 |  | BB1 | TT | 003 | BB1TT003 | FW pump 1 motor bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA |  | Field IO
120 | [26 empty] | _PV | Measurement | BB1TT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
121 |  | BB1 | SV | 410 | BB1SV410 | Feed water tank overflow valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4001 | BIN_VLV | AA005 | Field IO |  | tag changed | 1
122 | [7 empty] | own 24 VDC fuse | [18 empty] | _CTLR | Control command | BB1IV001 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | 24 VDC feed added | 1
123 |  | BB1 | GS | 005 | BB1GS005 | FW tank overflow On-Off valve position | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
124 | [26 empty] | _DI | Binary state | BB1GS005 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
125 |  | BB1 | GS | 006 | BB1GS006 | FW tank overflow On-Off valve position | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
126 | [26 empty] | _DI | Binary state | BB1GS006 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
127 |  | BB1 | GS | 007 | BB1GS007 | Feedwater pump 1 on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
128 | [26 empty] | _DI | Binary state | BB1GS007 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
129 |  | BB1 | GS | 008 | BB1GS008 | Feedwater pump 1 on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
130 | [26 empty] | _DI | Binary state | BB1GS008 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
131 |  | BB1 | GS | 009 | BB1GS009 | Feed water pump 2 on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
132 | [26 empty] | _DI | Binary state | BB1GS009 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
133 |  | BB1 | GS | 010 | BB1GS010 | Feed water pump 2 on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
134 | [26 empty] | _DI | Binary state | BB1GS010 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
135 |  | BB1 | LT | 101 | BB1LT101 | Steam drum level 1 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+JALAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
136 | [26 empty] | _PV_SRS | Measurement SRS | BB1LS100 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
137 |  | BB1 | LS | 103 | BB1LS103 | Steam drum level switch 1 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | LS003 | SRS |  | Instrument added | 2
138 | [26 empty] | _DI_SRS | Binary state SRS | BB1LS100 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Instrument added | 2
139 |  | BB1 | LS | 104 | BB1LS104 | Steam drum level switch 2 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | LS003 | SRS |  | Instrument added | 2
140 | [26 empty] | _DI_SRS | Binary state SRS | BB1LS100 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Instrument added | 2
141 |  | BB1 | IV | 004 | BB1IV004 | Boiler bottom blow down on-off valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4002 | BIN_VLV | AA005 | Field IO
142 | [7 empty] | own 24 VDC fuse | [18 empty] | _CTLR | Control command | BB1IV004 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | 24 VDC feed added | 1
143 |  | BB1 | GS | 011 | BB1GS011 | Boiler bottom blow down on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 1
144 | [26 empty] | _DI | Binary state | BB1GS007 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
145 |  | BB1 | GS | 012 | BB1GS012 | Boiler bottom blow down on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 1
146 | [26 empty] | _DI | Binary state | BB1GS008 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
147 |  | BB1 | PT | 203 | BB1PT203 | Steam drum pressure 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+JALAZ1 | G1/2 |  | 4002 | MEAS_ANA_SRS | PT001.1 | SRS
148 | [26 empty] | _PV_SRS | Measurement SRS | BB1PT203 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
149 |  | BB1 | TT | 008 | BB1TT008 | Temperature after economizer | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4002 | MEAS_ANA | TT001 | Field IO
150 | [26 empty] | _PV | Measurement | BB1TT008 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
151 |  | BB1 | LT | 102 | BB1LT102 | Steam drum level 2 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+JALAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
152 | [26 empty] | _PV_SRS | Measurement SRS | BB1LS101 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
153 |  | BB1 | PT | 201 | BB1PT201 | Steam drum pressure 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+JALAZ1 | G1/2 |  | 4002 | MEAS_ANA_SRS | PT001.1 | SRS
154 | [26 empty] | _PV_SRS | Measurement SRS | BB1PT201 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
155 |  | BB1 | LT | 103 | BB1LT103 | Steam drum level 3 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+JALAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
156 | [26 empty] | _PV_SRS | Measurement SRS | BB1LS102 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
157 |  | BB1 | FT | 200 | BB1FT200 | Heating steam to feed water tank flow measurement | [30 empty] | 0 | 5 | t/h |  |  | 1 | [17 empty] | E+H | PMD75-ACA7FG1DAEA+N3PJZ1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA | FT001 | Field IO
158 | [26 empty] | _PV | Measurement | BB1FT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
159 |  | BB1 | HS | 101 | BB1HS101 | Boiler emergency shutdown switch 1 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
160 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS101 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
161 |  | BB1 | HS | 103 | BB1HS103 | Boiler emergency shutdown switch 3 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
162 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
163 |  | BB1 | TT | 009 | BB1TT009 | Temperature before economizer | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4002 | MEAS_ANA | TT001 | Field IO
164 | [26 empty] | _PV | Measurement | BB1TT009 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
165 |  | BB1 | HS | 104 | BB1HS104 | Boiler emergency shutdown switch 4 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
166 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS104 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
167 |  | BB1 | HS | 102 | BB1HS102 | Boiler emergency shutdown switch 2 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
168 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS102 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
169 |  | BB1 | HS | 105 | BB1HS105 | Boiler emergency shutdown switch 5 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
170 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS105 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
171 |  | BB1 | HS | 106 | BB1HS106 | Boiler emergency shutdown switch 6 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
172 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS106 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
173 |  | BB1 | HS | 107 | BB1HS107 | Boiler emergency shutdown switch 7 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
174 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS107 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
175 |  | BB1 | HS | 108 | BB1HS108 | Boiler emergency shutdown switch 8 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
176 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS108 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
177 |  | BB1 | HS | 109 | BB1HS109 | Boiler emergency shutdown switch 9 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
178 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS109 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
179 |  | BB1 | HS | 110 | BB1HS110 | Boiler emergency shutdown switch 10 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
180 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS110 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
181 |  | BB1 | HS | 111 | BB1HS111 | Boiler emergency shutdown switch 11 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
182 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS111 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
183 |  | BB1 | HS | 112 | BB1HS112 | Boiler emergency shutdown switch 12 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
184 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS112 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
185 |  | BB1 | TT | 200 | BB1TT200 | Main steam temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4003 | MEAS_ANA | TT001 | Field IO
186 | [26 empty] | _PV | Measurement | BB1TT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
187 |  | BB1 | FT | 202 | BB1FT202 | Main steam flow | [30 empty] | 0 | 30 | t/h |  |  | 1 | [17 empty] | E+H | 7F2C1F-AAACCAAAAAAACSKA1+Z1 | Flange |  | 4003 | MEAS_ANA | Vortex | Field IO
188 | [26 empty] | _PV | Measurement | BB1FT202 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
189 |  | BB1 | IV | 202 | BB1IV202 | Main steam valve by-pass valve |  |  |  | 0.12 | 1.1 |  | 415 | [5 empty] | UPS | [20 empty] | 4 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
190 | [26 empty] | _CTLR_O | Open direction command | BB1IV202 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
191 | [26 empty] | _CTRL_C | Close direction command | BB1IV202 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
192 | [26 empty] | _TL_O | Torque limit open direction | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
193 | [26 empty] | _TL_C | Torque limit close direction | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
194 | [26 empty] | _FAULT | MCC fault | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
195 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
196 | [26 empty] | _POS | Position | BB1IV202 | [12 empty] | X | [22 empty] | MTR_VLV
197 |  | BB1 | CV | 201 | BB1CV201 | Start-up valve |  |  |  | 0.06 | 0.6 |  | 415 | [5 empty] | UPS | [20 empty] | 4 | 2 | 1 | [17 empty] | AUMA | SAR10.2 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
198 | [26 empty] | _CTLR_O | Open direction command | BB1CV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
199 | [26 empty] | _CTRL_C | Close direction command | BB1CV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
200 | [26 empty] | _TL_O | Torque limit open direction | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
201 | [26 empty] | _TL_C | Torque limit close direction | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
202 | [26 empty] | _FAULT | MCC fault | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
203 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
204 | [26 empty] | _POS | Position | BB1CV201 | [12 empty] | X | [22 empty] | MTR_VLV
205 |  | BB1 | IV | 201 | BB1IV201 | Main steam valve |  |  |  | 0.45 | 3.7 |  | 415 | [5 empty] | UPS | [20 empty] | 4 | 2 | 1 | [17 empty] | AUMA | SA14.2-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
206 | [26 empty] | _CTLR_O | Open direction command | BB1IV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
207 | [26 empty] | _CTRL_C | Close direction command | BB1IV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
208 | [26 empty] | _TL_O | Torque limit open direction | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
209 | [26 empty] | _TL_C | Torque limit close direction | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
210 | [26 empty] | _FAULT | MCC fault | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
211 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
212 | [26 empty] | _POS | Position | BB1IV201 | [12 empty] | X | [22 empty] | MTR_VLV
213 |  | BB1 | FT | 201 | BB1FT201 | Steam flow to sootblowing and air preheater | [30 empty] | 0 | 8 | t/h |  |  | 1 | [17 empty] | E+H | PMD75-ACA7FG1DAEA+N3PJZ1 | NPT1/4-18 IEC61518 |  | 4003 | MEAS_ANA | FT001 | Field IO
214 | [26 empty] | _PV | Measurement | BB1FT201 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
215 |  | BB1 | IV | 200 | BB1IV200 | Start-up check valve |  |  |  | 0.12 | 1.1 |  | 415 | [5 empty] | UPS | [20 empty] | 4 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
216 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
217 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
218 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
219 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
220 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
221 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
222 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
223 |  | BB1 | GS | 221 | BB1GS221 | Main steam valve by-pass open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
224 | [26 empty] | _DI | Binary state | BB1GS221 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
225 |  | BB1 | GS | 222 | BB1GS222 | Main steam valve by-pass close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
226 | [26 empty] | _DI | Binary state | BB1GS222 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
227 |  | BB1 | GS | 223 | BB1GS223 | Main steam line valve open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
228 | [26 empty] | _DI | Binary state | BB1GS223 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
229 |  | BB1 | GS | 224 | BB1GS224 | Main steam line valve close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
230 | [26 empty] | _DI | Binary state | BB1GS224 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
231 |  | BB1 | GS | 225 | BB1GS225 | Start-up line ON-OFF valve open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
232 | [26 empty] | _DI | Binary state | BB1GS225 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
233 |  | BB1 | GS | 226 | BB1GS226 | Start-up line ON-OFF valve close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
234 | [26 empty] | _DI | Binary state | BB1GS226 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
235 |  | BB1 | GS | 200 | BB1GS200 | Sootblower 1 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
236 | [26 empty] | _DI | Binary state | BB1GS200 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
237 |  | BB1 | GS | 201 | BB1GS201 | Sootblower 1 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
238 | [26 empty] | _DI | Binary state | BB1GS201 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
239 |  | BB1 | GS | 203 | BB1GS203 | Sootblower 2 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
240 | [26 empty] | _DI | Binary state | BB1GS203 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
241 |  | BB1 | GS | 204 | BB1GS204 | Sootblower 2 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
242 | [26 empty] | _DI | Binary state | BB1GS204 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
243 |  | BB1 | GS | 205 | BB1GS205 | Sootblower 3 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
244 | [26 empty] | _DI | Binary state | BB1GS205 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
245 |  | BB1 | GS | 206 | BB1GS206 | Sootblower 3 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
246 | [26 empty] | _DI | Binary state | BB1GS206 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
247 |  | BB1 | GS | 207 | BB1GS207 | Sootblower 5 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
248 | [26 empty] | _DI | Binary state | BB1GS207 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
249 |  | BB1 | GS | 208 | BB1GS208 | Sootblower 5 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
250 | [26 empty] | _DI | Binary state | BB1GS208 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
251 |  | BB1 | GS | 209 | BB1GS209 | Sootblower 6 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
252 | [26 empty] | _DI | Binary state | BB1GS209 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
253 |  | BB1 | GS | 210 | BB1GS210 | Sootblower 6 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
254 | [26 empty] | _DI | Binary state | BB1GS210 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
255 |  | BB1 | GS | 211 | BB1GS211 | Sootblower 7 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
256 | [26 empty] | _DI | Binary state | BB1GS211 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
257 |  | BB1 | GS | 212 | BB1GS212 | Sootblower 7 IN limit switch | [6 empty] | 24 | [26 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
258 | [26 empty] | _DI | Binary state | BB1GS212 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
259 |  | BB1 | GS | 213 | BB1GS213 | Sootblower 8 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
260 | [26 empty] | _DI | Binary state | BB1GS213 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
261 |  | BB1 | GS | 214 | BB1GS214 | Sootblower 8 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
262 | [26 empty] | _DI | Binary state | BB1GS214 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
263 |  | BB1 | IV | 203 | BB1IV203 | Sootblowing line on-off valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 4 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4004 | MTR_VLV |  |  |  | Changed to motor valve | 1
264 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
265 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
266 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
267 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
268 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
269 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
270 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
271 |  | BB1 | TT | 201 | BB1TT201 | Sootblowing line temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4004 | MEAS_ANA | TT001 | Field IO
272 | [26 empty] | _PV | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
273 |  | BB1 | TT | 450 | BB1TT450 | Electrical room temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [17 empty] | E+H | TST434-J1A3BK | Wall mount |  |  | MEAS_ANA | TT007 |  |  | Tag added | 4
274 | [26 empty] | _PV | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA
275 |  | BB1 | TT | 451 | BB1TT451 | PLC-cabinet temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [17 empty] | E+H | TST434-J1A3BK | Wall mount |  |  | MEAS_ANA | TT007 |  |  | Tag added | 4
276 | [26 empty] | _PV | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA
277 |  | BB1 | GS | 227 | BB1GS227 | Sootblowing line on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | MCC
278 | [26 empty] | _DI | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
279 |  | BB1 | GS | 228 | BB1GS228 | Sootblowing line on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | MCC
280 | [26 empty] | _DI | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
281 |  | BB1 | BL | 200 | BB1BL200 | Sootblower 1 |  |  |  | 0,37 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
282 | [26 empty] | _R_IN | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
283 | [26 empty] | _R_OUT | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
284 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
285 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
286 | [26 empty] | _CTRL_I | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
287 | [26 empty] | _CTRL_O | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
288 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
289 |  | BB1 | BL | 201 | BB1BL201 | Sootblower 2 |  |  |  | 0,37 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
290 | [26 empty] | _R_IN | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
291 | [26 empty] | _R_OUT | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
292 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
293 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
294 | [26 empty] | _CTRL_I | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
295 | [26 empty] | _CTRL_O | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
296 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
297 |  | BB1 | BL | 202 | BB1BL202 | Sootblower 3 |  |  |  | 0,37 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
298 | [26 empty] | _R_IN | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
299 | [26 empty] | _R_OUT | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
300 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
301 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
302 | [26 empty] | _CTRL_I | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
303 | [26 empty] | _CTRL_O | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
304 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
305 |  | BB1 | BL | 203 | BB1BL203 | Sootblower 4 |  |  |  | 0,37 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
306 | [26 empty] | _R_IN | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
307 | [26 empty] | _R_OUT | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
308 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
309 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
310 | [26 empty] | _CTRL_I | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
311 | [26 empty] | _CTRL_O | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
312 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
313 |  | BB1 | BL | 204 | BB1BL204 | Sootblower 5 |  |  |  | 0,37 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
314 | [26 empty] | _R_IN | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
315 | [26 empty] | _R_OUT | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
316 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
317 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
318 | [26 empty] | _CTRL_I | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
319 | [26 empty] | _CTRL_O | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
320 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
321 |  | BB1 | BL | 205 | BB1BL205 | Sootblower 6 |  |  |  | 0,37 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
322 | [26 empty] | _R_IN | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
323 | [26 empty] | _R_OUT | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
324 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
325 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
326 | [26 empty] | _CTRL_I | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
327 | [26 empty] | _CTRL_O | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
328 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
329 |  | BB1 | BL | 206 | BB1BL206 | Sootblower 7 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
330 | [26 empty] | _R_IN | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
331 | [26 empty] | _R_OUT | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
332 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
333 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
334 | [26 empty] | _CTRL_I | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
335 | [26 empty] | _CTRL_O | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
336 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
337 |  | BB1 | TT | 006 | BB1TT006 | Blow down tank temperature and control | [30 empty] | 0 | 100 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4005 | MEAS_ANA | TT001 | Field IO
338 | [26 empty] | _PV | Measurement | BB1TT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
339 |  | BB1 | CV | 003 | BB1CV003 | Continuous blow down valve |  |  |  |  | 2 |  | 240 | [26 empty] | 4 | 2 | 1 | [17 empty] | Gestra | BAE 46-1-ANSI + EF10-1 + 1000 ohm |  | Konwell/Gestra | 4005 | MTR_VLV | AA001 |  |  | Model added | 1
340 | [26 empty] | _CTLR_O | Open direction command | BB1CV003 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
341 | [26 empty] | _CTRL_C | Close direction command | BB1CV003 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
342 | [26 empty] | _TL_O | Torque limit open direction | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
343 | [26 empty] | _TL_C | Torque limit close direction | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
344 | [26 empty] | _FAULT | MCC fault | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
345 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
346 | [7 empty] | needs R/I converter 0...10 Kohm=4..20 mA | [18 empty] | _POS | Position | BB1CV003 | [12 empty] | X | [22 empty] | MTR_VLV
347 |  | BB1 | SV | 001 | BB1SV001 | Blow down tank cooling on/off valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4005 | BIN_VLV | AA005 | Field IO
348 | [7 empty] | own 24 VDC fuse | [18 empty] | _CTLR | Control command | BB1SV001 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
349 |  | BB1 | PT | 205 | BB1PT205 | Steam outlet pressure from accumulator | [30 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+JALAZ1 | G1/2 |  | 4006 | MEAS_ANA_SRS | PT001.1 | SRS |  | Moved to SRS | 2
350 | [26 empty] | _PV_SRS | Measurement SRS | BB1PT205 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS |  | Moved to SRS | 2
351 |  | BB1 | TT | 202 | BB1TT202 | Steam outlet temperature from accumulator | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
352 | [26 empty] | _PV | Measurement | BB1TT202 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
353 |  | BB1 | PT | 207 | BB1PT207 | Accumulator pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+JALAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
354 | [26 empty] | _PV | Measurement | BB1PT207 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
355 |  | BB1 | CV | 203 | BB1CV203 | Steam accumulator pressure control valve |  |  |  | 0.25 | 1.8 |  | 415 | [26 empty] | 4 | 2 | 1 | [17 empty] | AUMA | SAR14.2 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 1
356 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
357 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
358 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
359 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
360 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
361 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
362 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
363 |  | BB1 | GS | 231 | BB1GS231 | Steam accumulator pressure control valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | Field IO |  | Signal added | 1
364 | [26 empty] | _DI | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
365 |  | BB1 | GS | 230 | BB1GS230 | Steam accumulator pressure control valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | Field IO |  | Signal added | 1
366 | [26 empty] | _DI | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
367 |  | BB1 | TT | 007 | BB1TT007 | Accumulator temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
368 | [26 empty] | _PV | Measurement | BB1TT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
369 |  | BB1 | TT | 203 | BB1TT203 | 18bar(g) steam temperature |  | Transmitter wired to energy calculator | [28 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
370 | [26 empty] | _PV | Measurement | BB1TT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
371 |  | BB1 | CV | 202 | BB1CV202 | Steam pressure reduction valve |  |  |  | 0.25 | 1.8 |  | 415 | [26 empty] | 4 | 2 | 1 | [17 empty] | Auma | SAR14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
372 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
373 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
374 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
375 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
376 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
377 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
378 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
379 |  | BB1 | GS | 233 | BB1GS233 | Steam pressure reduction valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
380 | [26 empty] | _DI | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
381 |  | BB1 | GS | 232 | BB1GS232 | Steam pressure reduction valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
382 | [26 empty] | _DI | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
383 |  | BB1 | PT | 204 | BB1PT204 | Main steam pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+JALAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
384 | [26 empty] | _PV | Measurement | BB1PT204 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
385 |  | BB1 | LT | 004 | BB1LT004 | Steam accumulator level 2 | [30 empty] | 0 | 1800 | mm |  |  | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4006 | MEAS_ANA | LT001 | Field IO
386 | [26 empty] | _PV | Measurement | BB1LT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
387 |  | BB1 | IV | 204 | BB1IV204 | Main steam line accumulator bypass on-off valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 4 | 2 | 1 | [17 empty] | Auma | SA14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
388 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
389 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
390 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
391 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
392 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
393 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
394 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
395 |  | BB1 | GS | 217 | BB1GS217 | Main steam line accumulator bypass on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
396 | [26 empty] | _DI | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
397 |  | BB1 | GS | 218 | BB1GS218 | Main steam line accumulator bypass on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
398 | [26 empty] | _DI | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
399 |  | BB1 | PT | 208 | BB1PT208 | Accumulator pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+JALAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
400 | [26 empty] | _PV | Measurement | BB1PT208 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
401 |  | BB1 | FT | 203 | BB1FT203 | Steam to existing header flow measurement | [30 empty] | 0 | 25 | t/h |  |  | 1 | [17 empty] | E+H | 7F2C2H-AAACCAAAAAAACSKA1+Z1 | Flange |  | 4006 | MEAS_ANA | Vortex | Field IO
402 | [26 empty] | _PV | Measurement | BB1FT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
403 |  | BB1 | QT |  |  | Steam to existing header energy calculator | [6 empty] | 240 | [28 empty] | 1 | [17 empty] | E+H | RMS621-21BBA1221 |  |  | 4006 | MEAS_ANA |  | Field IO |  | Instrument added | 3
404 | [26 empty] | _PV | Measurement | BB1FT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
405 |  | BB1 | LT | 003 | BB1LT003 | Steam accumulator level 1 | [30 empty] | 0 | 1800 | mm |  |  | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+JAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4006 | MEAS_ANA | LT001 | Field IO
406 | [26 empty] | _PV | Measurement | BB1LT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
407 |  | BB1 | IV | 205 | BB1IV205 | Steam accumualtor ON-OFF isolating valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 4 | 2 | 1 | [17 empty] | Auma | SA14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
408 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
409 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
410 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
411 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
412 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
413 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
414 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
415 |  | BB1 | GS | 219 | BB1GS219 | Steam accumualtor ON-OFF isolating valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
416 | [26 empty] | _DI | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
417 |  | BB1 | GS | 220 | BB1GS220 | Steam accumualtor ON-OFF isolating valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
418 | [26 empty] | _DI | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
419 |  | BB1 | GS | 217 | BB1GS217 | Steam accumulator by-pass valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
420 | [26 empty] | _DI | Binary state | BB1GS217 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
421 |  | BB1 | GS | 218 | BB1GS218 | Steam accumulator by-pass valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
422 | [26 empty] | _DI | Binary state | BB1GS218 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
423 |  | BB1 | GS | 220 | BB1GS220 | Steam accumulator ON-OFF valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
424 | [26 empty] | _DI | Binary state | BB1GS220 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
425 |  | BB1 | GS | 219 | BB1GS219 | Steam accumulator ON-OFF valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
426 | [26 empty] | _DI | Binary state | BB1GS219 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
427 |  | BB1 | QT | 002 | BB1QT002 | pH measurement from feed water tank | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
428 | [26 empty] | _PV | Measurement | BB1QT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
429 |  | BB1 | QT | 006 | BB1QT006 | Conductivity measurement from main steam | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
430 | [26 empty] | _PV | Measurement | BB1QT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
431 |  | BB1 | QT | 005 | BB1QT005 | Conductivity measurement from saturated steam | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
432 | [26 empty] | _PV | Measurement | BB1QT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
433 |  | BB1 | QT | 003 | BB1QT003 | Conductivity measurement from condensate | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
434 | [26 empty] | _PV | Measurement | BB1QT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
435 |  | BB1 | QT | 007 | BB1QT007 | Conductivity measurement from feed water line | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
436 | [26 empty] | _PV | Measurement | BB1QT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
437 |  | BB1 | QT | 001 | BB1QT001 | Conductivity measurement from feed water tank | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
438 | [26 empty] | _PV | Measurement | BB1QT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
439 |  | BB1 | QT | 004 | BB1QT004 | Conductivity measurement from boiler water | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
440 | [26 empty] | _PV | Measurement | BB1QT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
441 |  | BB1 | PT | 400 | BB1PT400 | Primary air pressure |  | SIL2 classified transmitter | [28 empty] | 0 | 16 | kPa | [6 empty] | 1 | [13 empty] | E+H | PMC51-AA22IA1EGJGCJA+JALAZ1 | G1/2 |  | 4008 | MEAS_ANA_SRS | PT002 | SRS
442 | [26 empty] | _PV_SRS | Measurement SRS | BB1PT400 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
443 |  | BB1 | TT | 418 | BB1TT418 | Bed temperature 4 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK | G1/2" |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
444 | [26 empty] | _PV_SRS | Measurement SRS | BB1TT418 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
445 |  | BB1 | PT | 404 | BB1PT404 | Boiler upper part pressure 1 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+JALAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
446 | [26 empty] | _PV_SRS | Measurement SRS | BB1PT404 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
447 |  | BB1 | FT | 400 | BB1FT400 | Primary air flow |  | 0...11,21 mbar = 0...4,0 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB27CGLHAJA1A+JALAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | FT003 | SRS
448 | [26 empty] | _PV_SRS | Measurement SRS | BB1FT400 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
449 |  | BB1 | PT | 401 | BB1PT401 | Secondary air pressure |  | SIL2 classified transmitter | [28 empty] | 0 | 6 | kPa | [6 empty] | 1 | [13 empty] | E+H | PMC51-AA22IA1CGJGCJA+JALAZ1 | G1/2 |  | 4008 | MEAS_ANA_SRS | PT002 | SRS
450 | [26 empty] | _PV_SRS | Measurement SRS | BB1PT401 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
451 |  | BB1 | PT | 410 | BB1PT410 | Secondary air pressure inner front wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+JAZ1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
452 | [26 empty] | _PV | Measurement | BB1PT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
453 |  | BB1 | TT | 551 | BB1TT551 | Flue gas temperature 2 | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSXKC10B | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
454 | [26 empty] | _PV | Measurement | BB1TT551 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
455 |  | BB1 | TT | 400 | BB1TT400 | Primary air temperature before preheater | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSHK310B | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
456 | [26 empty] | _PV | Measurement | BB1TT400 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
457 |  | BB1 | PT | 403 | BB1PT403 | Secondary air pressure inner back wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+JAZ1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO
458 | [26 empty] | _PV | Measurement | BB1PT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
459 |  | BB1 | FT | 401 | BB1FT401 | Secondary air flow |  | 0...11,55 mbar = 0...4,6 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB27CGLHAJA1A+JALAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | FT003 | SRS
460 | [26 empty] | _PV_SRS | Measurement SRS | BB1FT401 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
461 |  | BB1 | TT | 417 | BB1TT417 | Bed temperature 3 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK | G1/2" |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
462 | [26 empty] | _PV_SRS | Measurement SRS | BB1TT417 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
463 |  | BB1 | PT | 550 | BB1PT550 | Flue gas pressure at the outlet of the boiler | [30 empty] | -35 | 35 | mbar |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+JAZ1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO
464 | [26 empty] | _PV | Measurement | BB1PT550 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
465 |  | BB1 | TT | 012 | BB1TT012 | Condensate temperature from primary air preheater | [30 empty] | 0 | 250 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4008 | MEAS_ANA | TT001 | Field IO |  | Max scale changed | 3
466 | [26 empty] | _PV | Measurement | BB1TT012 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
467 |  | BB1 | TT | 413 | BB1TT413 | Bed temperature 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK | G1/2" |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
468 | [26 empty] | _PV_SRS | Measurement SRS | BB1TT413 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
469 |  | BB1 | TT | 550 | BB1TT550 | Flue gas temperature 1 | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSXKC10B | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
470 | [26 empty] | _PV | Measurement | BB1TT550 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
471 |  | BB1 | TT | 412 | BB1TT412 | Boiler temperature after empty draft 2 | [30 empty] | 0 | 500 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABE3BHSXKC10B | G1/2 M / 1000 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
472 | [26 empty] | _PV | Measurement | BB1TT412 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
473 |  | BB1 | TT | 414 | BB1TT414 | Bed temperature 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK | G1/2" |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
474 | [26 empty] | _PV_SRS | Measurement SRS | BB1TT414 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
475 |  | BB1 | PT | 405 | BB1PT405 | Boiler upper part pressure 2 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+JALAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
476 | [26 empty] | _PV_SRS | Measurement SRS | BB1PT405 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
477 |  | BB1 | TT | 411 | BB1TT411 | Boiler temperature after empty draft 1 | [30 empty] | 0 | 500 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABE3BHSXKC10B | G1/2 M / 1000 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
478 | [26 empty] | _PV | Measurement | BB1TT411 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
479 |  | BB1 | QT | 550 | BB1QT550 | Fluegas oxygen measurement 1 |  | SIL2 classified transmitter | [10 empty] | UPS | [17 empty] | 0 | 25 | % | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | QT001/dn65 flange with counterflange. 1 meter probe | SRS |  | UPS feed added | 4
480 | [26 empty] | _PV_SRS | Measurement SRS | BB1QT550 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
481 |  | BB1 | FT | 550 | BB1FT550 | Recirculation gas flow |  | 0...10,19 mbar = 0...1,2 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB27CGLHAJA1A+JALAPDP3Z1 |  |  | 4008 | MEAS_ANA_SRS | FT003 | SRS
482 | [26 empty] | _PV_SRS | Measurement SRS | BB1FT550 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
483 |  | BB1 | QT | 551 | BB1QT551 | Fluegas oxygen measurement 2 |  | SIL2 classified transmitter | [10 empty] | UPS | [17 empty] | 0 | 25 | % | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | QT001/dn65 flange with counterflange. 1 meter probe | SRS |  | UPS feed added | 4
484 | [26 empty] | _PV_SRS | Measurement SRS | BB1QT551 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
485 |  | BB1 | QT | 552 | BB1QT552 | Fluegas CO measurement | [12 empty] | UPS | [17 empty] | 0 | 5000 | ppm |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | QT001/dn65 flange with counterflange. 1 meter probe | Field IO |  | UPS feed added | 4
486 | [26 empty] | _PV | Measurement | BB1QT552 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
487 |  | BB1 | TT | 405 | BB1TT405 | Primary air temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSHK310B | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
488 | [26 empty] | _PV | Measurement | BB1TT405 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
489 |  | BB1 | PT | 406 | BB1PT406 | Boiler upper part pressure 3 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+JALAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
490 | [26 empty] | _PV_SRS | Measurement SRS | BB1PT406 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
491 |  | BB1 | TT | 415 | BB1TT415 | Boiler bed temperature middle level | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEM | G1/2" |  | 4008 | MEAS_ANA | TT004 | Field IO
492 | [26 empty] | _PV | Measurement | BB1TT415 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
493 |  | BB1 | TT | 416 | BB1TT416 | Boiler bed temperature lower level | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEM | G1/2" |  | 4008 | MEAS_ANA | TT004 | Field IO
494 | [26 empty] | _PV | Measurement | BB1TT416 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
495 |  | BB1 | TT | 410 | BB1TT410 | Boiler 1st draft temperature | [30 empty] | 0 | 1200 | °C | [20 empty] | E+H |  | G1/2" |  | 4008 | MEAS_ANA | TT003 | Field IO |  | Deleted | 4
496 | [26 empty] | _PV | Measurement | BB1TT410 | [35 empty] | MEAS_ANA |  | Field IO
497 |  | BB1 | TT | 116 | BB1TT116 | Steam temperature to air preheater | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4008 | MEAS_ANA | TT001 | Field IO
498 | [26 empty] | _PV | Measurement | BB1TT116 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
499 |  | BB1 | TT | 308 | BB1TT308 | Boiler 1st draft temperature | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEK | G1/2" |  | 4008 | MEAS_ANA | TT003 | Field IO
500 | [26 empty] | _PV | Measurement | BB1TT308 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
501 |  | BB1 | DM | 300 | BB1DM300 | Tertiary air damper 1 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
502 | [26 empty] | _SP | Setpoint position | BB1DM300 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
503 | [26 empty] | _POS | Position feedback | BB1DM300 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
504 |  | BB1 | DM | 400 | BB1DM400 | Primary air damper | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
505 | [26 empty] | _SP | Setpoint position | BB1DM400 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
506 | [26 empty] | _POS | Position feedback | BB1DM400 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
507 |  | BB1 | DM | 550 | BB1DM550 | Recirculation gas damper | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
508 | [26 empty] | _SP | Setpoint position | BB1DM550 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
509 | [26 empty] | _POS | Position feedback | BB1DM550 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
510 |  | BB1 | DM | 301 | BB1DM301 | Secondary air damper 4 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
511 | [26 empty] | _SP | Setpoint position | BB1DM301 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
512 | [26 empty] | _POS | Position feedback | BB1DM301 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
513 |  | BB1 | DM | 302 | BB1DM302 | Secondary air damper 3 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
514 | [26 empty] | _SP | Setpoint position | BB1DM302 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
515 | [26 empty] | _POS | Position feedback | BB1DM302 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
516 |  | BB1 | DM | 304 | BB1DM304 | Secondary air damper 1 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
517 | [26 empty] | _SP | Setpoint position | BB1DM304 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
518 | [26 empty] | _POS | Position feedback | BB1DM304 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
519 |  | BB1 | DM | 303 | BB1DM303 | Secondary air damper 2 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
520 | [26 empty] | _SP | Setpoint position | BB1DM303 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
521 | [26 empty] | _POS | Position feedback | BB1DM303 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
522 |  | BB1 | QT | 553 | BB1QT553 | Boiler room gas detector | [35 empty] | 1 | [21 empty] | 4008 | MEAS_ANA | XS001 | Field IO
523 | [26 empty] | _PV | Measurement | BB1QT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
524 |  | BB1 | TT | 408 | BB1TT408 | Secondary air fan motor bearing temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO
525 | [26 empty] | _PV | Measurement | BB1TT408 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
526 |  | BB1 | TT | 423 | BB1TT423 | Secondary air fan motor bearing temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
527 | [26 empty] | _PV | Measurement | BB1TT408 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
528 |  | BB1 | TT | 406 | BB1TT406 | Secondary air fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO
529 | [26 empty] | _PV | Measurement | BB1TT406 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
530 |  | BB1 | TT | 404 | BB1TT404 | Primary air fan motor bearing temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO
531 | [26 empty] | _PV | Measurement | BB1TT404 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
532 |  | BB1 | TT | 409 | BB1TT409 | Primary air fan motor bearing temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
533 | [26 empty] | _PV | Measurement | BB1TT404 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
534 |  | BB1 | TT | 402 | BB1TT402 | Primary air fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO
535 | [26 empty] | _PV | Measurement | BB1TT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
536 |  | BB1 | TT | 403 | BB1TT403 | Primary air fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO
537 | [26 empty] | _PV | Measurement | BB1TT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
538 |  | BB1 | TT | 421 | BB1TT421 | Primary air fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
539 | [26 empty] | _PV | Measurement | BB1TT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
540 |  | BB1 | TT | 407 | BB1TT407 | Secondary air fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO
541 | [26 empty] | _PV | Measurement | BB1TT407 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
542 |  | BB1 | TT | 422 | BB1TT422 | Secondary air fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
543 | [26 empty] | _PV | Measurement | BB1TT407 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
544 |  | BB1 | IV | 206 | BB1IV206 | Primary air preheater on-off valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 4 | 2 | 1 | [17 empty] | Auma | SA07.6-22 + RWG |  | Konwell/Auma | 4008 | MTR_VLV | AA003 |  |  | Changed to motor valve | 3
545 | [26 empty] | _CTLR_O | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
546 | [26 empty] | _CTRL_C | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
547 | [26 empty] | _TL_O | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
548 | [26 empty] | _TL_C | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
549 | [26 empty] | _FAULT | MCC fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Signal desciption changed | 4
550 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Added signal | 4
551 | [26 empty] | _POS | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
552 |  | BB1 | CV | 004 | BB1CV004 | Primary air preheater control valve | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
553 | [26 empty] | _SP | Setpoint position | BB1CV004 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
554 | [26 empty] | _POS | Position feedback | BB1CV004 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
555 |  | BB1 | GS | 215 | BB1GS215 | Primary air preheater on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4008 | MEAS_BIN | XS002/XS004 | MCC
556 | [26 empty] | _DI | Binary state | BB1GS215 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
557 |  | BB1 | GS | 216 | BB1GS216 | Primary air preheater on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4008 | MEAS_BIN | XS002/XS004 | MCC
558 | [26 empty] | _DI | Binary state | BB1GS216 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
559 |  | BB1 | IL | 001 | BB1IL001 | Alarm horn and light CO alarm | [34 empty] | 1 | [22 empty] | 4008 | ALM_HORN |  | Field IO |  | Description changed | 2
560 | [26 empty] | _CTLR | Command | BB1IL001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
561 |  | BB1 | PT | 409 | BB1PT409 | Secondary air pressure outer front wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+JAZ1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
562 | [26 empty] | _PV | Measurement | BB1PT400 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
563 |  | BB1 | PT | 411 | BB1PT411 | Secondary air pressure outer back wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+JAZ1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
564 | [26 empty] | _PV | Measurement | BB1PT401 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
565 |  | BB1 | PT | 407 | BB1PT407 | Tertiary air pressure right wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+JAZ1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
566 | [26 empty] | _PV | Measurement | BB1PT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
567 |  | BB1 | PT | 408 | BB1PT408 | Tertiary air pressure left wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+JAZ1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
568 | [26 empty] | _PV | Measurement | BB1PT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
569 |  | BB1 | EM | 400 | BB1EM400 | Primary air fan |  |  |  | 132 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4008 | FRQ_DIR |  |  |  | Size and voltage | 1
570 | [26 empty] | _R | Running | BB1FF400 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
571 | [26 empty] | _FAULT | MCC Fault | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
572 | [26 empty] | _SS | Load isolator (Safety switch) | BB1FF400 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIR |  |  |  | Hardwired DI | 4
573 | [26 empty] | _VSD_F | VFD Alarm | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
574 | [26 empty] | _CTRL | Run command | BB1FF400 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
575 | [26 empty] | _CUR | Current | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
576 | [26 empty] | _SR | Speed reference | BB1FF400 | [21 empty] | X | [13 empty] | FRQ_DIR
577 | [26 empty] | _AS | Actual speed | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
578 | [26 empty] | _TORQ | Torque | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
579 | [26 empty] | _RPM | RPM | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
580 |  | BB1 | SI | 400 | BB1SI400 | Primary air fan safety interlock | [38 empty] | 1 | [18 empty] | 4008 | FAN_SRS_DO
581 | [26 empty] | _SI | Safety interlock | BB1SI400 | [15 empty] | X | [19 empty] | FAN_SRS_DO
582 |  | BB1 | SI | 410 | BB1SI410 | Primary air fan run status SRS | [37 empty] | 1 | [19 empty] | 4008 |  |  | MCC |  | Signal added | 2
583 | [26 empty] | _R | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
584 |  | BB1 | ST | 400 | BB1ST400 | Primary air fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
585 | [26 empty] | _ST | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
586 |  | BB1 | EM | 401 | BB1EM401 | Secondary air fan |  |  |  | 45 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4008 | FRQ_DIR |  |  |  | Size, name and voltage | 1
587 | [26 empty] | _R | Running | BB1FF401 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
588 | [26 empty] | _FAULT | MCC Fault | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
589 | [26 empty] | _SS | Load isolator (Safety switch) | BB1FF401 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIR |  |  |  | Hardwired DI | 4
590 | [26 empty] | _VSD_F | VFD Alarm | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
591 | [26 empty] | _CTRL | Run command | BB1FF401 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
592 | [26 empty] | _CUR | Current | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
593 | [26 empty] | _SR | Speed reference | BB1FF401 | [21 empty] | X | [13 empty] | FRQ_DIR
594 | [26 empty] | _AS | Actual speed | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
595 | [26 empty] | _TORQ | Torque | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
596 | [26 empty] | _RPM | RPM | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
597 |  | BB1 | SI | 401 | BB1SI401 | Secondary air fan safety interlock | [38 empty] | 1 | [18 empty] | 4008 | FAN_SRS_DO
598 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
599 |  | BB1 | SI | 411 | BB1SI411 | Secondary air fan run status SRS | [37 empty] | 1 | [19 empty] | 4008 |  |  | MCC |  | Signal added | 2
600 | [26 empty] | _R | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
601 |  | BB1 | ST | 401 | BB1ST401 | Secondary air fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
602 | [26 empty] | _ST | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
603 |  | BB1 | HS | 601 | BB1HS601 | Fuel system emergency shutdown switch 1 |  | Near door that leads hydraulic units | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
604 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS101 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
605 |  | BB1 | HS | 602 | BB1HS602 | Fuel system emergency shutdown switch 2 |  | Outside near lift doors fuel receiving station | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
606 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
607 |  | BB1 | HS | 603 | BB1HS603 | Fuel system emergency shutdown switch 3 |  | Screening station | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
608 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
609 |  | BB1 | HS | 604 | BB1HS604 | Fuel system emergency shutdown switch 4 |  | Outside, on Fuel silo level near door | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
610 | [26 empty] | _DI_SRS | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
611 |  | BB1 | GS | 621 | BB1GS621 | Unloading station 3, block 3, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
612 | [26 empty] | _DI | Binary state | BB1GS621 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
613 |  | BB1 | GS | 611 | BB1GS611 | Unloading station 2, block 2, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
614 | [26 empty] | _DI | Binary state | BB1GS611 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
615 |  | BB1 | GS | 606 | BB1GS606 | Unloading station 1, block 1, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
616 | [26 empty] | _DI | Binary state | BB1GS606 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
617 |  | BB1 | GS | 614 | BB1GS614 | Unloading station 2, block 2, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
618 | [26 empty] | _DI | Binary state | BB1GS614 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
619 |  | BB1 | GS | 619 | BB1GS619 | Unloading station 3, block 3, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
620 | [26 empty] | _DI | Binary state | BB1GS619 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
621 |  | BB1 | GS | 651 | BB1GS651 | Disc screen by-pass damper limit switch to screen | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack | Instrument type added | 1
622 | [26 empty] | _DI | Binary state | BB1GS651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
623 |  | BB1 | PS | 602 | BB1PS602 | Hydraulics unit 1, block 3, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
624 | [26 empty] | _DI | Binary state | BB1PT602 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
625 |  | BB1 | GS | 615 | BB1GS615 | Unloading station 2, block 2, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
626 | [26 empty] | _DI | Binary state | BB1GS615 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
627 |  | BB1 | GS | 623 | BB1GS623 | Unloading station 3, block 3, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
628 | [26 empty] | _DI | Binary state | BB1GS623 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
629 |  | BB1 | ST | 651 | BB1ST651 | Scraper conveyor 2, rotation guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
630 | [26 empty] | _DI | Binary state | BB1ST651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
631 |  | BB1 | GS | 603 | BB1GS603 | Unloading station 1, block 1, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
632 | [26 empty] | _DI | Binary state | BB1GS603 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
633 |  | BB1 | PS | 601 | BB1PS601 | Hydraulics unit 1, block 2, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
634 | [26 empty] | _DI | Binary state | BB1PT601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
635 |  | BB1 | GS | 650 | BB1GS650 | Disc screen by-pass damper limit switch by-pass pos. | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack | Instrument type added | 1
636 | [26 empty] | _DI | Binary state | BB1GS650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
637 |  | BB1 | GS | 622 | BB1GS622 | Unloading station 3, block 3, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
638 | [26 empty] | _DI | Binary state | BB1GS622 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
639 |  | BB1 | GS | 602 | BB1GS602 | Unloading station 1, block 1, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
640 | [26 empty] | _DI | Binary state | BB1GS602 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
641 |  | BB1 | LS | 655 | BB1LS655 | Scraper conveyor 2, turning point blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
642 | [26 empty] | _DI | Binary state | BB1LS655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
643 |  | BB1 | GS | 607 | BB1GS607 | Unloading station 1, block 1, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
644 | [26 empty] | _DI | Binary state | BB1GS607 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
645 |  | BB1 | GS | 605 | BB1GS605 | Unloading station 1, block 1, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
646 | [26 empty] | _DI | Binary state | BB1GS605 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
647 |  | BB1 | LS | 652 | BB1LS652 | Unloading station 2, block 2, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
648 | [26 empty] | _DI | Binary state | BB1LS652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
649 |  | BB1 | GS | 601 | BB1GS601 | Unloading station 1, block 1, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
650 | [26 empty] | _DI | Binary state | BB1GS601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
651 |  | BB1 | LS | 608 | BB1LS608 | Hydraulics unit 1, low oil level alarm | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | LS001 | Field IO | Fuel station IO-rack
652 | [26 empty] | _DI | Binary state | BB1LS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
653 |  | BB1 | LS | 656 | BB1LS656 | Scraper conveyor 2, fuel silo side blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO
654 | [26 empty] | _DI | Binary state | BB1LS656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
655 |  | BB1 | LS | 600 | BB1LS600 | Hydraulics unit 1, leaking pool limit switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | LS001 | Field IO | Fuel station IO-rack
656 | [26 empty] | _DI | Binary state | BB1LS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
657 |  | BB1 | GS | 609 | BB1GS609 | Unloading station 2, block 2, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
658 | [26 empty] | _DI | Binary state | BB1GS609 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
659 |  | BB1 | LS | 650 | BB1LS650 | Scraper conveyor 1 bed height level switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
660 | [26 empty] | _DI | Binary state | BB1LS650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
661 |  | BB1 | GS | 617 | BB1GS617 | Unloading station 3, block 3, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
662 | [26 empty] | _DI | Binary state | BB1GS617 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
663 |  | BB1 | LS | 651 | BB1LS651 | Unloading station 3, block 3, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
664 | [26 empty] | _DI | Binary state | BB1LS651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
665 |  | BB1 | GS | 612 | BB1GS612 | Unloading station 2, block 2, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
666 | [26 empty] | _DI | Binary state | BB1GS612 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
667 |  | BB1 | LS | 654 | BB1LS654 | Scraper conveyor 1, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
668 | [26 empty] | _DI | Binary state | BB1LS654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
669 |  | BB1 | GS | 613 | BB1GS613 | Unloading station 2, block 2, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
670 | [26 empty] | _DI | Binary state | BB1GS613 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
671 |  | BB1 | GS | 620 | BB1GS620 | Unloading station 3, block 3, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
672 | [26 empty] | _DI | Binary state | BB1GS620 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
673 |  | BB1 | GS | 618 | BB1GS618 | Unloading station 3, block 3, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
674 | [26 empty] | _DI | Binary state | BB1GS618 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
675 |  | BB1 | PS | 600 | BB1PS600 | Hydraulics unit 1, block 1, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
676 | [26 empty] | _DI | Binary state | BB1PT600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
677 |  | BB1 | GS | 608 | BB1GS608 | Unloading station 2, block 2, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
678 | [26 empty] | _DI | Binary state | BB1GS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
679 |  | BB1 | GS | 604 | BB1GS604 | Unloading station 1, block 1, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
680 | [26 empty] | _DI | Binary state | BB1GS604 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
681 |  | BB1 | LS | 653 | BB1LS653 | Unloading station 1, block 1, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
682 | [26 empty] | _DI | Binary state | BB1LS653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
683 |  | BB1 | GS | 616 | BB1GS616 | Unloading station 3, block 3, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
684 | [26 empty] | _DI | Binary state | BB1GS616 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 600 | BB1GS600 | Unloading station 1, block 1, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
686 | [26 empty] | _DI | Binary state | BB1GS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
687 |  | BB1 | ST | 650 | BB1ST650 | Scraper conveyor 1, rotation guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
688 | [26 empty] | _DI | Binary state | BB1ST650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
689 |  | BB1 | TT | 650 | BB1TT650 | Scraper conveyor 1, temperature measurement | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TMT82-55V0/101 |  |  | 4009 | MEAS_ANA | TT006 | Field IO | Fuel station IO-rack
690 | [26 empty] | _PV | Measurement | BB1TT650 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
691 |  | BB1 | GS | 610 | BB1GS610 | Unloading station 2, block 2, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
692 | [26 empty] | _DI | Binary state | BB1GS610 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
693 |  | BB1 | LT | 611 | BB1LT611 | Unloading station 1 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
694 | [26 empty] | _PV | Measurement | BB1LT509 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
695 |  | BB1 | LT | 612 | BB1LT612 | Unloading station 3 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
696 | [26 empty] | _PV | Measurement | BB1LT513 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
697 |  | BB1 | LT | 613 | BB1LT613 | Unloading station 2 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
698 | [26 empty] | _PV | Measurement | BB1LT512 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
699 |  | BB1 | SV | 601 | BB1SV601 | Control Valve push feeders unloading station 1 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
700 | [26 empty] | _CTLR_OUT | Control out | BB1SV601 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
701 | [26 empty] | _CTLR_IN | Control in | BB1SV601 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
702 |  | BB1 | ST | 675 | BB1ST675 | Leveling roller 3 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
703 | [26 empty] | _DI | Binary state | BB1ST703 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
704 |  | BB1 | SV | 603 | BB1SV603 | Control Valve push feeders unloading station 3 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
705 | [26 empty] | _CTLR_OUT | Control out | BB1SV603 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
706 | [26 empty] | _CTLR_IN | Control in | BB1SV603 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
707 |  | BB1 | SV | 602 | BB1SV602 | Control Valve push feeders unloading station 2 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
708 | [26 empty] | _CTLR_OUT | Control out | BB1SV602 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
709 | [26 empty] | _CTLR_IN | Control in | BB1SV602 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
710 |  | BB1 | TS | 608 | BB1TS608 | High temperature switch hydraulic oil | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack
711 | [26 empty] | _DI | Binary state | BB1TS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
712 |  | BB1 | ST | 673 | BB1ST673 | Leveling roller 1 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
713 | [26 empty] | _DI | Binary state | BB1ST701 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
714 |  | BB1 | TS | 600 | BB1TS600 | Hydraulics unit, thermostat for heater | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack
715 | [26 empty] | _DI | Binary state | BB1TS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
716 |  | BB1 | ST | 674 | BB1ST674 | Leveling roller 2 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
717 | [26 empty] | _DI | Binary state | BB1ST702 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
718 |  | BB1 | PS | 605 | BB1PS605 | Hydraulic oil return block 3 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
719 | [26 empty] | _DI | Binary state | BB1PS603 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
720 |  | BB1 | PS | 603 | BB1PS603 | Hydraulic oil return block 1 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
721 | [26 empty] | _DI | Binary state | BB1PS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
722 |  | BB1 | PS | 604 | BB1PS604 | Hydraulic oil return block 2 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
723 | [26 empty] | _DI | Binary state | BB1PS601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
724 |  | BB1 | EM | 603 | BB1EM603 | Fuel reception hydraulic unit 1, pump 1 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 3 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
725 | [26 empty] | _R | Running | BB1PU603 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH |  |  |  | Motor details | 1
726 | [26 empty] | _FAULT | MCC Fault | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH |  |  |  | Motor details | 1
727 | [26 empty] | _SS | Load isolator (Safety switch) | BB1PU603 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIRH |  |  |  | Hardwired DI | 4
728 | [26 empty] | _VSD_F | VFD Alarm | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
729 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
730 | [26 empty] | _CTRL | Run command | BB1PU603 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
731 | [26 empty] | _CUR | Current | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
732 | [26 empty] | _SR | Speed reference | BB1PU603 | [21 empty] | X | [13 empty] | FRQ_DIRH
733 | [26 empty] | _AS | Actual speed | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
734 | [26 empty] | _TORQ | Torque | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
735 | [26 empty] | _RPM | RPM | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
736 | [26 empty] | _L_RUN | Local run command | BB1PU603 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
737 | [26 empty] | _L/R | Local mode switch | BB1PU603 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
738 |  | BB1 | SI | 603 | BB1SI603 | Fuel reception hydraulic unit 1, pump 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
739 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
740 |  | BB1 | EM | 604 | BB1EM604 | Fuel reception hydraulic unit 1, pump 2 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 3 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
741 | [26 empty] | _R | Running | BB1PU604 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH
742 | [26 empty] | _FAULT | MCC Fault | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
743 | [26 empty] | _SS | Load isolator (Safety switch) | BB1PU604 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIRH |  |  |  | Hardwired DI | 4
744 | [26 empty] | _VSD_F | VFD Alarm | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
745 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
746 | [26 empty] | _CTRL | Run command | BB1PU604 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
747 | [26 empty] | _CUR | Current | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
748 | [26 empty] | _SR | Speed reference | BB1PU604 | [21 empty] | X | [13 empty] | FRQ_DIRH
749 | [26 empty] | _AS | Actual speed | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
750 | [26 empty] | _TORQ | Torque | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
751 | [26 empty] | _RPM | RPM | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
752 | [26 empty] | _L_RUN | Local run command | BB1PU604 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
753 | [26 empty] | _L/R | Local mode switch | BB1PU604 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
754 |  | BB1 | SI | 604 | BB1SI604 | Fuel reception hydraulic unit 1, pump 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
755 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
756 |  | BB1 | EM | 605 | BB1EM605 | Fuel reception hydraulic unit 1, pump 3 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 3 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
757 | [26 empty] | _R | Running | BB1PU605 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH
758 | [26 empty] | _FAULT | MCC Fault | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
759 | [26 empty] | _SS | Load isolator (Safety switch) | BB1PU605 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIRH |  |  |  | Hardwired DI | 4
760 | [26 empty] | _VSD_F | VFD Alarm | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
761 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
762 | [26 empty] | _CTRL | Run command | BB1PU605 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
763 | [26 empty] | _CUR | Current | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
764 | [26 empty] | _SR | Speed reference | BB1PU605 | [21 empty] | X | [13 empty] | FRQ_DIRH
765 | [26 empty] | _AS | Actual speed | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
766 | [26 empty] | _TORQ | Torque | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
767 | [26 empty] | _RPM | RPM | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
768 | [26 empty] | _L_RUN | Local run command | BB1PU605 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
769 | [26 empty] | _L/R | Local mode switch | BB1PU605 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
770 |  | BB1 | SI | 605 | BB1SI605 | Fuel reception hydraulic unit 1, pump 3 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
771 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
772 |  | BB1 | EM | 673 | BB1EM673 | Levelling roller 1 |  |  |  | 2,2 |  |  | 415 | [26 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size changed | 3
773 | [26 empty] | _R_FWD | Running FWD | BB1EM703 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
774 | [26 empty] | _R_BWD | Running BWD | BB1EM703 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
775 | [26 empty] | _FAULT | MCC Fault | BB1EM703 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
776 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
777 | [26 empty] | _L_FWD | Local FWD command | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
778 | [26 empty] | _L_BWD | Local BWD command | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
779 | [26 empty] | _L/R | Local mode switch | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
780 | [26 empty] | _CTRL_F | Run command FWD | BB1EM703 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
781 | [26 empty] | _CTRL_B | Run command BWD | BB1EM703 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
782 | [26 empty] | _CUR | Current | BB1EM703 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
783 |  | BB1 | EM | 674 | BB1EM674 | Levelling roller 2 |  |  |  | 3 |  |  | 415 | [26 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size changed | 3
784 | [26 empty] | _R_FWD | Running FWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
785 | [26 empty] | _R_BWD | Running BWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
786 | [26 empty] | _FAULT | MCC Fault | BB1EM704 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
787 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
788 | [26 empty] | _L_FWD | Local FWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
789 | [26 empty] | _L_BWD | Local BWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
790 | [26 empty] | _L/R | Local mode switch | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
791 | [26 empty] | _CTRL_F | Run command FWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
792 | [26 empty] | _CTRL_B | Run command BWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
793 | [26 empty] | _CUR | Current | BB1EM704 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
794 |  | BB1 | EM | 675 | BB1EM675 | Levelling roller 3 | [57 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor deleted | 2
795 | [26 empty] | _R_FWD | Running FWD | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
796 | [26 empty] | _R_BWD | Running BWD | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
797 | [26 empty] | _FAULT | MCC Fault | BB1EM703 | [28 empty] | NC | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
798 | [26 empty] | _L_FWD | Local FWD command | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
799 | [26 empty] | _L_BWD | Local BWD command | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
800 | [26 empty] | _L/R | Local mode switch | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
801 | [26 empty] | _CTRL_F | Run command FWD | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
802 | [26 empty] | _CTRL_B | Run command BWD | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
803 | [26 empty] | _CUR | Current | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
804 |  | BB1 | EM | 658 | BB1EM658 | Scraper Conveyor 1 |  |  |  | 15 |  |  | 415 | [26 empty] | 4 | [7 empty] | 4 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Tag changed and motor details | 1
805 | [26 empty] | _R_FWD | Running FWD | BB1CO653 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
806 | [26 empty] | _R_BWD | Running BWD | BB1CO653 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
807 | [26 empty] | _FAULT | MCC Fault | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
808 | [26 empty] | _SS | Load isolator (Safety switch) | BB1CO653 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
809 | [26 empty] | _VSD_F | VFD Alarm | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
810 | [26 empty] | _L_FWD | Local FWD command | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
811 | [26 empty] | _L_BWD | Local BWD command | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
812 | [26 empty] | _L/R | Local mode switch | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
813 | [26 empty] | _CTRL_F | Run command FWD | BB1CO653 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
814 | [26 empty] | _CTRL_B | Run command BWD | BB1CO653 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
815 | [26 empty] | _CUR | Current | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
816 | [26 empty] | _SR | Speed reference | BB1CO653 | [21 empty] | X | [13 empty] | FRQ_REVH
817 | [26 empty] | _AS | Actual speed | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
818 | [26 empty] | _TORQ | Torque | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
819 | [26 empty] | _RPM | RPM | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
820 |  | BB1 | SI | 658 | BB1SI658 | Scraper Conveyor 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
821 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
822 |  | BB1 | EM | 670 | BB1EM670 | Belt magnet |  |  |  | 2.2 | 4.2 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIRH_BUS |  |  |  | Motor details and type | 1
823 | [26 empty] | _R | Running | BB1CO654 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
824 | [26 empty] | _R_BWD | Running BWD | BB1CO654 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
825 | [26 empty] | _FAULT | MCC Fault | BB1CO654 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
826 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS |  |  |  | Added signal | 4
827 | [26 empty] | _L_RUN | Local run command | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
828 | [26 empty] | _L_BWD | Local BWD command | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
829 | [26 empty] | _L/R | Local mode switch | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
830 | [26 empty] | _CTRL | Run command | BB1CO654 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
831 | [26 empty] | _CTRL_B | Run command BWD | BB1CO654 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
832 | [26 empty] | _CUR | Current | BB1CO654 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
833 |  | BB1 | ST | 654 | BB1ST654 | Belt magnet rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
834 | [26 empty] | _DI | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
835 |  | BB1 | GS | 661 | BB1GS661 | Belt magnet deviation detector 1 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCRT115EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
836 | [26 empty] | _DI | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
837 |  | BB1 | GS | 662 | BB1GS662 | Belt magnet deviation detector 2 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCRT115EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
838 | [26 empty] | _DI | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
839 |  | BB1 | EM | 659 | BB1EM659 | Belt Conveyor |  |  |  | 4 | 7.6 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Motor details and type | 1
840 | [26 empty] | _R_FWD | Running FWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
841 | [26 empty] | _R_BWD | Running BWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
842 | [26 empty] | _FAULT | MCC Fault | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
843 | [26 empty] | _SS | Load isolator (Safety switch) | BB1CO655 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
844 | [26 empty] | _VSD_F | VFD Alarm | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
845 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
846 | [26 empty] | _L_FWD | Local FWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
847 | [26 empty] | _L_BWD | Local BWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
848 | [26 empty] | _L/R | Local mode switch | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
849 | [26 empty] | _CTRL_F | Run command FWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
850 | [26 empty] | _CTRL_B | Run command BWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
851 | [26 empty] | _CUR | Current | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
852 | [26 empty] | _SR | Speed reference | BB1CO655 | [21 empty] | X | [13 empty] | FRQ_REVH
853 | [26 empty] | _AS | Actual speed | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
854 | [26 empty] | _TORQ | Torque | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
855 | [26 empty] | _RPM | RPM | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
856 | [7 empty] | Brake |  |  |  |  | 240 | [55 empty] | Feed added | 1
857 |  | BB1 | SI | 659 | BB1SI659 | Belt Conveyor safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
858 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
859 |  | BB1 | ST | 652 | BB1ST652 | Belt conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
860 | [26 empty] | _DI | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
861 |  | BB1 | GS | 659 | BB1GS659 | Belt conveyor deviation detector 1 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Steute | Ex ES 98 SR-11-3GD |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
862 | [26 empty] | _DI | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
863 |  | BB1 | GS | 660 | BB1GS660 | Belt conveyor deviation detector 2 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Steute | Ex ES 98 SR-11-3GD |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
864 | [26 empty] | _DI | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
865 |  | BB1 | GS | 663 | BB1GS663 | Belt conveyor oversize detector | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
866 | [26 empty] | _DI | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
867 |  | BB1 | EM | 675 | BB1EM75 | Disc screen drive 1 |  |  |  | 7.5 | 13.7 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Tag changed | 3
868 | [26 empty] | _R_FWD | Running FWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
869 | [26 empty] | _R_BWD | Running BWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
870 | [26 empty] | _FAULT | MCC Fault | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
871 | [26 empty] | _SS | Load isolator (Safety switch) | BB1CO655 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
872 | [26 empty] | _VSD_F | VFD Alarm | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
873 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
874 | [26 empty] | _L_FWD | Local FWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
875 | [26 empty] | _L_BWD | Local BWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
876 | [26 empty] | _L/R | Local mode switch | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
877 | [26 empty] | _CTRL_F | Run command FWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
878 | [26 empty] | _CTRL_B | Run command BWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
879 | [26 empty] | _CUR | Current | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
880 | [26 empty] | _SR | Speed reference | BB1CO655 | [21 empty] | X | [13 empty] | FRQ_REVH
881 | [26 empty] | _AS | Actual speed | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
882 | [26 empty] | _TORQ | Torque | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
883 | [26 empty] | _RPM | RPM | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
884 |  | BB1 | SI | 675 | BB1SI675 | Disc screen drive 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
885 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
886 |  | BB1 | EM | 676 | BB1EM676 | Disc screen drive 2 |  |  |  | 7.5 | 13.7 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH | XS002 |  |  | Tag changed | 3
887 | [26 empty] | _R_FWD | Running FWD | BB1CO656 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
888 | [26 empty] | _R_BWD | Running BWD | BB1CO656 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
889 | [26 empty] | _FAULT | MCC Fault | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
890 | [26 empty] | _SS | Load isolator (Safety switch) | BB1CO656 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
891 | [26 empty] | _VSD_F | VFD Alarm | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
892 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
893 | [26 empty] | _L_FWD | Local FWD command | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
894 | [26 empty] | _L_BWD | Local BWD command | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
895 | [26 empty] | _L/R | Local mode switch | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
896 | [26 empty] | _CTRL_F | Run command FWD | BB1CO656 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
897 | [26 empty] | _CTRL_B | Run command BWD | BB1CO656 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
898 | [26 empty] | _CUR | Current | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
899 | [26 empty] | _SR | Speed reference | BB1CO656 | [21 empty] | X | [13 empty] | FRQ_REVH
900 | [26 empty] | _AS | Actual speed | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
901 | [26 empty] | _TORQ | Torque | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
902 | [26 empty] | _RPM | RPM | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
903 |  | BB1 | SI | 676 | BB1SI676 | Disc screen drive 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
904 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
905 |  | BB1 | ST | 656 | BB1ST656 | Disc screen drive 1 rotation guard | [33 empty] | 1 | [19 empty] | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument type added | 1
906 | [26 empty] | _DI | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
907 |  | BB1 | ST | 657 | BB1ST657 | Disc screen drive 2 rotation guard | [33 empty] | 1 | [19 empty] | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument type added | 1
908 | [26 empty] | _DI | Binary state | BB1ST657 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
909 |  | BB1 | EM | 672 | BB1EM672 | Scraper Conveyor 2 |  |  |  | 18,5 |  |  | 415 | [26 empty] | 4 | [7 empty] | 4 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Motor size changed | 3
910 | [26 empty] | _R_FWD | Running FWD | BB1CO657 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
911 | [26 empty] | _R_BWD | Running BWD | BB1CO657 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
912 | [26 empty] | _FAULT | MCC Fault | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
913 | [26 empty] | _SS | Load isolator (Safety switch) | BB1CO657 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
914 | [26 empty] | _VSD_F | VFD Alarm | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
915 | [26 empty] | _L_FWD | Local FWD command | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
916 | [26 empty] | _L_BWD | Local BWD command | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
917 | [26 empty] | _L/R | Local mode switch | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
918 | [26 empty] | _CTRL_F | Run command FWD | BB1CO657 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
919 | [26 empty] | _CTRL_B | Run command BWD | BB1CO657 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
920 | [26 empty] | _CUR | Current | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
921 | [26 empty] | _SR | Speed reference | BB1CO657 | [21 empty] | X | [13 empty] | FRQ_REVH
922 | [26 empty] | _AS | Actual speed | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
923 | [26 empty] | _TORQ | Torque | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
924 | [26 empty] | _RPM | RPM | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
925 |  | BB1 | SI | 672 | BB1SI672 | Scraper Conveyor 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
926 | [26 empty] | _SI | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
927 |  | BB1 | IJ | 002 | BB1IJ002 | Scraper Conveyor 1 Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4009 | ALM_HORN |  | Field IO | Fuel station IO-rack
928 | [26 empty] | _CTLR | Command | BB1IJ002 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO | Fuel station IO-rack
929 |  | BB1 | IJ | 001 | BB1IJ001 | Scraper Conveyor 2 Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4009 | ALM_HORN |  | Field IO
930 | [26 empty] | _CTLR | Command | BB1IJ001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
931 |  | BB1 | EM | 601 | BB1EM601 | Dust extraction rotary feeder |  | preliminary size |  | 0,75 | [29 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size added | 3
932 | [26 empty] | _R_FWD | Running FWD | BB1RV601 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
933 | [26 empty] | _R_BWD | Running BWD | BB1RV601 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
934 | [26 empty] | _FAULT | MCC Fault | BB1RV601 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
935 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
936 | [26 empty] | _L_FWD | Local FWD command | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
937 | [26 empty] | _L_BWD | Local BWD command | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
938 | [26 empty] | _L/R | Local mode switch | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
939 | [26 empty] | _CTRL_F | Run command FWD | BB1RV601 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
940 | [26 empty] | _CTRL_B | Run command BWD | BB1RV601 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
941 | [26 empty] | _CUR | Current | BB1RV601 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
942 |  | BB1 | EM | 606 | BB1EM606 | Dust extraction fan |  | preliminary size |  | 30 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIR |  |  |  | Changed to VSD use | 4
943 | [26 empty] | _R | Running | BB1FF401 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
944 | [26 empty] | _FAULT | MCC Fault | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
945 | [26 empty] | _SS | Load isolator (Safety switch) | BB1FF401 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIR |  |  |  | Hardwired DI | 4
946 | [26 empty] | _VSD_F | VFD Alarm | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
947 | [26 empty] | _CTRL | Run command | BB1FF401 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
948 | [26 empty] | _CUR | Current | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
949 | [26 empty] | _SR | Speed reference | BB1FF401 | [21 empty] | X | [13 empty] | FRQ_DIR
950 | [26 empty] | _AS | Actual speed | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
951 | [26 empty] | _TORQ | Torque | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
952 | [26 empty] | _RPM | RPM | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
953 |  | BB1 | EH | 600 | BB1EH600 | Electric heater hydraulic unit |  | preliminary size |  | 1,5 | [29 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIR_BUS
954 | [26 empty] | _R | Running | BB1EH600 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
955 | [26 empty] | _FAULT | MCC Fault | BB1EH600 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
956 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
957 | [26 empty] | _CTRL | Run command | BB1EH600 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
958 | [26 empty] | _CUR | Current | BB1EH600 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
959 |  | BB1 | CV | 402 | BB1CV402 | Fuel chute B carrying air control valve 2 | [35 empty] | 1 | 1 | [20 empty] | 4010 | CONT_VLV | AA002 | Field IO
960 | [26 empty] | _SP | Setpoint position | BB1CV402 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
961 | [26 empty] | _POS | Position feedback | BB1CV402 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
962 |  | BB1 | CV | 403 | BB1CV403 | Fuel chute A carrying air control valve 1 | [35 empty] | 1 | 1 | [20 empty] | 4010 | CONT_VLV | AA002 | Field IO
963 | [26 empty] | _SP | Setpoint position | BB1CV403 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
964 | [26 empty] | _POS | Position feedback | BB1CV403 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
965 |  | BB1 | GS | 652 | BB1GS652 | Explosion hatch limit switch 1 | [33 empty] | 1 | [19 empty] | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
966 | [26 empty] | _DI | Binary state | BB1GS652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
967 |  | BB1 | GS | 653 | BB1GS653 | Explosion hatch limit switch 2 | [33 empty] | 1 | [19 empty] | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
968 | [26 empty] | _DI | Binary state | BB1GS653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
969 |  | BB1 | GS | 654 | BB1GS654 | Explosion hatch limit switch 3 | [33 empty] | 0 | [22 empty] | LAITEX | 4010 | MEAS_BIN | XS002 |  |  | Instrument removed | 1
970 | [26 empty] | _DI | Binary state | BB1GS654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
971 |  | BB1 | GS | 655 | BB1GS655 | Explosion hatch limit switch 4 | [33 empty] | 0 | [22 empty] | LAITEX | 4010 | MEAS_BIN | XS002 |  |  | Instrument removed | 1
972 | [26 empty] | _DI | Binary state | BB1GS655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
973 |  | BB1 | LS | 657 | BB1LS657 | Fuel silo discharge screw blockage switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument type added | 1
974 | [26 empty] | _DI | Binary state | BB1LS657 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
975 |  | BB1 | LS | 658 | BB1LS658 | Fuel silo cross conveyor blockage switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Description changed | 2
976 | [26 empty] | _DI | Binary state | BB1LS658 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
977 |  | BB1 | LS |  | BB1LS | Fuel silo cross conveyor explosion hatch limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 2
978 | [26 empty] | _DI | Binary state | BB1LS658 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
979 |  | BB1 | LS | 659 | BB1LS659 | Fuel feeding screw 1 blockage switch | [33 empty] | 1 | [16 empty] | 3-wire |  |  | Telemechanique | XS630B1PAL10EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | 3-wire | 2
980 | [26 empty] | _DI | Binary state | BB1LS659 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
981 |  | BB1 | LS | 660 | BB1LS660 | Fuel feeding screw 2 blockage switch | [33 empty] | 1 | [16 empty] | 3-wire |  |  | Telemechanique | XS630B1PAL10EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | 3-wire | 2
982 | [26 empty] | _DI | Binary state | BB1LS660 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
983 |  | BB1 | LT | 650 | BB1LT650 | Fuel silo level radar 1 | [6 empty] | 240 | [5 empty] | UPS | [17 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT10-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 | Field IO |  | UPS feed added | 4
984 | [26 empty] | _PV | Measurement | BB1LT650 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA |  | Field IO
985 |  | BB1 | LT | 651 | BB1LT651 | Fuel silo level radar 2 | [6 empty] | 240 | [5 empty] | UPS | [17 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT10-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 |  |  | UPS feed added | 4
986 | [26 empty] | _PV | Measurement | BB1LT650 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA
987 |  | BB1 | LT | 652 | BB1LT652 | Fuel pocket level | [6 empty] | 240 | [5 empty] | UPS | [17 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT20-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 | Field IO |  | UPS feed added | 4
988 | [26 empty] | _PV | Measurement | BB1LT652 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA |  | Field IO
989 |  | BB1 | ST | 649 | BB1ST649 | Fuel silo cross conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Description modified | 3
990 | [26 empty] | _DI | Binary state | BB1ST649 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
991 |  | BB1 | ST | 652 | BB1ST652 | Rotating fuel spreader rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
992 | [26 empty] | _DI | Binary state | BB1ST652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
993 |  | BB1 | ST | 653 | BB1ST653 | Fuel feeding screw 2 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | 2-wire | 2
994 | [26 empty] | _DI | Binary state | BB1ST653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
995 |  | BB1 | ST | 654 | BB1ST654 | Fuel feeding rotary feeder 1 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
996 | [26 empty] | _DI | Binary state | BB1ST654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
997 |  | BB1 | ST | 655 | BB1ST655 | Fuel feeding rotary feeder 2 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
998 | [26 empty] | _DI | Binary state | BB1ST655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
999 |  | BB1 | ST | 659 | BB1ST659 | Fuel feeding screw 1 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | 2-wire | 2
1000 | [26 empty] | _DI | Binary state | BB1ST659 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1001 |  | BB1 | SV | 400 | BB1SV400 | Sealing air to rotary feeder solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
1002 | [26 empty] | _CTLR | Control command | BB1SV400 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1003 |  | BB1 | SV | 406 | BB1SV406 | Sealing air to rotary feeder solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
1004 | [26 empty] | _CTLR | Control command | BB1SV406 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1005 |  | BB1 | SV | 950 | BB1SV950 | Fuel silo fire water control valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
1006 | [26 empty] | _CTLR | Control command | BB1SV950 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1007 |  | BB1 | SV | 951 | BB1SV951 | Fuel pocket fire water control valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
1008 | [26 empty] | _CTLR | Control command | BB1SV951 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1009 |  | BB1 | TT | 652 | BB1TT652 | Fuel silo temperature measurement | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TST41N-MRDD82HA4P |  |  | 4010 | MEAS_ANA | TT006 | Field IO
1010 | [26 empty] | _PV | Measurement | BB1TT652 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1011 |  | BB1 | TT | 653 | BB1TT653 | Fuel pocket temperature | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TST41N-MRDD82HA4P |  |  | 4010 | MEAS_ANA | TT006 | Field IO
1012 | [26 empty] | _PV | Measurement | BB1TT653 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1013 |  | BB1 | IV | 650 | BB1IV650 | Slide gate valve |  |  |  | 2.2 | 4.2 | 1500 | 415 | [26 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor added | 1
1014 | [26 empty] | _R_FWD | Running FWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1015 | [26 empty] | _R_BWD | Running BWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1016 | [26 empty] | _FAULT | MCC Fault | BB1EM704 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1017 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
1018 | [26 empty] | _L_FWD | Local FWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1019 | [26 empty] | _L_BWD | Local BWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1020 | [26 empty] | _L/R | Local mode switch | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1021 | [26 empty] | _CTRL_F | Run command FWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1022 | [26 empty] | _CTRL_B | Run command BWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1023 | [26 empty] | _CUR | Current | BB1EM704 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1024 |  | BB1 | GS | 655 | BB1GS655 | Slide gate valve open limit switch | [33 empty] | 1 | [19 empty] | Telemecanique | XSAV-11801 |  |  | 4010 | MEAS_BIN |  | Field IO |  | Instrument added | 1
1025 | [26 empty] | _DI | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1026 |  | BB1 | GS | 656 | BB1GS656 | Slide gate valve close limit switch | [33 empty] | 1 | [19 empty] | Telemecanique | XSAV-11801 |  |  | 4010 | MEAS_BIN |  | Field IO |  | Instrument added | 1
1027 | [26 empty] | _DI | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1028 |  | BB1 | HC | 601 | BB1HC601 | Crane feed |  | 16 A breaker |  |  |  |  | 415 | [55 empty] | Crane added | 1
1029 |  | BB1 | FL | 650 | BB1FL650 | Fuel silo dust filter control box feed |  | 10 A breaker |  |  |  |  | 240 | [27 empty] | 1 | [22 empty] | 4010 | MCCB_1ph |  |  |  | Voltage level added | 1
1030 | [26 empty] | _R | Cleaning on | BB1FF650 | [11 empty] | X | [16 empty] | Pot.free | [10 empty] | Signal added | 1
1031 |  | BB1 | EM | 651 | BB1EM651 | Fuel silo dust filter fan | [33 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIR_BUS
1032 | [26 empty] | _R | Running | BB1FF650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1033 | [26 empty] | _FAULT | MCC Fault | BB1FF650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1034 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1035 | [26 empty] | _CTRL | Run command | BB1FF650 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1036 | [26 empty] | _CUR | Current | BB1FF650 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1037 |  | BB1 | EM | 652 | BB1EM652 | Rotating fuel spreader |  |  |  | 0.75 | 1.7 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIRH_BUS |  |  |  | Size, current and voltage | 1
1038 | [26 empty] | _R | Running | BB1SD650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
1039 | [26 empty] | _FAULT | MCC Fault | BB1SD650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
1040 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS |  |  |  | Added signal | 4
1041 | [26 empty] | _L_RUN | Local run command | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
1042 | [26 empty] | _L/R | Local mode switch | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
1043 | [26 empty] | _CTRL | Run command | BB1SD650 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
1044 | [26 empty] | _CUR | Current | BB1SD650 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
1045 |  | BB1 | EM | 662 | BB1EM662 | Fuel silo screw discharger |  |  |  | 22 | 39,5 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
1046 | [26 empty] | _R_FWD | Running FWD | BB1FD662 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1047 | [26 empty] | _R_BWD | Running BWD | BB1FD662 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1048 | [26 empty] | _FAULT | MCC Fault | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1049 | [26 empty] | _SS | Load isolator (Safety switch) | BB1FD662 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
1050 | [26 empty] | _VSD_F | VFD Alarm | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1051 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1052 | [26 empty] | _L_FWD | Local FWD command | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1053 | [26 empty] | _L_BWD | Local BWD command | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1054 | [26 empty] | _L/R | Local mode switch | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1055 | [26 empty] | _CTRL_F | Run command FWD | BB1FD662 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1056 | [26 empty] | _CTRL_B | Run command BWD | BB1FD662 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1057 | [26 empty] | _CUR | Current | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
1058 | [26 empty] | _SR | Speed reference | BB1FD662 | [21 empty] | X | [13 empty] | FRQ_REVH
1059 | [26 empty] | _AS | Actual speed | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
1060 | [26 empty] | _TORQ | Torque | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
1061 | [26 empty] | _RPM | RPM | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
1062 |  | BB1 | EM | 650 | BB1EM650 | Slewing motor for screw |  |  |  | 2.2 | 4.2 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
1063 | [26 empty] | _R_FWD | Running FWD | BB1EM650 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1064 | [26 empty] | _R_BWD | Running BWD | BB1EM650 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1065 | [26 empty] | _FAULT | MCC Fault | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1066 | [26 empty] | _SS | Load isolator (Safety switch) | BB1EM650 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
1067 | [26 empty] | _VSD_F | VFD Alarm | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1068 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1069 | [26 empty] | _L_FWD | Local FWD command | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1070 | [26 empty] | _L_BWD | Local BWD command | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1071 | [26 empty] | _L/R | Local mode switch | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1072 | [26 empty] | _CTRL_F | Run command FWD | BB1EM650 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1073 | [26 empty] | _CTRL_B | Run command BWD | BB1EM650 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1074 | [26 empty] | _CUR | Current | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
1075 | [26 empty] | _SR | Speed reference | BB1EM650 | [21 empty] | X | [13 empty] | FRQ_REVH
1076 | [26 empty] | _AS | Actual speed | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
1077 | [26 empty] | _TORQ | Torque | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
1078 | [26 empty] | _RPM | RPM | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
1079 |  | BB1 | EM | 660 | BB1EM660 | Cooling fan for slewing motor |  |  |  | 0.09 |  |  | 240 | [26 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIR_BUS |  |  |  | Motor typical changed | 4
1080 | [26 empty] | _R | Running | BB1FF650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1081 | [26 empty] | _FAULT | MCC Fault | BB1FF650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1082 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1083 | [26 empty] | _CTRL | Run command | BB1FF650 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1084 | [26 empty] | _CUR | Current | BB1FF650 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1085 |  | BB1 | EM | 654 | BB1EM654 | Lubrication unit |  | Fuse size C6A |  | 0.2 | 0.8 |  | 240 | [26 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIR_BUS |  |  |  | Motor typical changed | 4
1086 | [26 empty] | _R | Running | BB1FF650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1087 | [26 empty] | _FAULT | MCC Fault | BB1FF650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1088 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1089 | [26 empty] | _CTRL | Run command | BB1FF650 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1090 | [26 empty] | _CUR | Current | BB1FF650 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1091 |  | BB1 | LS | 661 | BB1LS661 | Lubrication alarm screw discharger | [33 empty] | 1 | [19 empty] | SKF | KFGS | LAITEX |  | 4010 | MEAS_BIN |  | Field IO |  | Tag changed | 3
1092 | [26 empty] | _DI | Binary state | BB1QA650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1093 |  | BB1 | EH | 662 | BB1EH662 | Heater for slipring unit |  |  |  | 0.4 | 1.7 |  | 240 | [26 empty] | 1 | [23 empty] | 4010 | MCCB_1ph |  |  |  | Details | 1
1094 |  | BB1 | EM | 663 | BB1EM663 | Fuel silo cross conveyor |  |  |  | 4 | 7.6 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
1095 | [26 empty] | _R_FWD | Running FWD | BB1FD663 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1096 | [26 empty] | _R_BWD | Running BWD | BB1FD663 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1097 | [26 empty] | _FAULT | MCC Fault | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1098 | [26 empty] | _SS | Load isolator (Safety switch) | BB1FD663 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
1099 | [26 empty] | _VSD_F | VFD Alarm | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1100 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1101 | [26 empty] | _L_FWD | Local FWD command | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1102 | [26 empty] | _L_BWD | Local BWD command | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1103 | [26 empty] | _L/R | Local mode switch | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1104 | [26 empty] | _CTRL_F | Run command FWD | BB1FD663 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1105 | [26 empty] | _CTRL_B | Run command BWD | BB1FD663 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1106 | [26 empty] | _CUR | Current | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
1107 | [26 empty] | _SR | Speed reference | BB1FD663 | [21 empty] | X | [13 empty] | FRQ_REVH
1108 | [26 empty] | _AS | Actual speed | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
1109 | [26 empty] | _TORQ | Torque | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
1110 | [26 empty] | _RPM | RPM | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
1111 |  | BB1 | EM | 664 | BB1EM664 | Fuel feeding screw 1 |  |  |  | 5.5 | 10 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
1112 | [26 empty] | _R_FWD | Running FWD | BB1FD664 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1113 | [26 empty] | _R_BWD | Running BWD | BB1FD664 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1114 | [26 empty] | _FAULT | MCC Fault | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1115 | [26 empty] | _SS | Load isolator (Safety switch) | BB1FD664 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
1116 | [26 empty] | _VSD_F | VFD Alarm | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1117 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1118 | [26 empty] | _L_FWD | Local FWD command | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1119 | [26 empty] | _L_BWD | Local BWD command | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1120 | [26 empty] | _L/R | Local mode switch | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1121 | [26 empty] | _CTRL_F | Run command FWD | BB1FD664 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1122 | [26 empty] | _CTRL_B | Run command BWD | BB1FD664 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1123 | [26 empty] | _CUR | Current | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
1124 | [26 empty] | _SR | Speed reference | BB1FD664 | [21 empty] | X | [13 empty] | FRQ_REVH
1125 | [26 empty] | _AS | Actual speed | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
1126 | [26 empty] | _TORQ | Torque | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
1127 | [26 empty] | _RPM | RPM | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
1128 |  | BB1 | EM | 653 | BB1EM653 | Cooling fan fuel feeding screw 1 |  |  |  | 0.15 | 0.33 |  | 415 | [26 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIR_BUS |  |  |  | Motor typical changed | 4
1129 | [26 empty] | _R | Running | BB1FF650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1130 | [26 empty] | _FAULT | MCC Fault | BB1FF650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1131 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1132 | [26 empty] | _CTRL | Run command | BB1FF650 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1133 | [26 empty] | _CUR | Current | BB1FF650 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1134 |  | BB1 | EM | 665 | BB1EM665 | Fuel feeding screw 2 |  |  |  | 5.5 | 10 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
1135 | [26 empty] | _R_FWD | Running FWD | BB1FD665 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1136 | [26 empty] | _R_BWD | Running BWD | BB1FD665 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1137 | [26 empty] | _FAULT | MCC Fault | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1138 | [26 empty] | _SS | Load isolator (Safety switch) | BB1FD665 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
1139 | [26 empty] | _VSD_F | VFD Alarm | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1140 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1141 | [26 empty] | _L_FWD | Local FWD command | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1142 | [26 empty] | _L_BWD | Local BWD command | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1143 | [26 empty] | _L/R | Local mode switch | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1144 | [26 empty] | _CTRL_F | Run command FWD | BB1FD665 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1145 | [26 empty] | _CTRL_B | Run command BWD | BB1FD665 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1146 | [26 empty] | _CUR | Current | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
1147 | [26 empty] | _SR | Speed reference | BB1FD665 | [21 empty] | X | [13 empty] | FRQ_REVH
1148 | [26 empty] | _AS | Actual speed | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
1149 | [26 empty] | _TORQ | Torque | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
1150 | [26 empty] | _RPM | RPM | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
1151 |  | BB1 | EM | 655 | BB1EM655 | Cooling fan fuel feeding screw 2 |  |  |  | 0.15 | 0.33 |  | 415 | [26 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIR_BUS |  |  |  | Motor typical changed | 4
1152 | [26 empty] | _R | Running | BB1FF650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1153 | [26 empty] | _FAULT | MCC Fault | BB1FF650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1154 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1155 | [26 empty] | _CTRL | Run command | BB1FF650 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1156 | [26 empty] | _CUR | Current | BB1FF650 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1157 |  | BB1 | EM | 657 | BB1EM657 | Fuel feeding rotary valve 1 |  |  |  | 7.5 | 13.7 | 1500 | 415 | [26 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor details | 1
1158 | [26 empty] | _R_FWD | Running FWD | BB1RV650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1159 | [26 empty] | _R_BWD | Running BWD | BB1RV650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1160 | [26 empty] | _FAULT | MCC Fault | BB1RV650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1161 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
1162 | [26 empty] | _L_FWD | Local FWD command | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1163 | [26 empty] | _L_BWD | Local BWD command | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1164 | [26 empty] | _L/R | Local mode switch | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1165 | [26 empty] | _CTRL_F | Run command FWD | BB1RV650 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1166 | [26 empty] | _CTRL_B | Run command BWD | BB1RV650 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1167 | [26 empty] | _CUR | Current | BB1RV650 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1168 |  | BB1 | EM | 656 | BB1EM656 | Fuel feeding rotary valve 2 |  |  |  | 7.5 | 13.7 | 1500 | 415 | [26 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor details | 1
1169 | [26 empty] | _R_FWD | Running FWD | BB1RV651 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1170 | [26 empty] | _R_BWD | Running BWD | BB1RV651 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1171 | [26 empty] | _FAULT | MCC Fault | BB1RV651 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1172 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
1173 | [26 empty] | _L_FWD | Local FWD command | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1174 | [26 empty] | _L_BWD | Local BWD command | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1175 | [26 empty] | _L/R | Local mode switch | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1176 | [26 empty] | _CTRL_F | Run command FWD | BB1RV651 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1177 | [26 empty] | _CTRL_B | Run command BWD | BB1RV651 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1178 | [26 empty] | _CUR | Current | BB1RV651 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1179 |  | BB1 | GS | 802 | BB1GS802 | Bottom ash valve limit switch | [33 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | XS002/XS004 | Field IO
1180 | [26 empty] | _DI | Binary state | BB1GS802 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1181 |  | BB1 | GS | 803 | BB1GS803 | Bottom ash dropping chute closing device limit switch | [33 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | XS002/XS004 | Field IO
1182 | [26 empty] | _DI | Binary state | BB1GS803 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1183 |  | BB1 | LS | 852 | BB1LS852 | Fly ash container level switch |  | harting connector | [31 empty] | 1 | [18 empty] | 24 VDC | E+H | FTE20-AA16AD11+Z1 | G1-1/2" Male |  | 4011 | MEAS_BIN | LS001 | Field IO
1184 | [26 empty] | _DI | Binary state | BB1LS852 | [10 empty] | X | [17 empty] | NC/NO | 24 VDC | [5 empty] | MEAS_BIN |  | Field IO
1185 |  | BB1 | PT | 552 | BB1PT552 | ESP inlet pressure transmitter |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [16 empty] | 24 VDC |  |  |  | IS SaveEnergy | 4011 | MEAS_ANA | PT002
1186 | [26 empty] | _PV | Measurement | BB1PT552 | [12 empty] | X | [22 empty] | MEAS_ANA
1187 |  | BB1 | PT | 553 | BB1PT553 | ESP outlet pressure transmitter |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA | PT002
1188 | [26 empty] | _PV | Measurement | BB1PT553 | [12 empty] | X | [22 empty] | MEAS_ANA
1189 |  | BB1 | QT | 554 | BB1QT554 | Opacity after ESP | [6 empty] | 24 VDC | [23 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | QT001 | Field IO
1190 | [26 empty] | _PV | Measurement | BB1QT554 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1191 |  | BB1 | ST | 805 | BB1ST805 | Heated ESP collection screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
1192 | [26 empty] | _DI | Binary state | BB1ST805 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1193 |  | BB1 | ST | 808 | BB1ST808 | ESP hopper 2 screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
1194 | [26 empty] | _DI | Binary state | BB1ST808 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1195 |  | BB1 | ST | 809 | BB1ST809 | ESP hopper 1 screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
1196 | [26 empty] | _DI | Binary state | BB1ST809 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1197 |  | BB1 | ST | 804 | BB1ST804 | ESP Rotary valve rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
1198 | [26 empty] | _DI | Binary state | BB1ST804 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1199 |  | BB1 | TT | 553 | BB1TT553 | Flue gas fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4011 | MEAS_ANA | TT005 | Field IO
1200 | [26 empty] | _PV | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1201 |  | BB1 | TT | 557 | BB1TT557 | Flue gas fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4011 | MEAS_ANA | TT005 | Field IO |  | signal added | 3
1202 | [26 empty] | _PV | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1203 |  | BB1 | TT | 558 | BB1TT558 | Flue gas fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4011 | MEAS_ANA | TT005 | Field IO |  | signal added | 3
1204 | [26 empty] | _PV | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1205 |  | BB1 | TT | 554 | BB1TT554 | Flue gas fan bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4011 | MEAS_ANA | TT005 | Field IO
1206 | [26 empty] | _PV | Measurement | BB1TT554 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1207 |  | BB1 | TT | 555 | BB1TT555 | Flue gas fan bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TMT82-AAA3CC1A1AAA1+Z1 | DIN |  | 4011 | MEAS_ANA | TT005 | Field IO
1208 | [26 empty] | _PV | Measurement | BB1TT555 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1209 |  | BB1 | TT | 556 | BB1TT556 | Flue gas temperature before stack | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSXKC10B | G1/2 M / 250 mm |  | 4011 | MEAS_ANA | TT003 | Field IO
1210 | [26 empty] | _PV | Measurement | BB1TT556 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1211 |  | BB1 | TT | 850 | BB1TT850 | ESP Ash hopper 1 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1212 | [26 empty] | _PV | Measurement | BB1TT850 | [12 empty] | X | [22 empty] | MEAS_ANA
1213 |  | BB1 | TT | 851 | BB1TT851 | ESP Ash hopper 2 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1214 | [26 empty] | _PV | Measurement | BB1TT851 | [12 empty] | X | [22 empty] | MEAS_ANA
1215 |  | BB1 | EH | 808 | BB1EH808 | ESP Ash hopper 2 heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1216 | [26 empty] | _FAULT | RCBO fault | BB1EH808 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1217 | [26 empty] | _CTLR | On command | BB1EH808 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1218 |  | BB1 | EH | 809 | BB1EH809 | ESP Ash hopper 1 heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1219 | [26 empty] | _FAULT | RCBO fault | BB1EH809 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1220 | [26 empty] | _CTLR | On command | BB1EH809 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1221 |  | BB1 | TS | 808 | BB1TS808 | ESP Ash hopper 2 overheat thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS001
1222 | [26 empty] | _DI | Binary state | BB1TS808 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1223 |  | BB1 | TS | 809 | BB1TS809 | ESP Ash hopper 1 overheat thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS001
1224 | [26 empty] | _DI | Binary state | BB1TS809 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1225 |  | BB1 | TS | 501 | BB1TS501 | ESP Insulator 1 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1226 | [26 empty] | _PV | Measurement | BB1TS501 | [12 empty] | X | [22 empty] | MEAS_ANA
1227 |  | BB1 | TS | 508 | BB1TS508 | ESP Insulator 2 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1228 | [26 empty] | _PV | Measurement | BB1TS508 | [12 empty] | X | [22 empty] | MEAS_ANA
1229 |  | BB1 | TT | 552 | BB1TT552 | Flue gas temperature before ESP |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1230 | [26 empty] | _PV | Measurement | BB1TT552 | [12 empty] | X | [22 empty] | MEAS_ANA
1231 |  | BB1 | EM | 509 | BB1EM509 | ESP DE rapping drive 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1232 | [26 empty] | _R | Running | BB1EM509 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1233 | [26 empty] | _FAULT | MCC Fault | BB1EM509 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1234 | [26 empty] | _CTRL | Run command | BB1EM509 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1235 |  | BB1 | EM | 510 | BB1EM510 | ESP CE rapping drive 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1236 | [26 empty] | _R | Running | BB1EM510 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1237 | [26 empty] | _FAULT | MCC Fault | BB1EM510 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1238 | [26 empty] | _CTRL | Run command | BB1EM510 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1239 |  | BB1 | EM | 511 | BB1EM511 | ESP DE rapping drive 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1240 | [26 empty] | _R | Running | BB1EM511 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1241 | [26 empty] | _FAULT | MCC Fault | BB1EM511 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1242 | [26 empty] | _CTRL | Run command | BB1EM511 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1243 |  | BB1 | EM | 512 | BB1EM512 | ESP CE rapping drive 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1244 | [26 empty] | _R | Running | BB1EM512 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1245 | [26 empty] | _FAULT | MCC Fault | BB1EM512 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1246 | [26 empty] | _CTRL | Run command | BB1EM512 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1247 |  | BB1 | EH | 501 | BB1EH501 | ESP insulators heating chamber 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1248 | [26 empty] | _R | Running | BB1EH501 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1249 | [26 empty] | _FAULT | MCC Fault | BB1EH501 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1250 | [26 empty] | _CTRL | Run command | BB1EH501 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1251 |  | BB1 | EH | 505 | BB1EH505 | ESP insulators heating chamber 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1252 | [26 empty] | _R | Running | BB1EH505 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1253 | [26 empty] | _FAULT | MCC Fault | BB1EH505 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1254 | [26 empty] | _CTRL | Run command | BB1EH505 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1255 |  | BB1 | IE | 501 | BB1IE501 | ESP HV Trafo 1 |  | Supply from ESP MCC | [55 empty] | 4011 | OESA_3ph
1256 |  | BB1 | IE | 502 | BB1IE502 | ESP HV Trafo 2 |  | Supply from ESP MCC | [55 empty] | 4011 | OESA_3ph
1257 |  | BB1 | FG | 300 | BB1FG300 | ESP hardwired signals to/from Boiler PLC | [33 empty] | 8 | 6 | [22 empty] | 4011 | ESP_DI_DO
1258 | [26 empty] | _AL | Collective Alarm | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1259 | [26 empty] | _WAR | Collective Warning | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1260 | [26 empty] | _SB | ESP in Standby | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1261 | [26 empty] | _RUN | ESP in Operation | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1262 | [27 empty] | ESP spare DI1 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1263 | [27 empty] | ESP spare DI2 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1264 | [27 empty] | ESP spare DI3 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1265 | [27 empty] | ESP spare DI4 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1266 | [26 empty] | _REMOTE | ESP External release filter | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1267 | [27 empty] | ESP spare DO1 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1268 | [27 empty] | ESP spare DO2 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1269 | [27 empty] | ESP spare DO3 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1270 | [27 empty] | ESP spare DO4 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1271 | [27 empty] | ESP spare DO5 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1272 |  | BB1 | EM | 809 | BB1EM809 | ESP ash hopper 1 screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1273 | [26 empty] | _R_FWD | Running FWD | BB1EM809 | [10 empty] | X | [24 empty] | DOL_REVH
1274 | [26 empty] | _R_BWD | Running BWD | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1275 | [26 empty] | _FAULT | MCC Fault | BB1EM809 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1276 | [26 empty] | _L_FWD | Local FWD command | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1277 | [26 empty] | _L_BWD | Local BWD command | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1278 | [26 empty] | _L/R | Local mode switch | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1279 | [26 empty] | _CTRL_F | Run command FWD | BB1EM809 | [11 empty] | X | [23 empty] | DOL_REVH
1280 | [26 empty] | _CTRL_B | Run command BWD | BB1EM809 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1281 |  | BB1 | EM | 808 | BB1EM808 | ESP ash hopper 2 screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1282 | [26 empty] | _R_FWD | Running FWD | BB1EM808 | [10 empty] | X | [24 empty] | DOL_REVH
1283 | [26 empty] | _R_BWD | Running BWD | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1284 | [26 empty] | _FAULT | MCC Fault | BB1EM808 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1285 | [26 empty] | _L_FWD | Local FWD command | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1286 | [26 empty] | _L_BWD | Local BWD command | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1287 | [26 empty] | _L/R | Local mode switch | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1288 | [26 empty] | _CTRL_F | Run command FWD | BB1EM808 | [11 empty] | X | [23 empty] | DOL_REVH
1289 | [26 empty] | _CTRL_B | Run command BWD | BB1EM808 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1290 |  | BB1 | EM | 805 | BB1EM805 | ESP collection screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1291 | [26 empty] | _R_FWD | Running FWD | BB1EM805 | [10 empty] | X | [24 empty] | DOL_REVH
1292 | [26 empty] | _R_BWD | Running BWD | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1293 | [26 empty] | _FAULT | MCC Fault | BB1EM805 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1294 | [26 empty] | _L_FWD | Local FWD command | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1295 | [26 empty] | _L_BWD | Local BWD command | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1296 | [26 empty] | _L/R | Local mode switch | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1297 | [26 empty] | _CTRL_F | Run command FWD | BB1EM805 | [11 empty] | X | [23 empty] | DOL_REVH
1298 | [26 empty] | _CTRL_B | Run command BWD | BB1EM805 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1299 |  | BB1 | EH | 805 | BB1EH805 | ESP collection screw heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1300 | [26 empty] | _FAULT | RCBO fault | BB1EH805 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1301 | [26 empty] | _CTLR | On command | BB1EH805 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1302 |  | BB1 | TS | 805 | BB1TS805 | ESP collection screw heating thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN
1303 | [26 empty] | _DI | Binary state | BB1TS805 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1304 |  | BB1 | EM | 804 | BB1EM804 | ESP Rotary valve |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1305 | [26 empty] | _R_FWD | Running FWD | BB1EM804 | [10 empty] | X | [24 empty] | DOL_REVH
1306 | [26 empty] | _R_BWD | Running BWD | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1307 | [26 empty] | _FAULT | MCC Fault | BB1EM804 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1308 | [26 empty] | _L_FWD | Local FWD command | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1309 | [26 empty] | _L_BWD | Local BWD command | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1310 | [26 empty] | _L/R | Local mode switch | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1311 | [26 empty] | _CTRL_F | Run command FWD | BB1EM804 | [11 empty] | X | [23 empty] | DOL_REVH
1312 | [26 empty] | _CTRL_B | Run command BWD | BB1EM804 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1313 |  | BB1 | EH | 804 | BB1EH804 | ESP Rotary valve heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1314 | [26 empty] | _FAULT | RCBO fault | BB1EH804 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1315 | [26 empty] | _CTLR | On command | BB1EH804 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1316 |  | BB1 | TS | 804 | BB1TS804 | ESP Rotary valve heating thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN
1317 | [26 empty] | _DI | Binary state | BB1TS804 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1318 |  | BB1 | EM | 815 | BB1EM815 | Fly ash container screw | [33 empty] | 1 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4011 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1319 | [26 empty] | _R_FWD | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1320 | [26 empty] | _R_BWD | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1321 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1322 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
1323 | [26 empty] | _CTRL_F | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1324 | [26 empty] | _CTRL_B | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1325 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1326 |  | BB1 | EM | 550 | BB1EM550 | Flue gas fan |  |  |  | 75 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4011 | FRQ_DIR |  |  |  | Size and voltage | 1
1327 | [26 empty] | _R | Running | BB1FF550 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
1328 | [26 empty] | _FAULT | MCC Fault | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1329 | [26 empty] | _SS | Load isolator (Safety switch) | BB1FF550 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_DIR |  |  |  | Hardwired DI | 4
1330 | [26 empty] | _VSD_F | VFD Alarm | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1331 | [26 empty] | _CTRL | Run command | BB1FF550 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
1332 | [26 empty] | _CUR | Current | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1333 | [26 empty] | _SR | Speed reference | BB1FF550 | [21 empty] | X | [13 empty] | FRQ_DIR
1334 | [26 empty] | _AS | Actual speed | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1335 | [26 empty] | _TORQ | Torque | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1336 | [26 empty] | _RPM | RPM | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1337 |  | BB1 | SI | 550 | BB1SI550 | Flue gas fan safety interlock | [38 empty] | 1 | [18 empty] | 4011 | FAN_SRS_DO
1338 | [26 empty] | _SI | Safety interlock | BB1SI550 | [15 empty] | X | [19 empty] | FAN_SRS_DO
1339 |  | BB1 | SI | 560 | BB1SI560 | Flue gas fan run status SRS | [37 empty] | 1 | [19 empty] | 4011 |  |  | MCC |  | Signal added | 2
1340 | [26 empty] | _R | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
1341 |  | BB1 | ST | 550 | BB1ST550 | Flue gas fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
1342 | [26 empty] | _ST | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
1343 |  | BB1 |  |  | BB1 | Flue gas fan heating |  | RCBO + Contactor |  |  |  |  | 240 | [27 empty] | 1 | [22 empty] | 4011 |  |  |  |  | Heater added | 3
1344 | [26 empty] | _CTLR | Heater On control | BB1SI401 | [11 empty] | X | [27 empty] | Heater added | 3
1345 |  | BB1 | CV | 405 | BB1CV405 | Bottom ash valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1346 | [7 empty] | own 24 VDC fuse | [18 empty] | _CTLR | Control command | BB1CV405 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1347 |  | BB1 | GS | 855 | BB1GS855 | Bottom ash valve solenoid valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1348 | [26 empty] | _DI | Binary state | BB1GS855 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1349 |  | BB1 | GS | 856 | BB1GS856 | Bottom ash valve solenoid valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1350 | [26 empty] | _DI | Binary state | BB1GS856 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1351 |  | BB1 | CV | 406 | BB1CV406 | Bottom ash valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1352 | [7 empty] | own 24 VDC fuse | [18 empty] | _CTLR | Control command | BB1CV406 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1353 |  | BB1 | GS | 857 | BB1GS857 | Bottom ash valve solenoid valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1354 | [26 empty] | _DI | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1355 |  | BB1 | GS | 858 | BB1GS858 | Bottom ash valve solenoid valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1356 | [26 empty] | _DI | Binary state | BB1GS858 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1357 |  | BB1 | CV | 412 | BB1CV412 | Bottom ash sieve bypass solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1358 | [7 empty] | own 24 VDC fuse | [18 empty] | _CTLR | Control command | BB1CV412 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1359 |  | BB1 | GS | 850 | BB1GS850 | Bottom ash sieve bypass valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1360 | [26 empty] | _DI | Binary state | BB1GS850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1361 |  | BB1 | GS | 851 | BB1GS851 | Bottom ash sieve bypass valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1362 | [26 empty] | _DI | Binary state | BB1GS851 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1363 |  | BB1 | CV | 413 | BB1CV413 | Control valve of pneumatic transmitter damper |  | Pneuplan PLC |  |  | Pneuplan PLC |  | 24 | [27 empty] | 2 | [21 empty] | Pneuplan | 4012 | BIN_VLV_2DO | AA004 | Field IO
1364 | [26 empty] | _CTLR_O | Open command | BB1CV413 | [11 empty] | X | [23 empty] | BIN_VLV_2DO |  | Field IO
1365 | [26 empty] | _CTRL_C | Close command | BB1CV413 | [11 empty] | X | [23 empty] | BIN_VLV_2DO |  | Field IO
1366 |  | BB1 | CV | 414 | BB1CV414 | Work air to pneumatic transmitter pneumatic valve |  | Pneuplan PLC |  |  | Pneuplan PLC |  | 24 | [27 empty] | 1 | [21 empty] | Pneuplan | 4012 | BIN_VLV | AA004 | Field IO
1367 | [26 empty] | _CTLR | Control command | BB1CV414 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1368 |  | BB1 | FS | 003 | BB1FS003 | Bottom ash cooling flow switch | [6 empty] | 24 VDC | [26 empty] | 1 | [18 empty] | 24 VDC | E+H | DTT31-A1A111AE2ABB | G1/2" |  | 4012 | MEAS_BIN | FS001 | Field IO |  | 24 VDC supply added | 4
1369 | [26 empty] | _DI | Binary state | BB1FS003 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1370 |  | BB1 | SV | 405 | BB1SV405 | Sand filling valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA003 | Field IO
1371 | [26 empty] | _CTLR | Control command | BB1SV405 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1372 |  | BB1 | GS | 801 | BB1GS801 | Sand filling valve position open limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | AA005 | Field IO
1373 | [26 empty] | _DI | Binary state | BB1GS801 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1374 |  | BB1 | GS | 800 | BB1GS800 | Sand filling valve position close limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS001 | Field IO
1375 | [26 empty] | _DI | Binary state | BB1GS800 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1376 |  | BB1 | GS | 854 | BB1GS854 | Bottom ash dropping chute limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO |  | Tag changed | 3
1377 | [26 empty] | _DI | Binary state | BB1GS852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1378 |  | BB1 | GS | 853 | BB1GS853 | Bottom ash dropping chute closing device limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO
1379 | [26 empty] | _DI | Binary state | BB1GS853 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1380 |  | BB1 | GS | 859 | BB1GS859 | Bottom ash to container in place |  | Harting connector (jumper in container side..> DI=1 connector in place) | [31 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO |  | Tag changed | 3
1381 | [26 empty] | _DI | Binary state | BB1GS854 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1382 |  | BB1 | LS | 850 | BB1LS850 | Bottom ash container level switch |  | harting connector | [31 empty] | 1 | [18 empty] | 24 VDC | E+H | FTE20-AA16AD11+Z1 | G1-1/2" Male |  | 4012 | MEAS_BIN | LS001 | Field IO
1383 | [26 empty] | _DI | Binary state | BB1LS850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1384 |  | BB1 | LS | 851 | BB1LS851 | Bottom ash container level switch |  | harting connector | [31 empty] | 1 | [18 empty] | 24 VDC | E+H | FTE20-AA16AD11+Z1 | G1-1/2" Male |  | 4012 | MEAS_BIN | LS001 | Field IO
1385 | [26 empty] | _DI | Binary state | BB1LS851 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1386 |  | BB1 | LT | 800 | BB1LT800 | Recycled bed material hopper level switch |  | Pneuplan PLC |  |  | Pneuplan PLC | [30 empty] | 1 | [20 empty] | Pneuplan | 4012 | MEAS_ANA |  | Field IO
1387 | [26 empty] | _PV | Measurement | BB1LT800 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1388 |  | BB1 | LT | 802 | BB1LT802 | Sand silo level measurement | [6 empty] | 24 VDC | [23 empty] | 0 | 100 | % |  |  | 1 | [17 empty] | E+H | FMP57-AAACCALCA4CJJ+JDZ1 | DN150 |  | 4012 | MEAS_ANA | LT003 | Field IO
1389 | [26 empty] | _PV | Measurement | BB1LT802 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1390 |  | BB1 | PT | 009 | BB1PT009 | Cooling water pressure before pump | [30 empty] | 0 | 6 | bar(g) |  |  | 1 | [13 empty] | Pressure |  |  |  | E+H | PMP51-AA22IA1PGJGCJA1+JAZ1 | G1/2 |  | 4012 | MEAS_ANA | PT001.1 | Field IO
1391 | [26 empty] | _PV | Measurement | BB1PT009 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1392 |  | BB1 | PT | 800 | BB1PT800 | Recycled bed material damper pressure switch |  | Pneuplan PLC |  |  | Pneuplan PLC | [28 empty] | 1 | [22 empty] | Pneuplan | 4012 | MEAS_BIN |  | Field IO
1393 | [26 empty] | _DI | Binary state | BB1PT800 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1394 |  | BB1 | EM | 856 | BB1EM856 | Purified sand screw conveyor | [33 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor added | 2
1395 | [26 empty] | _R_FWD | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1396 | [26 empty] | _R_BWD | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1397 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1398 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
1399 | [26 empty] | _L_FWD | Local FWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1400 | [26 empty] | _L_BWD | Local BWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1401 | [26 empty] | _L/R | Local mode switch | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1402 | [26 empty] | _CTRL_F | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1403 | [26 empty] | _CTRL_B | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1404 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1405 |  | BB1 | ST | 856 | BB1ST856 | Purified sand screw conveyor rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument added | 2
1406 | [26 empty] | _DI | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO |  | Instrument added | 2
1407 |  | BB1 | EM | 852 | BB1EM852 | Bottom ash conveyor |  |  |  | 2.2 | 4.2 | 1500 | 415 |  | X | [24 empty] | 4 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4012 | FRQ_REVH |  |  |  | Tag changed | 2
1408 | [26 empty] | _R_FWD | Running FWD | BB1EM850 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1409 | [26 empty] | _R_BWD | Running BWD | BB1EM850 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1410 | [26 empty] | _FAULT | MCC Fault | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1411 | [26 empty] | _SS | Load isolator (Safety switch) | BB1EM850 | [10 empty] | X | [17 empty] | NC | [6 empty] | FRQ_REVH |  |  |  | Hardwired DI | 4
1412 | [26 empty] | _VSD_F | VFD Alarm | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1413 | [26 empty] | _TF | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1414 | [26 empty] | _L_FWD | Local FWD command | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1415 | [26 empty] | _L_BWD | Local BWD command | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1416 | [26 empty] | _L/R | Local mode switch | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1417 | [26 empty] | _CTRL_F | Run command FWD | BB1EM850 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1418 | [26 empty] | _CTRL_B | Run command BWD | BB1EM850 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1419 | [26 empty] | _CUR | Current | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1420 | [26 empty] | _SR | Speed reference | BB1EM850 | [21 empty] | X | [13 empty] | FRQ_REVH
1421 | [26 empty] | _AS | Actual speed | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1422 | [26 empty] | _TORQ | Torque | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1423 | [26 empty] | _RPM | RPM | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1424 |  | BB1 | ST | 850 | BB1ST850 | Bottom ash conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemecanique | XSAV-11801 |  |  | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
1425 | [26 empty] | _DI | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1426 |  | BB1 | GS | 852 | BB1GS852 | Bottom ash conveyor blockage detector | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemecanique | XS530B1MAL2 |  |  | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument added | 1
1427 | [26 empty] | _DI | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1428 |  | BB1 | IJ | 004 | BB1IJ004 | Bottom ash conveyor Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4012 | ALM_HORN |  | Field IO |  | Instrument added | 2
1429 | [26 empty] | _CTLR | Command | BB1IJ001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
1430 |  | BB1 | EM | 850 | BB1EM850 | 2nd pass fly ash rotary valve |  |  |  |  | 0,37 |  | 415 | [26 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor details | 1
1431 | [26 empty] | _R_FWD | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1432 | [26 empty] | _R_BWD | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1433 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1434 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
1435 | [26 empty] | _L_FWD | Local FWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1436 | [26 empty] | _L_BWD | Local BWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1437 | [26 empty] | _L/R | Local mode switch | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1438 | [26 empty] | _CTRL_F | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1439 | [26 empty] | _CTRL_B | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1440 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1441 |  | BB1 | ST | 852 | BB1ST852 | 2nd pass fly ash rotary valve rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO
1442 | [26 empty] | _DI | Binary state | BB1ST852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1443 |  | BB1 | EM | 851 | BB1EM851 | 3rd pass fly ash rotary valve |  |  |  |  | 0,37 |  | 415 | [26 empty] | 4 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor details | 1
1444 | [26 empty] | _R_FWD | Running FWD | BB1EM851 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1445 | [26 empty] | _R_BWD | Running BWD | BB1EM851 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1446 | [26 empty] | _FAULT | MCC Fault | BB1EM851 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1447 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Added signal | 4
1448 | [26 empty] | _L_FWD | Local FWD command | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1449 | [26 empty] | _L_BWD | Local BWD command | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1450 | [26 empty] | _L/R | Local mode switch | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1451 | [26 empty] | _CTRL_F | Run command FWD | BB1EM851 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1452 | [26 empty] | _CTRL_B | Run command BWD | BB1EM851 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1453 | [26 empty] | _CUR | Current | BB1EM851 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1454 |  | BB1 | ST | 853 | BB1ST853 | 3rd pass fly ash rotary valve rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO
1455 | [26 empty] | _DI | Binary state | BB1ST853 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1456 |  | BB1 | SV | 401 | BB1SV401 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA005 | Field IO
1457 | [26 empty] | _CTLR | Control command | BB1SV401 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1458 |  | BB1 | SV | 402 | BB1SV402 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA005 | Field IO
1459 | [26 empty] | _CTLR | Control command | BB1SV402 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1460 |  | BB1 | SV | 403 | BB1SV403 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 0 | [22 empty] | 4012 | BIN_VLV | AA005 |  |  | Removed | 1
1461 | [26 empty] | _CTLR | Control command | BB1SV403 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  |  |  | Removed | 1
1462 |  | BB1 | SV | 404 | BB1SV404 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 0 | [22 empty] | 4012 | BIN_VLV | AA005 |  |  | Removed | 1
1463 | [26 empty] | _CTLR | Control command | BB1SV404 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  |  |  | Removed | 1
1464 |  | BB1 | TT | 031 | BB1TT031 | Cooling water temperature after bottom ash conveyor | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TR15-A3B101J0K300B | D4 |  | 4012 | MEAS_ANA | TT001 | Field IO
1465 | [26 empty] | _PV | Measurement | BB1TT031 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1466 |  | BB1 | EM | 014 | BB1EM008 | Conveyor cooling pump |  |  |  | 1,1 |  |  | 415 | [26 empty] | 1 | [7 empty] | 2 | 1 | 1 | [12 empty] | Grundfos | 4012 | DOL_DIR_BUS |  |  |  | Motor size changed | 3
1467 | [26 empty] | _R | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1468 | [26 empty] | _FAULT | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1469 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1470 | [26 empty] | _CTRL | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1471 | [26 empty] | _CUR | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1472 |  | BB1 | EM | 855 | BB1EM855 | Ash container screw |  |  |  | 1,5 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REV_BUS |  |  |  | Motor details | 1
1473 | [26 empty] | _R_FWD | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1474 | [26 empty] | _R_BWD | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1475 | [26 empty] | _FAULT | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1476 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
1477 | [26 empty] | _CTRL_F | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS
1478 | [26 empty] | _CTRL_B | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS
1479 | [26 empty] | _CUR | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS
1480 |  | BB1 | EM | 018 | BB1EM009 | Bottom ash conveyor heat exchanger fan |  | preliminary 6x0,72 kW, 1.42 A |  | 7,5 |  |  | 415 | [26 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4012 | DOL_DIR_BUS |  |  |  | Tag changed | 2
1481 | [26 empty] | _R | Running | BB1FF009 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1482 | [26 empty] | _FAULT | MCC Fault | BB1FF009 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1483 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1484 | [26 empty] | _CTRL | Run command | BB1FF009 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1485 | [26 empty] | _CUR | Current | BB1FF009 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1486 |  | BB1 | FM | 001 | BB1FM001 | Bottom ash sieve feed |  | supply fuse 16A |  | 1,4 |  |  | 415 | [26 empty] | 5 | 1 | [22 empty] | 4012 | OESA_3ph |  |  |  | Details | 1
1487 | [26 empty] | _ES | Emergency stop | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1488 | [7 empty] | ask preliminary drawings from KPA | [18 empty] | _R | Running | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1489 | [26 empty] | _M/A | manual/auto | [11 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1490 | [26 empty] | _TF | Thermistor fault | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1491 | [26 empty] | _VOLT | Voltage OK | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1492 | [26 empty] | _ON/OFF | Start/stop | BB1BU500 | [11 empty] | X | [16 empty] | pot.free | [6 empty] | OESA_3ph |  |  |  | signals added | 1
1493 |  | BB1 | HC | 601 | BB1HC601 | Electrical hoist feed |  |  |  |  | 2,8 |  | 415 | [50 empty] | 4012 | OESA_3ph |  |  |  | Deleted | 4
1494 |  | BB1 | TN | ??? | BB1TN??? | Sand transmitter 230 Vac feed | [33 empty] | 1 | [23 empty] | 4012 | MCCB_1ph
1495 |  | BB1 | BU | 500 | BB1BU500 | Burner |  | MCB 16A feed |  |  |  |  | 240 | [26 empty] | 5 | 5 | 2 | 2 |  |  |  |  | 6 | 5 | 2 | 2 | [12 empty] | 4013 | BURNER |  |  |  | Feed values added | 4
1496 | [26 empty] | _AL | Alarm | BB1BU500 | [10 empty] | X | [24 empty] | BURNER |  |  |  | Updated signal | 4
1497 | [26 empty] | _BS | Burner starting | BB1BU500 | [10 empty] | X | [24 empty] | BURNER |  |  |  | Updated signal | 4
1498 | [26 empty] | _FAULT | Burner failure | BB1BU500 | [10 empty] | X | [24 empty] | BURNER |  |  |  | Updated signal | 4
1499 | [26 empty] | _RUN | Burner running | BB1BU500 | [10 empty] | X | [24 empty] | BURNER |  |  |  | Updated signal | 4
1500 | [26 empty] | _REM | Remote use active | BB1BU500 | [10 empty] | X | [24 empty] | BURNER |  |  |  | Updated signal | 4
1501 | [26 empty] | _SI | Burner safety loop | BB1BU500 | [15 empty] | X | [19 empty] | BURNER |  |  |  | Changed to SDO | 4
1502 | [26 empty] | _CTRL | Remote start | BB1BU500 | [11 empty] | X | [23 empty] | BURNER |  |  |  | Updated signal | 4
1503 | [26 empty] | _ACK | Remote reset | BB1BU500 | [11 empty] | X | [23 empty] | BURNER |  |  |  | Updated signal | 4
1504 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1505 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1506 | [26 empty] | _RSP | External setpoint MW | BB1BU500 | [12 empty] | X | [22 empty] | BURNER |  |  |  | Updated signal | 4
1507 | [27 empty] | AI reservation | BB1BU500 | [12 empty] | X | [22 empty] | BURNER
1508 | [26 empty] | _MW | Actual value MW | BB1BU500 | [13 empty] | X | [21 empty] | BURNER |  |  |  | Updated signal | 4
1509 | [27 empty] | AO reservation | BB1BU500 | [13 empty] | X | [21 empty] | BURNER
1510 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1511 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1512 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1513 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1514 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1515 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1516 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1517 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1518 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1519 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1520 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1521 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1522 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1523 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1524 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1525 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1526 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1527 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1528 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1529 |  | BB1 | EM | 402 | BB1EM402 | Compressor 1 |  | Preliminary size |  | 30 |  |  | 415 | [26 empty] | 3 | 2 | [22 empty] | 4014 | COMPR |  | Field IO |  | Motor size and tag changed | 3
1530 | [26 empty] | _FAULT | Fault | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1531 | [26 empty] | _R | Running | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1532 | [27 empty] | Reserve | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1533 | [26 empty] | _CTRL | Remote run command | BB1EM400 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1534 | [26 empty] | _ACK | Fault acknowledge | BB1EM400 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1535 |  | BB1 | EM | 403 | BB1EM403 | Compressor 2 |  | Preliminary size |  | 30 |  |  | 415 | [26 empty] | 3 | 2 | [22 empty] | 4014 | COMPR |  | Field IO |  | Motor size and tag changed | 3
1536 | [26 empty] | _FAULT | Fault | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1537 | [26 empty] | _R | Running | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1538 | [27 empty] | Reserve | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1539 | [26 empty] | _CTRL | Remote run command | BB1EM402 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1540 | [26 empty] | _ACK | Fault acknowledge | BB1EM402 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1541 |  | BB1 | DR | 400 | BB1DR400 | Compressor 1 dryer |  |  |  | 4 |  |  | 415 | [26 empty] | 1 | [23 empty] | 4014 | MCCB_1ph |  |  |  | motor details | 1
1542 |  | BB1 | DR | 401 | BB1DR401 | Compressor 2 dryer |  |  |  | 4 |  |  | 415 | [26 empty] | 1 | [23 empty] | 4014 | MCCB_1ph |  |  |  | motor details | 1
1543 |  | BB1 | PT | 478 | BB1PT478 | Instrument air pressure | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1PGBGCJA1+JAZ1 | G1/2 |  | 4014 | MEAS_ANA | PT002 | Field IO
1544 | [26 empty] | _PV | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1545 |  | BB1 | PT | 402 | BB1PT402 | Instrument air pressure after dryer | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1PGBGCJA1+JAZ1 | G1/2 |  | 4014 | MEAS_ANA | PT002 | Field IO |  | Instrument added | 3
1546 | [26 empty] | _PV | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
1547 |  | BB1 | TT | 430 | BB1TT430 | Instrument air tank temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFK310B | G1/2 |  | 4014 | MEAS_ANA | TT003 | Field IO |  | Instrument added | 3
1548 | [26 empty] | _PV | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
1549 |  | BB1 | GS | 020 | BB1GS020 | Emergency shower use switch | [33 empty] | 1 | [23 empty] | 4014 | MEAS_BIN | XS001 | Field IO
1550 | [26 empty] | _DI | Binary state | BB1GS020 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1551 |  | BB1 | TT | 401 | BB1TT401 | Boiler room upper part temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [17 empty] | E+H | TST434-J1A3BK | Wall mount |  | 4014 | MEAS_ANA | TT007 | Field IO
1552 | [26 empty] | _PV | Measurement | BB1TT401 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1553 |  | BB1 | EM | 411 | BB1EM411 | Exhaust fan 1 |  |  |  | 1,9 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | Tag changed | 4
1554 | [26 empty] | _R_FWD | Running FWD | BB1EM401 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1555 | [26 empty] | _R_BWD | Running BWD | BB1EM401 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1556 | [26 empty] | _FAULT | MCC Fault | BB1EM401 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1557 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
1558 | [26 empty] | _CTRL_F | Run command FWD | BB1EM401 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1559 | [26 empty] | _CTRL_B | Run command BWD | BB1EM401 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1560 | [26 empty] | _CUR | Current | BB1EM401 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1561 |  | BB1 | EM | 412 | BB1EM412 | Exhaust fan 2 |  |  |  | 1,9 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | Tag changed | 4
1562 | [26 empty] | _R_FWD | Running FWD | BB1EM402 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1563 | [26 empty] | _R_BWD | Running BWD | BB1EM402 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1564 | [26 empty] | _FAULT | MCC Fault | BB1EM402 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1565 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
1566 | [26 empty] | _CTRL_F | Run command FWD | BB1EM402 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1567 | [26 empty] | _CTRL_B | Run command BWD | BB1EM402 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1568 | [26 empty] | _CUR | Current | BB1EM402 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1569 |  | BB1 | EM | 413 | BB1EM413 | Exhaust fan 3 |  |  |  | 1,9 |  |  | 415 | [26 empty] | 1 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | Tag changed | 4
1570 | [26 empty] | _R_FWD | Running FWD | BB1EM403 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1571 | [26 empty] | _R_BWD | Running BWD | BB1EM403 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1572 | [26 empty] | _FAULT | MCC Fault | BB1EM403 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1573 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Added signal | 4
1574 | [26 empty] | _CTRL_F | Run command FWD | BB1EM403 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1575 | [26 empty] | _CTRL_B | Run command BWD | BB1EM403 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1576 | [26 empty] | _CUR | Current | BB1EM403 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1577 |  | BB1 | EM | 405 | BB1EM405 | Air intake grill 1 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1578 |  |  |  |  | BB1GS401 | [21 empty] | _LS_O | Open limit switch | BB1EM405 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1579 | [26 empty] | _CTLR_O | Open command | BB1EM405 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1580 |  | BB1 | EM | 406 | BB1EM406 | Air intake grill 2 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1581 |  |  |  |  | BB1GS412 | [21 empty] | _LS_O | Open limit switch | BB1EM406 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1582 | [26 empty] | _CTLR_O | Open command | BB1EM406 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1583 |  | BB1 | EM | 407 | BB1EM407 | Air intake grill 3 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1584 |  |  |  |  | BB1GS413 | [21 empty] | _LS_O | Open limit switch | BB1EM407 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1585 | [26 empty] | _CTLR_O | Open command | BB1EM407 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1586 |  | BB1 | EM | 408 | BB1EM408 | Boiler house heater 1 |  |  |  | 15 |  |  | 415 | [26 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4014 | DOL_DIR_BUS |  |  |  | Motor feed type changed | 2
1587 | [26 empty] | _R | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1588 | [26 empty] | _FAULT | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1589 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1590 | [26 empty] | _CTRL | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1591 | [26 empty] | _CUR | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1592 |  | BB1 | EM | 409 | BB1EM409 | Boiler house heater 2 |  |  |  | 15 |  |  | 415 | [26 empty] | 1 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4014 | DOL_DIR_BUS |  |  |  | Motor feed type changed | 2
1593 | [26 empty] | _R | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1594 | [26 empty] | _FAULT | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1595 | [26 empty] | _SS | Load isolator (Safety switch) | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR_BUS |  |  |  | Added signal | 4
1596 | [26 empty] | _CTRL | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1597 | [26 empty] | _CUR | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1598 |  | BB1 | CP | 002 | BB1CP002 | Smoke Exhaust cabinet | [6 empty] | 240 | [5 empty] | UPS | [20 empty] | 1 | [24 empty] | MCCB_1ph |  |  |  | UPS feed added | 4
1599
1600 |  |  |  |  | SPARE1 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1601 |  |  |  |  | SPARE2 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1602 |  |  |  |  | SPARE3 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1603 |  |  |  |  | SPARE4 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1604 |  |  |  |  | SPARE5 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1605 |  |  |  |  | SPARE6 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1606 |  |  |  |  | SPARE7 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1607 |  |  |  |  | SPARE8 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1608 |  |  |  |  | SPARE9 | SPARE FEED (L1L2L3NPE WIRED TO TERMINALS + CONTROL VOLTAGE MCCB) | [6 empty] | 415
1609 |  |  |  |  | SPARE10 | SPARE FEED (OESA 250 A) | [6 empty] | 415
1610 |  |  |  |  | SPARE11 | SPARE FEED (OESA 125 A) | [6 empty] | 415
1611 |  |  |  |  | SPARE12 | SPARE FEED (OESA 125 A) | [6 empty] | 415
1612 |  |  |  |  | SPARE13 | SPARE FEED (OESA 125 A) | [6 empty] | 415
1613 |  |  |  |  | SPARE14 | SPARE FEED (OESA 63 A) | [6 empty] | 415
1614 |  |  |  |  | SPARE15 | SPARE FEED (OESA 63 A) | [6 empty] | 415
1615 |  |  |  |  | SPARE16 | MCCB 3XC25A | [6 empty] | 415
1616 |  |  |  |  | SPARE17 | MCCB 3XC25A | [6 empty] | 415
1617 |  |  |  |  | SPARE18 | MCCB 3XC25A | [6 empty] | 415
1618 |  |  |  |  | SPARE19 | MCCB 3XC16A | [6 empty] | 415
1619 |  |  |  |  | SPARE20 | MCCB 3XC16A | [6 empty] | 415
1620 |  |  |  |  | SPARE21 | MCCB 3XC16A | [6 empty] | 415
1621 |  |  |  |  | SPARE22 | MCCB 3X1C6A | [6 empty] | 415
1622 |  |  |  |  | SPARE23 | MCCB 3XC16A + RCD | [6 empty] | 415
1623 |  |  |  |  | SPARE24 | MCCB 3XC16A + RCD | [6 empty] | 415
1624 |  |  |  |  | SPARE25 | MCCB 3X1C0A + RCD | [6 empty] | 415
1625 |  |  |  |  | SPARE26 | MCCB 3XC10A + RCD | [6 empty] | 415
1626 |  |  |  |  | SPARE27 | MCCB 1XC16A | [6 empty] | 240
1627 |  |  |  |  | SPARE28 | MCCB 1XC16A | [6 empty] | 240
1628 |  |  |  |  | SPARE29 | MCCB 1XC16A | [6 empty] | 240
1629 |  |  |  |  | SPARE30 | MCCB 1XC16A | [6 empty] | 240
1630 |  |  |  |  | SPARE31 | MCCB 1XC16A | [6 empty] | 240
1631 |  |  |  |  | SPARE32 | MCCB 1XC16A | [6 empty] | 240
1632 |  |  |  |  | SPARE33 | MCCB 1XC10A | [6 empty] | 240
1633 |  |  |  |  | SPARE34 | MCCB 1XC10A | [6 empty] | 240
1634 |  |  |  |  | SPARE35 | MCCB 1XC10A | [6 empty] | 240
1635 |  |  |  |  | SPARE36 | MCCB 1XC10A | [6 empty] | 240
1636 |  |  |  |  | SPARE37 | MCCB 1XC10A | [6 empty] | 240
1637 |  |  |  |  | SPARE38 | MCCB 1XC10A | [6 empty] | 240
1638 |  |  |  |  | SPARE39 | MCCB 1XC10A + RCD | [6 empty] | 240
1639 |  |  |  |  | SPARE40 | MCCB 1XC10A + RCD | [6 empty] | 240
1640 |  |  |  |  | SPARE41 | MCCB 1XC10A + RCD | [6 empty] | 240
1641 |  |  |  |  | SPARE42 | MCCB 1XC10A + RCD | [6 empty] | 240
1642 |  |  |  |  | SPARE43 | MCCB 1XC16A + RCD | [6 empty] | 240
1643 |  |  |  |  | SPARE44 | MCCB 1XC16A + RCD | [6 empty] | 240
1644 |  |  |  |  | SPARE45 | MCCB 1XC16A + RCD | [6 empty] | 240
1645 |  |  |  |  | SPARE46 | MCCB 1XC16A + RCD | [6 empty] | 240
1646 |  |  |  |  | SPARE47 | MCCD 1x16A + RCD + Contactor | [6 empty] | 240
1647 |  |  |  |  | SPARE48 | MCCD 1x16A + RCD + Contactor | [6 empty] | 240
1648 |  |  |  |  | SPARE49 | MCCD 1x10A + RCD + Contactor | [6 empty] | 240
1649 |  |  |  |  | SPARE50 | MCCD 1x10A + RCD + Contactor | [6 empty] | 240
1650 |  |  |  |  | SPARE51 | MCCD 3x16A + RCD + Contactor | [6 empty] | 415
1651 |  |  |  |  | SPARE52 | MCCD 3x16A + RCD + Contactor | [6 empty] | 415
1652 |  |  |  |  | SPARE53 | DISTRIBUTION BREAKER 100 A to Client | [6 empty] | 415
1653 |  |  |  |  | SPARE54 | DISTRIBUTION BREAKER 100 A to Client | [6 empty] | 415
1654 |  |  |  |  | BB1DB001 | MAINTENANCE POWER OUTLET 1 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1655 |  |  |  |  | BB1DB002 | MAINTENANCE POWER OUTLET 2 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1656 |  |  |  |  | BB1DB003 | MAINTENANCE POWER OUTLET 3 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1657 |  |  |  |  | BB1DB004 | MAINTENANCE POWER OUTLET 4 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1658 |  |  |  |  | BB1DB005 | MAINTENANCE POWER OUTLET 5 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1659 |  |  |  |  | BB1DB006 | MAINTENANCE POWER OUTLET 6 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1660 |  |  |  |  | BB1DB007 | MAINTENANCE POWER OUTLET 7 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1661 |  |  |  |  | BB1DB008 | MAINTENANCE POWER OUTLET 8 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1662 |  |  |  |  | BB1DB009 | MAINTENANCE POWER OUTLET 9 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1663 |  |  |  |  | BB1DB010 | MAINTENANCE POWER OUTLET 10 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1664 |  |  |  |  | BB1DB011 | MAINTENANCE POWER OUTLET 11 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1665 |  |  |  |  | BB1DB012 | MAINTENANCE POWER OUTLET 12 |  | 1X63A 3PH, 2X16A 1-PH |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1666 |  |  |  |  | BB1CP050 | FUEL RECEIVING STATION LIFT DOOR 1 |  | 16 A MCB |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1667 |  |  |  |  | BB1CP051 | FUEL RECEIVING STATION LIFT DOOR 2 |  | 16 A MCB |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1668 |  |  |  |  | BB1CP052 | FUEL RECEIVING STATION LIFT DOOR 3 |  | 16 A MCB |  |  |  |  | 415 | [55 empty] | Feed in Building DB | 3
1669 |  |  |  |  | BB1EQ001 | AUTOMATION CABINET | [6 empty] | 240 | [5 empty] | UPS | [49 empty] | UPS feed added | 4
1670 |  |  |  |  | BB1EQ002 | IT CABINET |  | 2x25A feed for cabinet |  |  |  |  | 240 | [5 empty] | UPS | [49 empty] | Detail about feed added | 4
1671 |  |  |  |  | BB1DB013 | BUILDING ELECTRIFICATION CABINET |  |  |  |  | 400 A breaker |  | 415 | [55 empty] | Breaker size added | 3
1672 |  |  |  |  | BB1EQ003 | UPS | [6 empty] | 415 | [26 empty] | 1
1673 | [5 empty] | HMI Sockets 1 in Control room | [6 empty] | 240 | [5 empty] | UPS | [49 empty] | Feed added | 4
1674 | [5 empty] | HMI Sockets 2 in Control room | [6 empty] | 240 | [5 empty] | UPS | [49 empty] | Feed added | 4
1675 | [5 empty] | 16A MCB Feed for weight bridge controller |  | cabling in customer scope |  |  | 16 |  | 240 | [5 empty] | UPS | [49 empty] | Feed added | 4
1676 | [5 empty] | 16A MCB Feed for customer PLC-cabinet |  | cabling in customer scope |  |  | 16 |  | 240 | [5 empty] | UPS | [8 empty] | UPS OK LAMP | [11 empty] | X | [28 empty] | Feed added | 4
1677 | [5 empty] | ESP MCC feed |  |  |  | 132 | 315 |  | 415 | [55 empty] | Feed added | 1
1678 |  |  |  |  | BB1EW001 | kWH-measurement | [6 empty] | 415 | [28 empty] | 1
[28 empty] | kWh-measurement | [13 empty] | X
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## Sheet1 (hidden)
TAG | DESCRIPTION | DEVICE_COUNT | DO | DI | AO | AI | SDO | SDI | SAO | SAI
KPA_FLOORX_IO | KPA NON ASSIGNED IO | 485 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR0_IO | KPA LEVEL 0 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR1_IO | KPA LEVEL 1 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR2_IO | KPA LEVEL 2 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR3_IO | KPA LEVEL 3 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR4_IO | KPA LEVEL 4 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FUEL_STATION_IO | KPA FUEL STATION REMOTE IO CABINET | 132 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_MCC | KPA REMOTE IO INTERNAL TO MCC | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_PLC | KPA PLC CABINET | 87 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
ESP_PLC | ESP PLC CABINET | 8 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
ESP_MCC | ESP REMOTE IO INTERNAL TO MCC | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## _Parameters
Parameter | Value
jobNumber | 38025
dwgCategory | ELE
protoPath | S:\Elecdes\prototypes\gen6\INSTRUMENTATION\
protoPathMotor | S:\Elecdes\prototypes\gen6\MOTORS\