## POINTIO_1DI_LOOP24VDC
PREFIX | DRAWING | PROTOTYPE | W1NAME | W2NAME | X1NAME | X1DESC | P1NAME | P1RACK | P1SLOT | P1CHAN | P1MFG | P1CATN | P1CATD | P1CATD2 | P1TAG | P1DESC2 | P1DESC3 | P1DESC4 | P1T1 | P1T2 | P1T1TYPE | P1T2TYPE | D1TAG | D1DESC2 | D1DESC3 | D1DESC4 | D1TYPE | D1T1 | D1T2 | C1CATN | C1CATD | C1TAG | C1CORE1 | C1CORE2
38025-ELE | 01-300._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | #N/A | #N/A | KPA_FLOORX_IO | KPA NON ASSIGNED IO | #N/A | #N/A | #N/A | #N/A | 2 | #N/A | #N/A | #N/A | <004> | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | <ExcelError> | <ExcelError> | <ExcelError> | <ExcelError> | <004> | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | <ExcelError> | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | <004>/01 | BN | BU
38025-ELE | 01-301._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:35.DI:V+ BB1FS003 | RIO_02:35.DI:01 BB1FS003 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 35 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1FS003 | BOTTOM ASH COOLING | FLOW SWITCH | None | V+ | 1 | 24VDC | DI | BB1FS003 | BOTTOM ASH COOLING | FLOW SWITCH | None | FLOW SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1FS003/01 | BN | BU
38025-ELE | 01-302._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:01.DI:V+ BB1GS001 | RIO_01:01.DI:00 BB1GS001 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 01 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS001 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | V+ | 0 | 24VDC | DI | BB1GS001 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS001/01 | BN | BU
38025-ELE | 01-303._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:01.DI:V+ BB1GS002 | RIO_01:01.DI:01 BB1GS002 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 01 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS002 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | V+ | 1 | 24VDC | DI | BB1GS002 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS002/01 | BN | BU
38025-ELE | 01-304._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:00.DI:V+ BB1GS003 | RIO_01:00.DI:03 BB1GS003 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 00 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS003 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | V+ | 3 | 24VDC | DI | BB1GS003 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS003/01 | BN | BU
38025-ELE | 01-305._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:00.DI:V+ BB1GS004 | RIO_01:00.DI:02 BB1GS004 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 00 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS004 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | V+ | 2 | 24VDC | DI | BB1GS004 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS004/01 | BN | BU
38025-ELE | 01-306._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:01.DI:V+ BB1GS005 | RIO_01:01.DI:02 BB1GS005 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 01 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS005 | FW TANK OVERFLOW ON-OFF | VALVE POSITION | None | V+ | 2 | 24VDC | DI | BB1GS005 | FW TANK OVERFLOW ON-OFF | VALVE POSITION | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS005/01 | BN | BU
38025-ELE | 01-307._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:01.DI:V+ BB1GS006 | RIO_01:01.DI:03 BB1GS006 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 01 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS006 | FW TANK OVERFLOW ON-OFF | VALVE POSITION | None | V+ | 3 | 24VDC | DI | BB1GS006 | FW TANK OVERFLOW ON-OFF | VALVE POSITION | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS006/01 | BN | BU
38025-ELE | 01-308._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:02.DI:V+ BB1GS007 | RIO_01:02.DI:00 BB1GS007 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 02 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS007 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN | None | V+ | 0 | 24VDC | DI | BB1GS007 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS007/01 | BN | BU
38025-ELE | 01-309._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:02.DI:V+ BB1GS008 | RIO_01:02.DI:01 BB1GS008 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 02 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS008 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE | None | V+ | 1 | 24VDC | DI | BB1GS008 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS008/01 | BN | BU
38025-ELE | 01-310._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:02.DI:V+ BB1GS009 | RIO_01:02.DI:02 BB1GS009 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 02 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS009 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN | None | V+ | 2 | 24VDC | DI | BB1GS009 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS009/01 | BN | BU
38025-ELE | 01-311._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:02.DI:V+ BB1GS010 | RIO_01:02.DI:03 BB1GS010 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 02 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS010 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE | None | V+ | 3 | 24VDC | DI | BB1GS010 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS010/01 | BN | BU
38025-ELE | 01-312._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:03.DI:V+ BB1GS011 | RIO_01:03.DI:00 BB1GS011 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 03 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS011 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | V+ | 0 | 24VDC | DI | BB1GS011 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS011/01 | BN | BU
38025-ELE | 01-313._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:03.DI:V+ BB1GS012 | RIO_01:03.DI:01 BB1GS012 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 03 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS012 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | V+ | 1 | 24VDC | DI | BB1GS012 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS012/01 | BN | BU
38025-ELE | 01-314._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:38.DI:V+ BB1GS020 | RIO_02:38.DI:03 BB1GS020 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 38 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS020 | EMERGENCY SHOWER | USE SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS020 | EMERGENCY SHOWER | USE SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS020/01 | BN | BU
38025-ELE | 01-315._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:05.DI:V+ BB1GS200 | RIO_02:05.DI:00 BB1GS200 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 05 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS200 | SOOTBLOWER 1 IN | LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS200 | SOOTBLOWER 1 IN | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS200/01 | BN | BU
38025-ELE | 01-316._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:05.DI:V+ BB1GS201 | RIO_02:05.DI:01 BB1GS201 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 05 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS201 | SOOTBLOWER 1 OUT | LIMIT SWITCH | None | V+ | 1 | 24VDC | DI | BB1GS201 | SOOTBLOWER 1 OUT | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS201/01 | BN | BU
38025-ELE | 01-317._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:05.DI:V+ BB1GS203 | RIO_02:05.DI:02 BB1GS203 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 05 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS203 | SOOTBLOWER 2 OUT | LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS203 | SOOTBLOWER 2 OUT | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS203/01 | BN | BU
38025-ELE | 01-318._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:05.DI:V+ BB1GS204 | RIO_02:05.DI:03 BB1GS204 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 05 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS204 | SOOTBLOWER 2 IN | LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS204 | SOOTBLOWER 2 IN | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS204/01 | BN | BU
38025-ELE | 01-319._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:06.DI:V+ BB1GS205 | RIO_02:06.DI:00 BB1GS205 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 06 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS205 | SOOTBLOWER 3 OUT | LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS205 | SOOTBLOWER 3 OUT | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS205/01 | BN | BU
38025-ELE | 01-320._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:06.DI:V+ BB1GS206 | RIO_02:06.DI:01 BB1GS206 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 06 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS206 | SOOTBLOWER 3 IN | LIMIT SWITCH | None | V+ | 1 | 24VDC | DI | BB1GS206 | SOOTBLOWER 3 IN | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS206/01 | BN | BU
38025-ELE | 01-321._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:06.DI:V+ BB1GS207 | RIO_02:06.DI:02 BB1GS207 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 06 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS207 | SOOTBLOWER 5 OUT | LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS207 | SOOTBLOWER 5 OUT | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS207/01 | BN | BU
38025-ELE | 01-322._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:06.DI:V+ BB1GS208 | RIO_02:06.DI:03 BB1GS208 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 06 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS208 | SOOTBLOWER 5 IN | LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS208 | SOOTBLOWER 5 IN | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS208/01 | BN | BU
38025-ELE | 01-323._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:07.DI:V+ BB1GS209 | RIO_02:07.DI:00 BB1GS209 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 07 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS209 | SOOTBLOWER 6 OUT | LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS209 | SOOTBLOWER 6 OUT | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS209/01 | BN | BU
38025-ELE | 01-324._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:07.DI:V+ BB1GS210 | RIO_02:07.DI:01 BB1GS210 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 07 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS210 | SOOTBLOWER 6 IN | LIMIT SWITCH | None | V+ | 1 | 24VDC | DI | BB1GS210 | SOOTBLOWER 6 IN | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS210/01 | BN | BU
38025-ELE | 01-325._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:07.DI:V+ BB1GS211 | RIO_02:07.DI:02 BB1GS211 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 07 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS211 | SOOTBLOWER 7 OUT | LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS211 | SOOTBLOWER 7 OUT | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS211/01 | BN | BU
38025-ELE | 01-326._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:07.DI:V+ BB1GS212 | RIO_02:07.DI:03 BB1GS212 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 07 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS212 | SOOTBLOWER 7 IN | LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS212 | SOOTBLOWER 7 IN | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS212/01 | BN | BU
38025-ELE | 01-327._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:08.DI:V+ BB1GS213 | RIO_02:08.DI:00 BB1GS213 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 08 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS213 | SOOTBLOWER 8 OUT | LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS213 | SOOTBLOWER 8 OUT | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS213/01 | BN | BU
38025-ELE | 01-328._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:08.DI:V+ BB1GS214 | RIO_02:08.DI:01 BB1GS214 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 08 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS214 | SOOTBLOWER 8 IN | LIMIT SWITCH | None | V+ | 1 | 24VDC | DI | BB1GS214 | SOOTBLOWER 8 IN | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS214/01 | BN | BU
38025-ELE | 01-329._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:12.DI:V+ BB1GS215 | RIO_02:12.DI:00 BB1GS215 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 12 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS215 | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | V+ | 0 | 24VDC | DI | BB1GS215 | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS215/01 | BN | BU
38025-ELE | 01-330._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:12.DI:V+ BB1GS216 | RIO_02:12.DI:01 BB1GS216 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 12 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS216 | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | V+ | 1 | 24VDC | DI | BB1GS216 | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS216/01 | BN | BU
38025-ELE | 01-331._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:10.DI:V+ BB1GS217 | RIO_02:10.DI:00 BB1GS217 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 10 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS217 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | V+ | 0 | 24VDC | DI | BB1GS217 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS217/01 | BN | BU
38025-ELE | 01-332._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:10.DI:V+ BB1GS218 | RIO_02:10.DI:01 BB1GS218 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 10 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS218 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | V+ | 1 | 24VDC | DI | BB1GS218 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS218/01 | BN | BU
38025-ELE | 01-333._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:10.DI:V+ BB1GS219 | RIO_02:10.DI:02 BB1GS219 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 10 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS219 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | V+ | 2 | 24VDC | DI | BB1GS219 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS219/01 | BN | BU
38025-ELE | 01-334._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:10.DI:V+ BB1GS220 | RIO_02:10.DI:03 BB1GS220 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 10 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS220 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | V+ | 3 | 24VDC | DI | BB1GS220 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS220/01 | BN | BU
38025-ELE | 01-335._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:03.DI:V+ BB1GS221 | RIO_01:03.DI:02 BB1GS221 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 03 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS221 | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS221 | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS221/01 | BN | BU
38025-ELE | 01-336._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:03.DI:V+ BB1GS222 | RIO_01:03.DI:03 BB1GS222 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 03 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS222 | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS222 | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS222/01 | BN | BU
38025-ELE | 01-337._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:04.DI:V+ BB1GS223 | RIO_02:04.DI:00 BB1GS223 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 04 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS223 | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS223 | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS223/01 | BN | BU
38025-ELE | 01-338._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:04.DI:V+ BB1GS224 | RIO_02:04.DI:01 BB1GS224 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 04 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS224 | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH | None | V+ | 1 | 24VDC | DI | BB1GS224 | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS224/01 | BN | BU
38025-ELE | 01-339._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:04.DI:V+ BB1GS225 | RIO_02:04.DI:02 BB1GS225 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 04 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS225 | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS225 | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS225/01 | BN | BU
38025-ELE | 01-340._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:04.DI:V+ BB1GS226 | RIO_02:04.DI:03 BB1GS226 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 04 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS226 | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS226 | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS226/01 | BN | BU
38025-ELE | 01-341._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:08.DI:V+ BB1GS227 | RIO_02:08.DI:02 BB1GS227 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 08 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS227 | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS227 | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS227/01 | BN | BU
38025-ELE | 01-342._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:08.DI:V+ BB1GS228 | RIO_02:08.DI:03 BB1GS228 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 08 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS228 | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS228 | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS228/01 | BN | BU
38025-ELE | 01-343._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:09.DI:V+ BB1GS230 | RIO_02:09.DI:01 BB1GS230 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 09 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS230 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | V+ | 1 | 24VDC | DI | BB1GS230 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS230/01 | BN | BU
38025-ELE | 01-344._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:09.DI:V+ BB1GS231 | RIO_02:09.DI:00 BB1GS231 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 09 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS231 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | V+ | 0 | 24VDC | DI | BB1GS231 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS231/01 | BN | BU
38025-ELE | 01-345._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:09.DI:V+ BB1GS232 | RIO_02:09.DI:03 BB1GS232 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 09 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS232 | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS232 | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS232/01 | BN | BU
38025-ELE | 01-346._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:09.DI:V+ BB1GS233 | RIO_02:09.DI:02 BB1GS233 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 09 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS233 | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS233 | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS233/01 | BN | BU
38025-ELE | 01-347._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:21.DI:V+ BB1GS600 | RIO_02:21.DI:03 BB1GS600 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 21 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS600 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN | None | V+ | 3 | 24VDC | DI | BB1GS600 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS600/01 | BN | BU
38025-ELE | 01-348._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:17.DI:V+ BB1GS601 | RIO_02:17.DI:01 BB1GS601 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 17 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS601 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT | None | V+ | 1 | 24VDC | DI | BB1GS601 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS601/01 | BN | BU
38025-ELE | 01-349._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:16.DI:V+ BB1GS602 | RIO_02:16.DI:00 BB1GS602 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 16 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS602 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN | None | V+ | 0 | 24VDC | DI | BB1GS602 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS602/01 | BN | BU
38025-ELE | 01-350._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:15.DI:V+ BB1GS603 | RIO_02:15.DI:00 BB1GS603 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 15 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS603 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT | None | V+ | 0 | 24VDC | DI | BB1GS603 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS603/01 | BN | BU
38025-ELE | 01-351._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:21.DI:V+ BB1GS604 | RIO_02:21.DI:00 BB1GS604 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 21 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS604 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN | None | V+ | 0 | 24VDC | DI | BB1GS604 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS604/01 | BN | BU
38025-ELE | 01-352._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:16.DI:V+ BB1GS605 | RIO_02:16.DI:03 BB1GS605 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 16 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS605 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT | None | V+ | 3 | 24VDC | DI | BB1GS605 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS605/01 | BN | BU
38025-ELE | 01-353._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:13.DI:V+ BB1GS606 | RIO_02:13.DI:00 BB1GS606 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 13 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS606 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN | None | V+ | 0 | 24VDC | DI | BB1GS606 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS606/01 | BN | BU
38025-ELE | 01-354._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:16.DI:V+ BB1GS607 | RIO_02:16.DI:02 BB1GS607 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 16 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS607 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT | None | V+ | 2 | 24VDC | DI | BB1GS607 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS607/01 | BN | BU
38025-ELE | 01-355._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:20.DI:V+ BB1GS608 | RIO_02:20.DI:03 BB1GS608 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 20 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS608 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN | None | V+ | 3 | 24VDC | DI | BB1GS608 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS608/01 | BN | BU
38025-ELE | 01-356._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:18.DI:V+ BB1GS609 | RIO_02:18.DI:01 BB1GS609 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 18 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS609 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT | None | V+ | 1 | 24VDC | DI | BB1GS609 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS609/01 | BN | BU
38025-ELE | 01-357._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:22.DI:V+ BB1GS610 | RIO_02:22.DI:01 BB1GS610 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 22 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS610 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN | None | V+ | 1 | 24VDC | DI | BB1GS610 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS610/01 | BN | BU
38025-ELE | 01-358._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:12.DI:V+ BB1GS611 | RIO_02:12.DI:03 BB1GS611 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 12 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS611 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT | None | V+ | 3 | 24VDC | DI | BB1GS611 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS611/01 | BN | BU
38025-ELE | 01-359._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:19.DI:V+ BB1GS612 | RIO_02:19.DI:01 BB1GS612 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 19 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS612 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN | None | V+ | 1 | 24VDC | DI | BB1GS612 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS612/01 | BN | BU
38025-ELE | 01-360._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:19.DI:V+ BB1GS613 | RIO_02:19.DI:03 BB1GS613 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 19 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS613 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT | None | V+ | 3 | 24VDC | DI | BB1GS613 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS613/01 | BN | BU
38025-ELE | 01-361._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:13.DI:V+ BB1GS614 | RIO_02:13.DI:01 BB1GS614 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 13 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS614 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN | None | V+ | 1 | 24VDC | DI | BB1GS614 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS614/01 | BN | BU
38025-ELE | 01-362._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:14.DI:V+ BB1GS615 | RIO_02:14.DI:01 BB1GS615 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 14 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS615 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT | None | V+ | 1 | 24VDC | DI | BB1GS615 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS615/01 | BN | BU
38025-ELE | 01-363._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:21.DI:V+ BB1GS616 | RIO_02:21.DI:02 BB1GS616 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 21 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS616 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN | None | V+ | 2 | 24VDC | DI | BB1GS616 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS616/01 | BN | BU
38025-ELE | 01-364._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:18.DI:V+ BB1GS617 | RIO_02:18.DI:03 BB1GS617 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 18 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS617 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT | None | V+ | 3 | 24VDC | DI | BB1GS617 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS617/01 | BN | BU
38025-ELE | 01-365._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:20.DI:V+ BB1GS618 | RIO_02:20.DI:01 BB1GS618 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 20 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS618 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN | None | V+ | 1 | 24VDC | DI | BB1GS618 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS618/01 | BN | BU
38025-ELE | 01-366._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:13.DI:V+ BB1GS619 | RIO_02:13.DI:02 BB1GS619 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 13 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS619 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT | None | V+ | 2 | 24VDC | DI | BB1GS619 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS619/01 | BN | BU
38025-ELE | 01-367._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:20.DI:V+ BB1GS620 | RIO_02:20.DI:00 BB1GS620 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 20 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS620 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN | None | V+ | 0 | 24VDC | DI | BB1GS620 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS620/01 | BN | BU
38025-ELE | 01-368._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:12.DI:V+ BB1GS621 | RIO_02:12.DI:02 BB1GS621 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 12 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS621 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT | None | V+ | 2 | 24VDC | DI | BB1GS621 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS621/01 | BN | BU
38025-ELE | 01-369._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:15.DI:V+ BB1GS622 | RIO_02:15.DI:03 BB1GS622 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 15 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS622 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN | None | V+ | 3 | 24VDC | DI | BB1GS622 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS622/01 | BN | BU
38025-ELE | 01-370._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:14.DI:V+ BB1GS623 | RIO_02:14.DI:02 BB1GS623 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 14 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS623 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT | None | V+ | 2 | 24VDC | DI | BB1GS623 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS623/01 | BN | BU
38025-ELE | 01-371._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:15.DI:V+ BB1GS650 | RIO_02:15.DI:02 BB1GS650 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 15 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS650 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | V+ | 2 | 24VDC | DI | BB1GS650 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS650/01 | BN | BU
38025-ELE | 01-372._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:13.DI:V+ BB1GS651 | RIO_02:13.DI:03 BB1GS651 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 13 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS651 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | V+ | 3 | 24VDC | DI | BB1GS651 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS651/01 | BN | BU
38025-ELE | 01-373._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:26.DI:V+ BB1GS652 | RIO_02:26.DI:03 BB1GS652 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 26 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS652 | EXPLOSION HATCH | LIMIT SWITCH 1 | None | V+ | 3 | 24VDC | DI | BB1GS652 | EXPLOSION HATCH | LIMIT SWITCH 1 | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS652/01 | BN | BU
38025-ELE | 01-374._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:27.DI:V+ BB1GS653 | RIO_02:27.DI:00 BB1GS653 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 27 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS653 | EXPLOSION HATCH | LIMIT SWITCH 2 | None | V+ | 0 | 24VDC | DI | BB1GS653 | EXPLOSION HATCH | LIMIT SWITCH 2 | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS653/01 | BN | BU
38025-ELE | 01-375._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:27.DI:V+ BB1GS654 | RIO_02:27.DI:01 BB1GS654 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 27 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS654 | EXPLOSION HATCH | LIMIT SWITCH 3 | None | V+ | 1 | 24VDC | DI | BB1GS654 | EXPLOSION HATCH | LIMIT SWITCH 3 | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS654/01 | BN | BU
38025-ELE | 01-376._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:27.DI:V+ BB1GS655 | RIO_02:27.DI:02 BB1GS655 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 27 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS655 | EXPLOSION HATCH | LIMIT SWITCH 4 | None | V+ | 2 | 24VDC | DI | BB1GS655 | EXPLOSION HATCH | LIMIT SWITCH 4 | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS655/01 | BN | BU
38025-ELE | 01-377._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:30.DI:V+ BB1GS656 | RIO_02:30.DI:02 BB1GS656 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 30 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS656 | SLIDE GATE VALVE CLOSE | LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS656 | SLIDE GATE VALVE CLOSE | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS656/01 | BN | BU
38025-ELE | 01-378._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:25.DI:V+ BB1GS659 | RIO_02:25.DI:02 BB1GS659 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 25 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS659 | BELT CONVEYOR | DEVIATION DETECTOR 1 | None | V+ | 2 | 24VDC | DI | BB1GS659 | BELT CONVEYOR | DEVIATION DETECTOR 1 | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS659/01 | BN | BU
38025-ELE | 01-379._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:25.DI:V+ BB1GS660 | RIO_02:25.DI:03 BB1GS660 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 25 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS660 | BELT CONVEYOR | DEVIATION DETECTOR 2 | None | V+ | 3 | 24VDC | DI | BB1GS660 | BELT CONVEYOR | DEVIATION DETECTOR 2 | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS660/01 | BN | BU
38025-ELE | 01-380._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:24.DI:V+ BB1GS661 | RIO_02:24.DI:03 BB1GS661 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 24 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS661 | BELT MAGNET | DEVIATION DETECTOR 1 | None | V+ | 3 | 24VDC | DI | BB1GS661 | BELT MAGNET | DEVIATION DETECTOR 1 | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS661/01 | BN | BU
38025-ELE | 01-381._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:25.DI:V+ BB1GS662 | RIO_02:25.DI:00 BB1GS662 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 25 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS662 | BELT MAGNET | DEVIATION DETECTOR 2 | None | V+ | 0 | 24VDC | DI | BB1GS662 | BELT MAGNET | DEVIATION DETECTOR 2 | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS662/01 | BN | BU
38025-ELE | 01-382._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:26.DI:V+ BB1GS663 | RIO_02:26.DI:00 BB1GS663 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 26 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS663 | BELT CONVEYOR | OVERSIZE DETECTOR | None | V+ | 0 | 24VDC | DI | BB1GS663 | BELT CONVEYOR | OVERSIZE DETECTOR | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS663/01 | BN | BU
38025-ELE | 01-383._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:35.DI:V+ BB1GS800 | RIO_02:35.DI:03 BB1GS800 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 35 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS800 | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | V+ | 3 | 24VDC | DI | BB1GS800 | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS800/01 | BN | BU
38025-ELE | 01-384._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:35.DI:V+ BB1GS801 | RIO_02:35.DI:02 BB1GS801 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 35 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS801 | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | V+ | 2 | 24VDC | DI | BB1GS801 | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS801/01 | BN | BU
38025-ELE | 01-385._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:31.DI:V+ BB1GS802 | RIO_02:31.DI:00 BB1GS802 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 31 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS802 | BOTTOM ASH VALVE | LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS802 | BOTTOM ASH VALVE | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS802/01 | BN | BU
38025-ELE | 01-386._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:31.DI:V+ BB1GS803 | RIO_02:31.DI:01 BB1GS803 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 31 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS803 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | V+ | 1 | 24VDC | DI | BB1GS803 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS803/01 | BN | BU
38025-ELE | 01-387._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:34.DI:V+ BB1GS850 | RIO_02:34.DI:03 BB1GS850 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 34 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS850 | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS850 | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS850/01 | BN | BU
38025-ELE | 01-388._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:35.DI:V+ BB1GS851 | RIO_02:35.DI:00 BB1GS851 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 35 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS851 | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS851 | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS851/01 | BN | BU
38025-ELE | 01-389._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:38.DI:V+ BB1GS852 | RIO_02:38.DI:00 BB1GS852 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 38 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS852 | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR | None | V+ | 0 | 24VDC | DI | BB1GS852 | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS852/01 | BN | BU
38025-ELE | 01-390._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:36.DI:V+ BB1GS853 | RIO_02:36.DI:01 BB1GS853 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 36 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS853 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | V+ | 1 | 24VDC | DI | BB1GS853 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS853/01 | BN | BU
38025-ELE | 01-391._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:36.DI:V+ BB1GS854 | RIO_02:36.DI:00 BB1GS854 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 36 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS854 | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS854 | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS854/01 | BN | BU
38025-ELE | 01-392._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:33.DI:V+ BB1GS855 | RIO_02:33.DI:03 BB1GS855 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 33 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1GS855 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH | None | V+ | 3 | 24VDC | DI | BB1GS855 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS855/01 | BN | BU
38025-ELE | 01-393._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:34.DI:V+ BB1GS856 | RIO_02:34.DI:00 BB1GS856 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 34 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1GS856 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH | None | V+ | 0 | 24VDC | DI | BB1GS856 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS856/01 | BN | BU
38025-ELE | 01-394._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:34.DI:V+ BB1GS857 | RIO_02:34.DI:01 BB1GS857 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 34 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1GS857 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH | None | V+ | 1 | 24VDC | DI | BB1GS857 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS857/01 | BN | BU
38025-ELE | 01-395._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:34.DI:V+ BB1GS858 | RIO_02:34.DI:02 BB1GS858 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 34 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1GS858 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH | None | V+ | 2 | 24VDC | DI | BB1GS858 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH | None | GATE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1GS858/01 | BN | BU
38025-ELE | 01-396._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:18.DI:V+ BB1LS600 | RIO_02:18.DI:00 BB1LS600 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 18 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS600 | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | V+ | 0 | 24VDC | DI | BB1LS600 | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS600/01 | BN | BU
38025-ELE | 01-397._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:17.DI:V+ BB1LS608 | RIO_02:17.DI:02 BB1LS608 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 17 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS608 | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM | None | V+ | 2 | 24VDC | DI | BB1LS608 | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS608/01 | BN | BU
38025-ELE | 01-398._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:18.DI:V+ BB1LS650 | RIO_02:18.DI:02 BB1LS650 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 18 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS650 | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH | None | V+ | 2 | 24VDC | DI | BB1LS650 | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS650/01 | BN | BU
38025-ELE | 01-399._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:19.DI:V+ BB1LS651 | RIO_02:19.DI:00 BB1LS651 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 19 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS651 | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD | None | V+ | 0 | 24VDC | DI | BB1LS651 | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS651/01 | BN | BU
38025-ELE | 01-400._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:17.DI:V+ BB1LS652 | RIO_02:17.DI:00 BB1LS652 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 17 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS652 | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD | None | V+ | 0 | 24VDC | DI | BB1LS652 | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS652/01 | BN | BU
38025-ELE | 01-401._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:21.DI:V+ BB1LS653 | RIO_02:21.DI:01 BB1LS653 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 21 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1LS653 | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD | None | V+ | 1 | 24VDC | DI | BB1LS653 | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS653/01 | BN | BU
38025-ELE | 01-402._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:19.DI:V+ BB1LS654 | RIO_02:19.DI:02 BB1LS654 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 19 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS654 | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD | None | V+ | 2 | 24VDC | DI | BB1LS654 | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS654/01 | BN | BU
38025-ELE | 01-403._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:16.DI:V+ BB1LS655 | RIO_02:16.DI:01 BB1LS655 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 16 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1LS655 | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | V+ | 1 | 24VDC | DI | BB1LS655 | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS655/01 | BN | BU
38025-ELE | 01-404._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:17.DI:V+ BB1LS656 | RIO_02:17.DI:03 BB1LS656 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 17 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1LS656 | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | V+ | 3 | 24VDC | DI | BB1LS656 | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS656/01 | BN | BU
38025-ELE | 01-405._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:27.DI:V+ BB1LS657 | RIO_02:27.DI:03 BB1LS657 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 27 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1LS657 | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH | None | V+ | 3 | 24VDC | DI | BB1LS657 | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS657/01 | BN | BU
38025-ELE | 01-406._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:28.DI:V+ BB1LS658 | RIO_02:28.DI:00 BB1LS658 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 28 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS658 | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH | None | V+ | 0 | 24VDC | DI | BB1LS658 | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS658/01 | BN | BU
38025-ELE | 01-407._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:28.DI:V+ BB1LS659 | RIO_02:28.DI:01 BB1LS659 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 28 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1LS659 | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH | None | V+ | 1 | 24VDC | DI | BB1LS659 | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS659/01 | BN | BU
38025-ELE | 01-408._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:28.DI:V+ BB1LS660 | RIO_02:28.DI:02 BB1LS660 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 28 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1LS660 | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH | None | V+ | 2 | 24VDC | DI | BB1LS660 | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS660/01 | BN | BU
38025-ELE | 01-409._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:30.DI:V+ BB1LS661 | RIO_02:30.DI:03 BB1LS661 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 30 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1LS661 | LUBRICATION ALARM | SCREW DISCHARGER | None | V+ | 3 | 24VDC | DI | BB1LS661 | LUBRICATION ALARM | SCREW DISCHARGER | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS661/01 | BN | BU
38025-ELE | 01-410._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:00.DI:V+ BB1LS700 | RIO_01:00.DI:00 BB1LS700 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 00 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS700 | CHEMICAL TANK 1 | LEVEL SWITCH | None | V+ | 0 | 24VDC | DI | BB1LS700 | CHEMICAL TANK 1 | LEVEL SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS700/01 | BN | BU
38025-ELE | 01-411._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_01:00.DI:V+ BB1LS701 | RIO_01:00.DI:01 BB1LS701 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 01 | 00 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1LS701 | CHEMICAL TANK 2 | LEVEL SWITCH | None | V+ | 1 | 24VDC | DI | BB1LS701 | CHEMICAL TANK 2 | LEVEL SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS701/01 | BN | BU
38025-ELE | 01-412._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:36.DI:V+ BB1LS850 | RIO_02:36.DI:03 BB1LS850 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 36 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1LS850 | BOTTOM ASH CONTAINER | LEVEL SWITCH | None | V+ | 3 | 24VDC | DI | BB1LS850 | BOTTOM ASH CONTAINER | LEVEL SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS850/01 | BN | BU
38025-ELE | 01-413._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:37.DI:V+ BB1LS851 | RIO_02:37.DI:00 BB1LS851 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 37 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1LS851 | BOTTOM ASH CONTAINER | LEVEL SWITCH | None | V+ | 0 | 24VDC | DI | BB1LS851 | BOTTOM ASH CONTAINER | LEVEL SWITCH | None | LEVEL SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1LS851/01 | BN | BU
38025-ELE | 01-414._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:20.DI:V+ BB1PS600 | RIO_02:20.DI:02 BB1PS600 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 20 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1PS600 | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH | None | V+ | 2 | 24VDC | DI | BB1PS600 | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH | None | PRESSURE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1PS600/01 | BN | BU
38025-ELE | 01-415._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:15.DI:V+ BB1PS601 | RIO_02:15.DI:01 BB1PS601 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 15 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1PS601 | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH | None | V+ | 1 | 24VDC | DI | BB1PS601 | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH | None | PRESSURE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1PS601/01 | BN | BU
38025-ELE | 01-416._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:14.DI:V+ BB1PS602 | RIO_02:14.DI:00 BB1PS602 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 14 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1PS602 | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH | None | V+ | 0 | 24VDC | DI | BB1PS602 | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH | None | PRESSURE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1PS602/01 | BN | BU
38025-ELE | 01-417._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:24.DI:V+ BB1PS603 | RIO_02:24.DI:00 BB1PS603 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 24 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1PS603 | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | V+ | 0 | 24VDC | DI | BB1PS603 | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | PRESSURE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1PS603/01 | BN | BU
38025-ELE | 01-418._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:24.DI:V+ BB1PS604 | RIO_02:24.DI:01 BB1PS604 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 24 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1PS604 | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | V+ | 1 | 24VDC | DI | BB1PS604 | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | PRESSURE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1PS604/01 | BN | BU
38025-ELE | 01-419._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:23.DI:V+ BB1PS605 | RIO_02:23.DI:03 BB1PS605 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 23 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1PS605 | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | V+ | 3 | 24VDC | DI | BB1PS605 | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | PRESSURE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1PS605/01 | BN | BU
38025-ELE | 01-420._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:28.DI:V+ BB1ST649 | RIO_02:28.DI:03 BB1ST649 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 28 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST649 | FUEL SILO CROSS CONVEYOR | ROTATION GUARD | None | V+ | 3 | 24VDC | DI | BB1ST649 | FUEL SILO CROSS CONVEYOR | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST649/01 | BN | BU
38025-ELE | 01-421._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:22.DI:V+ BB1ST650 | RIO_02:22.DI:00 BB1ST650 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 22 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1ST650 | SCRAPER CONVEYOR 1, | ROTATION GUARD | None | V+ | 0 | 24VDC | DI | BB1ST650 | SCRAPER CONVEYOR 1, | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST650/01 | BN | BU
38025-ELE | 01-422._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:14.DI:V+ BB1ST651 | RIO_02:14.DI:03 BB1ST651 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 14 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST651 | SCRAPER CONVEYOR 2, | ROTATION GUARD | None | V+ | 3 | 24VDC | DI | BB1ST651 | SCRAPER CONVEYOR 2, | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST651/01 | BN | BU
38025-ELE | 01-423._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:25.DI:V+ BB1ST652 | RIO_02:25.DI:01 BB1ST652 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 25 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST652 | BELT CONVEYOR | ROTATION GUARD | None | V+ | 1 | 24VDC | DI | BB1ST652 | BELT CONVEYOR | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST652/01 | BN | BU
38025-ELE | 01-424._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:29.DI:V+ BB1ST653 | RIO_02:29.DI:01 BB1ST653 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 29 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST653 | FUEL FEEDING SCREW 2 | ROTATION GUARD | None | V+ | 1 | 24VDC | DI | BB1ST653 | FUEL FEEDING SCREW 2 | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST653/01 | BN | BU
38025-ELE | 01-425._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:24.DI:V+ BB1ST654 | RIO_02:24.DI:02 BB1ST654 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 24 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST654 | BELT MAGNET | ROTATION GUARD | None | V+ | 2 | 24VDC | DI | BB1ST654 | BELT MAGNET | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST654/01 | BN | BU
38025-ELE | 01-426._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:29.DI:V+ BB1ST655 | RIO_02:29.DI:03 BB1ST655 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 29 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST655 | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD | None | V+ | 3 | 24VDC | DI | BB1ST655 | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST655/01 | BN | BU
38025-ELE | 01-427._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:26.DI:V+ BB1ST656 | RIO_02:26.DI:01 BB1ST656 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 26 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST656 | DISC SCREEN DRIVE 1 | ROTATION GUARD | None | V+ | 1 | 24VDC | DI | BB1ST656 | DISC SCREEN DRIVE 1 | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST656/01 | BN | BU
38025-ELE | 01-428._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:26.DI:V+ BB1ST657 | RIO_02:26.DI:02 BB1ST657 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 26 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST657 | DISC SCREEN DRIVE 2 | ROTATION GUARD | None | V+ | 2 | 24VDC | DI | BB1ST657 | DISC SCREEN DRIVE 2 | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST657/01 | BN | BU
38025-ELE | 01-429._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:30.DI:V+ BB1ST659 | RIO_02:30.DI:00 BB1ST659 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 30 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1ST659 | FUEL FEEDING SCREW 1 | ROTATION GUARD | None | V+ | 0 | 24VDC | DI | BB1ST659 | FUEL FEEDING SCREW 1 | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST659/01 | BN | BU
38025-ELE | 01-430._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:23.DI:V+ BB1ST673 | RIO_02:23.DI:00 BB1ST673 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 23 | 00 | 2 | 1734-IB4D*M1 | 1734-IB4D | Digital Input 1 (00,01) | BB1ST673 | LEVELING ROLLER 1 | SPEED SWITCH | None | V+ | 0 | 24VDC | DI | BB1ST673 | LEVELING ROLLER 1 | SPEED SWITCH | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST673/01 | BN | BU
38025-ELE | 01-431._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:23.DI:V+ BB1ST674 | RIO_02:23.DI:02 BB1ST674 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 23 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST674 | LEVELING ROLLER 2 | SPEED SWITCH | None | V+ | 2 | 24VDC | DI | BB1ST674 | LEVELING ROLLER 2 | SPEED SWITCH | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST674/01 | BN | BU
38025-ELE | 01-432._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:22.DI:V+ BB1ST675 | RIO_02:22.DI:02 BB1ST675 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 22 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST675 | LEVELING ROLLER 3 | SPEED SWITCH | None | V+ | 2 | 24VDC | DI | BB1ST675 | LEVELING ROLLER 3 | SPEED SWITCH | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST675/01 | BN | BU
38025-ELE | 01-433._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:37.DI:V+ BB1ST850 | RIO_02:37.DI:03 BB1ST850 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 37 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1ST850 | BOTTOM ASH CONVEYOR | ROTATION GUARD | None | V+ | 3 | 24VDC | DI | BB1ST850 | BOTTOM ASH CONVEYOR | ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST850/01 | BN | BU
38025-ELE | 01-434._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:38.DI:V+ BB1ST852 | RIO_02:38.DI:01 BB1ST852 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 38 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1ST852 | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD | None | V+ | 1 | 24VDC | DI | BB1ST852 | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST852/01 | BN | BU
38025-ELE | 01-435._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:38.DI:V+ BB1ST853 | RIO_02:38.DI:02 BB1ST853 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 38 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST853 | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD | None | V+ | 2 | 24VDC | DI | BB1ST853 | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST853/01 | BN | BU
38025-ELE | 01-436._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:37.DI:V+ BB1ST856 | RIO_02:37.DI:02 BB1ST856 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 37 | 02 | 2 | 1734-IB4D*M3 | 1734-IB4D | Digital Input 3 (04,05) | BB1ST856 | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD | None | V+ | 2 | 24VDC | DI | BB1ST856 | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD | None | SPEED SWITCH/ROTATION GUARD | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1ST856/01 | BN | BU
38025-ELE | 01-437._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:23.DI:V+ BB1TS600 | RIO_02:23.DI:01 BB1TS600 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 23 | 01 | 2 | 1734-IB4D*M2 | 1734-IB4D | Digital Input 2 (02,03) | BB1TS600 | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER | None | V+ | 1 | 24VDC | DI | BB1TS600 | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER | None | TEMPERATURE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1TS600/01 | BN | BU
38025-ELE | 01-438._L0 | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DI_LOOP24VDC | RIO_02:22.DI:V+ BB1TS608 | RIO_02:22.DI:03 BB1TS608 | KPA_FLOORX_IO | KPA NON ASSIGNED IO | RIO_ | 02 | 22 | 03 | 2 | 1734-IB4D*M4 | 1734-IB4D | Digital Input 4 (06,07) | BB1TS608 | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL | None | V+ | 3 | 24VDC | DI | BB1TS608 | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL | None | TEMPERATURE SWITCH | + | - | 1P-2C-F-1 | PVC90 2 Core Flex 1mm^2 | BB1TS608/01 | BN | BU