## TAG_DATA
| Prototype Mapping |  | DBF ENTRIES |  |  |  | Panel | [5 empty] | PLC | [12 empty] | Devices | [6 empty] | Cable
Tag | Typical | ProtoName | DWGPREFIX | DWGNUMBER | W1NAME | W2NAME | X1NAME | X1DESC | X1VDC24 | X1VDC0 | X1XIO | X1XIOFI | P1NAME | P1RACK | P1SLOT | P1CHAN | P1CATN | P1CATD | P1CATD2 | P1TAG | P1DESC2 | P1DESC3 | P1DESC4 | P1T1 | P1T2 | P1T1TYPE | P1T2TYPE | D1TAG | D1DESC2 | D1DESC3 | D1DESC4 | D1TYPE | C1TAG
0 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | 0 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | 0 | #N/A | #N/A | #N/A |  | 0/01
<001> | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | <001> | ELECTRICAL ROOM | TEMPERATURE |  |  | #N/A |  | #N/A | <001> | ELECTRICAL ROOM | TEMPERATURE |  |  | <001>/01
<002> | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | <002> | PLC-CABINET | TEMPERATURE |  |  | #N/A |  | #N/A | <002> | PLC-CABINET | TEMPERATURE |  |  | <002>/01
<003> | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | <003> | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  |  | #N/A |  | #N/A | <003> | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  |  | <003>/01
<004> | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-300_.L0 | RIO:01.DI:V+ <004> | RIO01:01.DI:00 <004> | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 01 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | <004> | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | 01 | 01 | 24VDC | DI | <004> | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH | LIMIT SWITCH | <004>/01
<005> | MCCB_1ph |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A | 1 |  |  |  | <005> | SAND TRANSMITTER | 230 VAC FEED |  |  | #N/A |  | #N/A | <005> | SAND TRANSMITTER | 230 VAC FEED |  |  | <005>/01
BB1BL200 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A | 2 |  |  |  | BB1BL200 | SOOTBLOWER 1 |  |  |  | #N/A |  | #N/A | BB1BL200 | SOOTBLOWER 1 |  |  |  | BB1BL200/01
BB1BL201 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A | 3 |  |  |  | BB1BL201 | SOOTBLOWER 2 |  |  |  | #N/A |  | #N/A | BB1BL201 | SOOTBLOWER 2 |  |  |  | BB1BL201/01
BB1BL202 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A | 4 |  |  |  | BB1BL202 | SOOTBLOWER 3 |  |  |  | #N/A |  | #N/A | BB1BL202 | SOOTBLOWER 3 |  |  |  | BB1BL202/01
BB1BL203 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A | 5 |  |  |  | BB1BL203 | SOOTBLOWER 4 |  |  |  | #N/A |  | #N/A | BB1BL203 | SOOTBLOWER 4 |  |  |  | BB1BL203/01
BB1BL204 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A | 6 |  |  |  | BB1BL204 | SOOTBLOWER 5 |  |  |  | #N/A |  | #N/A | BB1BL204 | SOOTBLOWER 5 |  |  |  | BB1BL204/01
BB1BL205 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A | 7 |  |  |  | BB1BL205 | SOOTBLOWER 6 |  |  |  | #N/A |  | #N/A | BB1BL205 | SOOTBLOWER 6 |  |  |  | BB1BL205/01
BB1BL206 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1BL206 | SOOTBLOWER 7 |  |  |  | #N/A |  | #N/A | BB1BL206 | SOOTBLOWER 7 |  |  |  | BB1BL206/01
BB1BU500 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1BU500 | BURNER SIGNALS |  |  |  | #N/A |  | #N/A | BB1BU500 | BURNER SIGNALS |  |  |  | BB1BU500/01
BB1CP002 | MCCB_1ph |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CP002 | SMOKE EXHAUST CABINET |  |  |  | #N/A |  | #N/A | BB1CP002 | SMOKE EXHAUST CABINET |  |  |  | BB1CP002/01
BB1CV001 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV001 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1CV001 | #N/A | #N/A | #N/A |  | BB1CV001/01
BB1CV002 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV002 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1CV002 | #N/A | #N/A | #N/A |  | BB1CV002/01
BB1CV003 | MTR_VLV_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV003 | CONTINUOUS BLOW DOWN | VALVE |  |  | #N/A |  | #N/A | BB1CV003 | CONTINUOUS BLOW DOWN | VALVE |  |  | BB1CV003/01
BB1CV004 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV004 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1CV004 | #N/A | #N/A | #N/A |  | BB1CV004/01
BB1CV200 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV200 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1CV200 | #N/A | #N/A | #N/A |  | BB1CV200/01
BB1CV201 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV201 | START-UP VALVE |  |  |  | #N/A |  | #N/A | BB1CV201 | START-UP VALVE |  |  |  | BB1CV201/01
BB1CV202 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV202 | STEAM PRESSURE REDUCTION | VALVE |  |  | #N/A |  | #N/A | BB1CV202 | STEAM PRESSURE REDUCTION | VALVE |  |  | BB1CV202/01
BB1CV203 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV203 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE |  |  | #N/A |  | #N/A | BB1CV203 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE |  |  | BB1CV203/01
BB1CV402 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV402 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1CV402 | #N/A | #N/A | #N/A |  | BB1CV402/01
BB1CV403 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV403 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1CV403 | #N/A | #N/A | #N/A |  | BB1CV403/01
BB1CV405 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV405 | BOTTOM ASH VALVE | SOLENOID VALVE |  |  | #N/A |  | #N/A | BB1CV405 | BOTTOM ASH VALVE | SOLENOID VALVE |  |  | BB1CV405/01
BB1CV406 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV406 | BOTTOM ASH VALVE | SOLENOID VALVE |  |  | #N/A |  | #N/A | BB1CV406 | BOTTOM ASH VALVE | SOLENOID VALVE |  |  | BB1CV406/01
BB1CV412 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV412 | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  |  | #N/A |  | #N/A | BB1CV412 | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  |  | BB1CV412/01
BB1CV413 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV413 | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER |  | #N/A |  | #N/A | BB1CV413 | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER |  | BB1CV413/01
BB1CV414 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1CV414 | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE |  | #N/A |  | #N/A | BB1CV414 | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE |  | BB1CV414/01
BB1DM300 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DM300 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1DM300 | #N/A | #N/A | #N/A |  | BB1DM300/01
BB1DM301 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DM301 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1DM301 | #N/A | #N/A | #N/A |  | BB1DM301/01
BB1DM302 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DM302 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1DM302 | #N/A | #N/A | #N/A |  | BB1DM302/01
BB1DM303 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DM303 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1DM303 | #N/A | #N/A | #N/A |  | BB1DM303/01
BB1DM304 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DM304 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1DM304 | #N/A | #N/A | #N/A |  | BB1DM304/01
BB1DM400 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DM400 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1DM400 | #N/A | #N/A | #N/A |  | BB1DM400/01
BB1DM550 | #N/A |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DM550 | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | BB1DM550 | #N/A | #N/A | #N/A |  | BB1DM550/01
BB1DR400 | MCCB_1ph |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DR400 | COMPRESSOR 1 DRYER |  |  |  | #N/A |  | #N/A | BB1DR400 | COMPRESSOR 1 DRYER |  |  |  | BB1DR400/01
BB1DR401 | MCCB_1ph |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1DR401 | COMPRESSOR 2 DRYER |  |  |  | #N/A |  | #N/A | BB1DR401 | COMPRESSOR 2 DRYER |  |  |  | BB1DR401/01
BB1EH600 | DOL_DIR_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EH600 | ELECTRIC HEATER | HYDRAULIC UNIT |  |  | #N/A |  | #N/A | BB1EH600 | ELECTRIC HEATER | HYDRAULIC UNIT |  |  | BB1EH600/01
BB1EH662 | MCCB_1ph |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EH662 | HEATER FOR SLIPRING UNIT |  |  |  | #N/A |  | #N/A | BB1EH662 | HEATER FOR SLIPRING UNIT |  |  |  | BB1EH662/01
BB1EM001 | FRQ_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM001 | FEED WATER PUMP 1 |  |  |  | #N/A |  | #N/A | BB1EM001 | FEED WATER PUMP 1 |  |  |  | BB1EM001/01
BB1EM002 | FRQ_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM002 | FEED WATER PUMP 2 |  |  |  | #N/A |  | #N/A | BB1EM002 | FEED WATER PUMP 2 |  |  |  | BB1EM002/01
BB1EM008 | DOL_DIR_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM008 | CONVEYOR COOLING PUMP |  |  |  | #N/A |  | #N/A | BB1EM008 | CONVEYOR COOLING PUMP |  |  |  | BB1EM008/01
BB1EM009 | DOL_DIR_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM009 | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN |  |  | #N/A |  | #N/A | BB1EM009 | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN |  |  | BB1EM009/01
BB1EM400 | FRQ_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM400 | PRIMARY AIR FAN |  |  |  | #N/A |  | #N/A | BB1EM400 | PRIMARY AIR FAN |  |  |  | BB1EM400/01
BB1EM401 | FRQ_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM401 | SECONDARY AIR FAN |  |  |  | #N/A |  | #N/A | BB1EM401 | SECONDARY AIR FAN |  |  |  | BB1EM401/01
BB1EM402 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM402 | COMPRESSOR 1 |  |  |  | #N/A |  | #N/A | BB1EM402 | COMPRESSOR 1 |  |  |  | BB1EM402/01
BB1EM403 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM403 | COMPRESSOR 2 |  |  |  | #N/A |  | #N/A | BB1EM403 | COMPRESSOR 2 |  |  |  | BB1EM403/01
BB1EM405 | BELIMO_VLV |  | #N/A | #N/A | S:\Elecdes\prototypes\v6\INSTRUMENTATION\BELIMO_VLV | BMCC |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM405 | AIR INTAKE GRILL 1 | OPEN |  |  | #N/A |  | #N/A | BB1EM405 | AIR INTAKE GRILL 1 | OPEN |  |  | BB1EM405/01
BB1EM406 | BELIMO_VLV |  | #N/A | #N/A | testVa |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM406 | AIR INTAKE GRILL 2 | OPEN |  |  | #N/A |  | #N/A | BB1EM406 | AIR INTAKE GRILL 2 | OPEN |  |  | BB1EM406/01
BB1EM407 | BELIMO_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM407 | AIR INTAKE GRILL 3 | OPEN |  |  | #N/A |  | #N/A | BB1EM407 | AIR INTAKE GRILL 3 | OPEN |  |  | BB1EM407/01
BB1EM408 | DOL_DIR_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM408 | BOILER HOUSE HEATER 1 |  |  |  | #N/A |  | #N/A | BB1EM408 | BOILER HOUSE HEATER 1 |  |  |  | BB1EM408/01
BB1EM409 | DOL_DIR_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM409 | BOILER HOUSE HEATER 2 |  |  |  | #N/A |  | #N/A | BB1EM409 | BOILER HOUSE HEATER 2 |  |  |  | BB1EM409/01
BB1EM550 | FRQ_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM550 | FLUE GAS FAN |  |  |  | #N/A |  | #N/A | BB1EM550 | FLUE GAS FAN |  |  |  | BB1EM550/01
BB1EM601 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM601 | DUST EXTRACTION | ROTARY FEEDER |  |  | #N/A |  | #N/A | BB1EM601 | DUST EXTRACTION | ROTARY FEEDER |  |  | BB1EM601/01
BB1EM603 | FRQ_DIRH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM603 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  |  | #N/A |  | #N/A | BB1EM603 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  |  | BB1EM603/01
BB1EM604 | FRQ_DIRH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM604 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  |  | #N/A |  | #N/A | BB1EM604 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  |  | BB1EM604/01
BB1EM605 | FRQ_DIRH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM605 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  |  | #N/A |  | #N/A | BB1EM605 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  |  | BB1EM605/01
BB1EM606 | DOL_DIR_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM606 | DUST EXTRACTION FAN |  |  |  | #N/A |  | #N/A | BB1EM606 | DUST EXTRACTION FAN |  |  |  | BB1EM606/01
BB1EM650 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM650 | SLEWING MOTOR FOR SCREW |  |  |  | #N/A |  | #N/A | BB1EM650 | SLEWING MOTOR FOR SCREW |  |  |  | BB1EM650/01
BB1EM651 | DOL_DIR_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM651 | FUEL SILO DUST FILTER FAN |  |  |  | #N/A |  | #N/A | BB1EM651 | FUEL SILO DUST FILTER FAN |  |  |  | BB1EM651/01
BB1EM652 | DOL_DIRH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM652 | ROTATING FUEL SPREADER |  |  |  | #N/A |  | #N/A | BB1EM652 | ROTATING FUEL SPREADER |  |  |  | BB1EM652/01
BB1EM653 | DOL_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM653 | COOLING FAN FUEL | FEEDING SCREW 1 |  |  | #N/A |  | #N/A | BB1EM653 | COOLING FAN FUEL | FEEDING SCREW 1 |  |  | BB1EM653/01
BB1EM654 | DOL_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM654 | LUBRICATION UNIT |  |  |  | #N/A |  | #N/A | BB1EM654 | LUBRICATION UNIT |  |  |  | BB1EM654/01
BB1EM655 | DOL_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM655 | COOLING FAN FUEL | FEEDING SCREW 2 |  |  | #N/A |  | #N/A | BB1EM655 | COOLING FAN FUEL | FEEDING SCREW 2 |  |  | BB1EM655/01
BB1EM656 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM656 | FUEL FEEDING | ROTARY VALVE 2 |  |  | #N/A |  | #N/A | BB1EM656 | FUEL FEEDING | ROTARY VALVE 2 |  |  | BB1EM656/01
BB1EM657 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM657 | FUEL FEEDING | ROTARY VALVE 1 |  |  | #N/A |  | #N/A | BB1EM657 | FUEL FEEDING | ROTARY VALVE 1 |  |  | BB1EM657/01
BB1EM658 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM658 | SCRAPER CONVEYOR 1 |  |  |  | #N/A |  | #N/A | BB1EM658 | SCRAPER CONVEYOR 1 |  |  |  | BB1EM658/01
BB1EM659 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM659 | BELT CONVEYOR |  |  |  | #N/A |  | #N/A | BB1EM659 | BELT CONVEYOR |  |  |  | BB1EM659/01
BB1EM660 | DOL_DIR |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM660 | COOLING FAN FOR | SLEWING MOTOR |  |  | #N/A |  | #N/A | BB1EM660 | COOLING FAN FOR | SLEWING MOTOR |  |  | BB1EM660/01
BB1EM662 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM662 | FUEL SILO SCREW DISCHARGE |  |  |  | #N/A |  | #N/A | BB1EM662 | FUEL SILO SCREW DISCHARGE |  |  |  | BB1EM662/01
BB1EM663 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM663 | FUEL SILO CROSS CONVEYOR |  |  |  | #N/A |  | #N/A | BB1EM663 | FUEL SILO CROSS CONVEYOR |  |  |  | BB1EM663/01
BB1EM664 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM664 | FUEL FEEDING SCREW 1 |  |  |  | #N/A |  | #N/A | BB1EM664 | FUEL FEEDING SCREW 1 |  |  |  | BB1EM664/01
BB1EM665 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM665 | FUEL FEEDING SCREW 2 |  |  |  | #N/A |  | #N/A | BB1EM665 | FUEL FEEDING SCREW 2 |  |  |  | BB1EM665/01
BB1EM670 | DOL_DIRH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM670 | BELT MAGNET |  |  |  | #N/A |  | #N/A | BB1EM670 | BELT MAGNET |  |  |  | BB1EM670/01
BB1EM672 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM672 | SCRAPER CONVEYOR 2 |  |  |  | #N/A |  | #N/A | BB1EM672 | SCRAPER CONVEYOR 2 |  |  |  | BB1EM672/01
BB1EM673 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM673 | LEVELLING ROLLER 1 |  |  |  | #N/A |  | #N/A | BB1EM673 | LEVELLING ROLLER 1 |  |  |  | BB1EM673/01
BB1EM674 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM674 | LEVELLING ROLLER 2 |  |  |  | #N/A |  | #N/A | BB1EM674 | LEVELLING ROLLER 2 |  |  |  | BB1EM674/01
BB1EM675 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM675 | DISC SCREEN DRIVE 1 |  |  |  | #N/A |  | #N/A | BB1EM675 | DISC SCREEN DRIVE 1 |  |  |  | BB1EM675/01
BB1EM676 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM676 | DISC SCREEN DRIVE 2 |  |  |  | #N/A |  | #N/A | BB1EM676 | DISC SCREEN DRIVE 2 |  |  |  | BB1EM676/01
BB1EM703 | DOL_DIRH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM703 | CHEMICAL FILLING PUMP 1 |  |  |  | #N/A |  | #N/A | BB1EM703 | CHEMICAL FILLING PUMP 1 |  |  |  | BB1EM703/01
BB1EM704 | DOL_DIRH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM704 | CHEMICAL FILLING PUMP 2 |  |  |  | #N/A |  | #N/A | BB1EM704 | CHEMICAL FILLING PUMP 2 |  |  |  | BB1EM704/01
BB1EM815 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM815 | FLY ASH CONTAINER SCREW |  |  |  | #N/A |  | #N/A | BB1EM815 | FLY ASH CONTAINER SCREW |  |  |  | BB1EM815/01
BB1EM850 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM850 | 2ND PASS FLY ASH | ROTARY VALVE |  |  | #N/A |  | #N/A | BB1EM850 | 2ND PASS FLY ASH | ROTARY VALVE |  |  | BB1EM850/01
BB1EM851 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM851 | 3RD PASS FLY ASH | ROTARY VALVE |  |  | #N/A |  | #N/A | BB1EM851 | 3RD PASS FLY ASH | ROTARY VALVE |  |  | BB1EM851/01
BB1EM852 | FRQ_REVH |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM852 | BOTTOM ASH CONVEYOR |  |  |  | #N/A |  | #N/A | BB1EM852 | BOTTOM ASH CONVEYOR |  |  |  | BB1EM852/01
BB1EM855 | DOL_REV_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM855 | ASH CONTAINER SCREW |  |  |  | #N/A |  | #N/A | BB1EM855 | ASH CONTAINER SCREW |  |  |  | BB1EM855/01
BB1EM856 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1EM856 | PURIFIED SAND | SCREW CONVEYOR |  |  | #N/A |  | #N/A | BB1EM856 | PURIFIED SAND | SCREW CONVEYOR |  |  | BB1EM856/01
BB1FG300 | ESP_DI_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FG300 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC |  |  | #N/A |  | #N/A | BB1FG300 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC |  |  | BB1FG300/01
BB1FL650 | MCCB_1ph |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FL650 | FUEL SILO DUST FILTER | CONTROL BOX FEED |  |  | #N/A |  | #N/A | BB1FL650 | FUEL SILO DUST FILTER | CONTROL BOX FEED |  |  | BB1FL650/01
BB1FM001 | OESA_3ph |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FM001 | BOTTOM ASH SIEVE FEED |  |  |  | #N/A |  | #N/A | BB1FM001 | BOTTOM ASH SIEVE FEED |  |  |  | BB1FM001/01
BB1FS003 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-301_.L0 | RIO:01.DI:V+ BB1FS003 | RIO01:01.DI:01 BB1FS003 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 01 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1FS003 | BOTTOM ASH COOLING | FLOW SWITCH |  | 01 | 02 | 24VDC | DI | BB1FS003 | BOTTOM ASH COOLING | FLOW SWITCH |  | FLOW SWITCH | BB1FS003/01
BB1FT001 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FT001 | FEED WATER FLOW | AND CONTROL |  |  | #N/A |  | #N/A | BB1FT001 | FEED WATER FLOW | AND CONTROL |  |  | BB1FT001/01
BB1FT200 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FT200 | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT |  | #N/A |  | #N/A | BB1FT200 | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT |  | BB1FT200/01
BB1FT201 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FT201 | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  |  | #N/A |  | #N/A | BB1FT201 | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  |  | BB1FT201/01
BB1FT202 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FT202 | MAIN STEAM FLOW |  |  |  | #N/A |  | #N/A | BB1FT202 | MAIN STEAM FLOW |  |  |  | BB1FT202/01
BB1FT203 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FT203 | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  |  | #N/A |  | #N/A | BB1FT203 | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  |  | BB1FT203/01
BB1FT400 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FT400 | PRIMARY AIR FLOW |  |  |  | #N/A |  | #N/A | BB1FT400 | PRIMARY AIR FLOW |  |  |  | BB1FT400/01
BB1FT401 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FT401 | SECONDARY AIR FLOW |  |  |  | #N/A |  | #N/A | BB1FT401 | SECONDARY AIR FLOW |  |  |  | BB1FT401/01
BB1FT550 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1FT550 | RECIRCULATION GAS FLOW |  |  |  | #N/A |  | #N/A | BB1FT550 | RECIRCULATION GAS FLOW |  |  |  | BB1FT550/01
BB1GS001 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-302_.L0 | RIO:01.DI:V+ BB1GS001 | RIO01:01.DI:02 BB1GS001 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 01 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS001 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | 01 | 03 | 24VDC | DI | BB1GS001 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | GATE SWITCH | BB1GS001/01
BB1GS002 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-303_.L0 | RIO:01.DI:V+ BB1GS002 | RIO01:01.DI:03 BB1GS002 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 01 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS002 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | 01 | 04 | 24VDC | DI | BB1GS002 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | GATE SWITCH | BB1GS002/01
BB1GS003 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-304_.L0 | RIO:01.DI:V+ BB1GS003 | RIO01:01.DI:04 BB1GS003 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 01 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS003 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | 01 | 05 | 24VDC | DI | BB1GS003 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | GATE SWITCH | BB1GS003/01
BB1GS004 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-305_.L0 | RIO:01.DI:V+ BB1GS004 | RIO01:01.DI:05 BB1GS004 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 01 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS004 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | 01 | 06 | 24VDC | DI | BB1GS004 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH | GATE SWITCH | BB1GS004/01
BB1GS005 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-306_.L0 | RIO:01.DI:V+ BB1GS005 | RIO01:01.DI:06 BB1GS005 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 01 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS005 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | 01 | 07 | 24VDC | DI | BB1GS005 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | GATE SWITCH | BB1GS005/01
BB1GS006 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-307_.L0 | RIO:01.DI:V+ BB1GS006 | RIO01:01.DI:07 BB1GS006 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 01 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS006 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | 01 | 08 | 24VDC | DI | BB1GS006 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  | GATE SWITCH | BB1GS006/01
BB1GS007 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-308_.L0 | RIO:01.DI:V+ BB1GS007 | RIO01:02.DI:00 BB1GS007 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 02 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS007 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | 01 | 01 | 24VDC | DI | BB1GS007 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  | GATE SWITCH | BB1GS007/01
BB1GS008 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-309_.L0 | RIO:01.DI:V+ BB1GS008 | RIO01:02.DI:01 BB1GS008 | KPA_+FLOORX_IO | #N/A |  |  |  |  | RIO | 01 | 02 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS008 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | 01 | 02 | 24VDC | DI | BB1GS008 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | GATE SWITCH | BB1GS008/01
BB1GS009 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-310_.L0 | RIO:01.DI:V+ BB1GS009 | RIO01:02.DI:02 BB1GS009 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 02 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS009 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | 01 | 03 | 24VDC | DI | BB1GS009 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  | GATE SWITCH | BB1GS009/01
BB1GS010 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-311_.L0 | RIO:01.DI:V+ BB1GS010 | RIO01:02.DI:03 BB1GS010 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 02 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS010 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | 01 | 04 | 24VDC | DI | BB1GS010 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  | GATE SWITCH | BB1GS010/01
BB1GS011 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-312_.L0 | RIO:01.DI:V+ BB1GS011 | RIO01:02.DI:04 BB1GS011 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 02 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS011 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | 01 | 05 | 24VDC | DI | BB1GS011 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN | GATE SWITCH | BB1GS011/01
BB1GS012 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-313_.L0 | RIO:01.DI:V+ BB1GS012 | RIO01:02.DI:05 BB1GS012 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 02 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS012 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | 01 | 06 | 24VDC | DI | BB1GS012 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE | GATE SWITCH | BB1GS012/01
BB1GS020 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-314_.L0 | RIO:01.DI:V+ BB1GS020 | RIO01:02.DI:06 BB1GS020 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 02 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS020 | EMERGENCY SHOWER | USE SWITCH |  | 01 | 07 | 24VDC | DI | BB1GS020 | EMERGENCY SHOWER | USE SWITCH |  | GATE SWITCH | BB1GS020/01
BB1GS200 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-315_.L0 | RIO:01.DI:V+ BB1GS200 | RIO01:02.DI:07 BB1GS200 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 02 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS200 | SOOTBLOWER 1 IN | LIMIT SWITCH |  | 01 | 08 | 24VDC | DI | BB1GS200 | SOOTBLOWER 1 IN | LIMIT SWITCH |  | GATE SWITCH | BB1GS200/01
BB1GS201 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-316_.L0 | RIO:01.DI:V+ BB1GS201 | RIO01:03.DI:00 BB1GS201 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 03 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS201 | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | 01 | 01 | 24VDC | DI | BB1GS201 | SOOTBLOWER 1 OUT | LIMIT SWITCH |  | GATE SWITCH | BB1GS201/01
BB1GS203 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-317_.L0 | RIO:01.DI:V+ BB1GS203 | RIO01:03.DI:01 BB1GS203 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 03 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS203 | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | 01 | 02 | 24VDC | DI | BB1GS203 | SOOTBLOWER 2 OUT | LIMIT SWITCH |  | GATE SWITCH | BB1GS203/01
BB1GS204 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-318_.L0 | RIO:01.DI:V+ BB1GS204 | RIO01:03.DI:02 BB1GS204 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 03 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS204 | SOOTBLOWER 2 IN | LIMIT SWITCH |  | 01 | 03 | 24VDC | DI | BB1GS204 | SOOTBLOWER 2 IN | LIMIT SWITCH |  | GATE SWITCH | BB1GS204/01
BB1GS205 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-319_.L0 | RIO:01.DI:V+ BB1GS205 | RIO01:03.DI:03 BB1GS205 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 03 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS205 | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | 01 | 04 | 24VDC | DI | BB1GS205 | SOOTBLOWER 3 OUT | LIMIT SWITCH |  | GATE SWITCH | BB1GS205/01
BB1GS206 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-320_.L0 | RIO:01.DI:V+ BB1GS206 | RIO01:03.DI:04 BB1GS206 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 03 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS206 | SOOTBLOWER 3 IN | LIMIT SWITCH |  | 01 | 05 | 24VDC | DI | BB1GS206 | SOOTBLOWER 3 IN | LIMIT SWITCH |  | GATE SWITCH | BB1GS206/01
BB1GS207 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-321_.L0 | RIO:01.DI:V+ BB1GS207 | RIO01:03.DI:05 BB1GS207 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 03 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS207 | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | 01 | 06 | 24VDC | DI | BB1GS207 | SOOTBLOWER 5 OUT | LIMIT SWITCH |  | GATE SWITCH | BB1GS207/01
BB1GS208 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-322_.L0 | RIO:01.DI:V+ BB1GS208 | RIO01:03.DI:06 BB1GS208 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 03 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS208 | SOOTBLOWER 5 IN | LIMIT SWITCH |  | 01 | 07 | 24VDC | DI | BB1GS208 | SOOTBLOWER 5 IN | LIMIT SWITCH |  | GATE SWITCH | BB1GS208/01
BB1GS209 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-323_.L0 | RIO:01.DI:V+ BB1GS209 | RIO01:03.DI:07 BB1GS209 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 03 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS209 | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | 01 | 08 | 24VDC | DI | BB1GS209 | SOOTBLOWER 6 OUT | LIMIT SWITCH |  | GATE SWITCH | BB1GS209/01
BB1GS210 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-324_.L0 | RIO:01.DI:V+ BB1GS210 | RIO01:04.DI:00 BB1GS210 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 04 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS210 | SOOTBLOWER 6 IN | LIMIT SWITCH |  | 01 | 01 | 24VDC | DI | BB1GS210 | SOOTBLOWER 6 IN | LIMIT SWITCH |  | GATE SWITCH | BB1GS210/01
BB1GS211 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-325_.L0 | RIO:01.DI:V+ BB1GS211 | RIO01:04.DI:01 BB1GS211 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 04 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS211 | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | 01 | 02 | 24VDC | DI | BB1GS211 | SOOTBLOWER 7 OUT | LIMIT SWITCH |  | GATE SWITCH | BB1GS211/01
BB1GS212 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-326_.L0 | RIO:01.DI:V+ BB1GS212 | RIO01:04.DI:02 BB1GS212 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 04 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS212 | SOOTBLOWER 7 IN | LIMIT SWITCH |  | 01 | 03 | 24VDC | DI | BB1GS212 | SOOTBLOWER 7 IN | LIMIT SWITCH |  | GATE SWITCH | BB1GS212/01
BB1GS213 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-327_.L0 | RIO:01.DI:V+ BB1GS213 | RIO01:04.DI:03 BB1GS213 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 04 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS213 | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | 01 | 04 | 24VDC | DI | BB1GS213 | SOOTBLOWER 8 OUT | LIMIT SWITCH |  | GATE SWITCH | BB1GS213/01
BB1GS214 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-328_.L0 | RIO:01.DI:V+ BB1GS214 | RIO01:04.DI:04 BB1GS214 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 04 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS214 | SOOTBLOWER 8 IN | LIMIT SWITCH |  | 01 | 05 | 24VDC | DI | BB1GS214 | SOOTBLOWER 8 IN | LIMIT SWITCH |  | GATE SWITCH | BB1GS214/01
BB1GS215 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-329_.L0 | RIO:01.DI:V+ BB1GS215 | RIO01:04.DI:05 BB1GS215 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 04 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS215 | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | 01 | 06 | 24VDC | DI | BB1GS215 | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH | GATE SWITCH | BB1GS215/01
BB1GS216 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-330_.L0 | RIO:01.DI:V+ BB1GS216 | RIO01:04.DI:06 BB1GS216 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 04 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS216 | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | 01 | 07 | 24VDC | DI | BB1GS216 | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH | GATE SWITCH | BB1GS216/01
BB1GS217 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-331_.L0 | RIO:01.DI:V+ BB1GS217 | RIO01:04.DI:07 BB1GS217 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 04 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS217 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | 01 | 08 | 24VDC | DI | BB1GS217 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH | GATE SWITCH | BB1GS217/01
BB1GS218 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-332_.L0 | RIO:01.DI:V+ BB1GS218 | RIO01:05.DI:00 BB1GS218 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 05 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS218 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | 01 | 01 | 24VDC | DI | BB1GS218 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH | GATE SWITCH | BB1GS218/01
BB1GS219 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-333_.L0 | RIO:01.DI:V+ BB1GS219 | RIO01:05.DI:01 BB1GS219 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 05 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS219 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | 01 | 02 | 24VDC | DI | BB1GS219 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH | GATE SWITCH | BB1GS219/01
BB1GS220 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-334_.L0 | RIO:01.DI:V+ BB1GS220 | RIO01:05.DI:02 BB1GS220 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 05 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS220 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | 01 | 03 | 24VDC | DI | BB1GS220 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH | GATE SWITCH | BB1GS220/01
BB1GS221 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-335_.L0 | RIO:01.DI:V+ BB1GS221 | RIO01:05.DI:03 BB1GS221 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 05 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS221 | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | 01 | 04 | 24VDC | DI | BB1GS221 | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  | GATE SWITCH | BB1GS221/01
BB1GS222 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-336_.L0 | RIO:01.DI:V+ BB1GS222 | RIO01:05.DI:04 BB1GS222 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 05 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS222 | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | 01 | 05 | 24VDC | DI | BB1GS222 | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  | GATE SWITCH | BB1GS222/01
BB1GS223 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-337_.L0 | RIO:01.DI:V+ BB1GS223 | RIO01:05.DI:05 BB1GS223 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 05 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS223 | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | 01 | 06 | 24VDC | DI | BB1GS223 | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  | GATE SWITCH | BB1GS223/01
BB1GS224 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-338_.L0 | RIO:01.DI:V+ BB1GS224 | RIO01:05.DI:06 BB1GS224 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 05 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS224 | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | 01 | 07 | 24VDC | DI | BB1GS224 | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  | GATE SWITCH | BB1GS224/01
BB1GS225 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-339_.L0 | RIO:01.DI:V+ BB1GS225 | RIO01:05.DI:07 BB1GS225 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 05 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS225 | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | 01 | 08 | 24VDC | DI | BB1GS225 | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | GATE SWITCH | BB1GS225/01
BB1GS226 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-340_.L0 | RIO:01.DI:V+ BB1GS226 | RIO01:06.DI:00 BB1GS226 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 06 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS226 | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | 01 | 01 | 24VDC | DI | BB1GS226 | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | GATE SWITCH | BB1GS226/01
BB1GS227 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-341_.L0 | RIO:01.DI:V+ BB1GS227 | RIO01:06.DI:01 BB1GS227 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 06 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS227 | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | 01 | 02 | 24VDC | DI | BB1GS227 | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  | GATE SWITCH | BB1GS227/01
BB1GS228 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-342_.L0 | RIO:01.DI:V+ BB1GS228 | RIO01:06.DI:02 BB1GS228 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 06 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS228 | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | 01 | 03 | 24VDC | DI | BB1GS228 | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  | GATE SWITCH | BB1GS228/01
BB1GS230 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-343_.L0 | RIO:01.DI:V+ BB1GS230 | RIO01:06.DI:03 BB1GS230 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 06 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS230 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | 01 | 04 | 24VDC | DI | BB1GS230 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH | GATE SWITCH | BB1GS230/01
BB1GS231 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-344_.L0 | RIO:01.DI:V+ BB1GS231 | RIO01:06.DI:04 BB1GS231 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 06 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS231 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | 01 | 05 | 24VDC | DI | BB1GS231 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH | GATE SWITCH | BB1GS231/01
BB1GS232 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-345_.L0 | RIO:01.DI:V+ BB1GS232 | RIO01:06.DI:05 BB1GS232 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 06 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS232 | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | 01 | 06 | 24VDC | DI | BB1GS232 | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  | GATE SWITCH | BB1GS232/01
BB1GS233 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-346_.L0 | RIO:01.DI:V+ BB1GS233 | RIO01:06.DI:06 BB1GS233 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 06 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS233 | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | 01 | 07 | 24VDC | DI | BB1GS233 | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  | GATE SWITCH | BB1GS233/01
BB1GS401 | BELIMO_VLV__ |  | #N/A | #N/A | S:\Elecdes\prototypes\v6\INSTRUMENTATION\BELIMO_VLV_VARIANT | BRIO |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1GS401 | AIR INTAKE GRILL 1 | OPENED LIMIT |  |  | #N/A |  | #N/A | BB1GS401 | AIR INTAKE GRILL 1 | OPENED LIMIT |  |  | BB1GS401/01
BB1GS412 | BELIMO_VLV__ |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1GS412 | AIR INTAKE GRILL 2 | OPENED LIMIT |  |  | #N/A |  | #N/A | BB1GS412 | AIR INTAKE GRILL 2 | OPENED LIMIT |  |  | BB1GS412/01
BB1GS413 | BELIMO_VLV__ |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1GS413 | AIR INTAKE GRILL 3 | OPENED LIMIT |  |  | #N/A |  | #N/A | BB1GS413 | AIR INTAKE GRILL 3 | OPENED LIMIT |  |  | BB1GS413/01
BB1GS600 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-347_.L0 | RIO:01.DI:V+ BB1GS600 | RIO01:06.DI:07 BB1GS600 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 06 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS600 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | 01 | 08 | 24VDC | DI | BB1GS600 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  | GATE SWITCH | BB1GS600/01
BB1GS601 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-348_.L0 | RIO:01.DI:V+ BB1GS601 | RIO01:07.DI:00 BB1GS601 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 07 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS601 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | 01 | 01 | 24VDC | DI | BB1GS601 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  | GATE SWITCH | BB1GS601/01
BB1GS602 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-349_.L0 | RIO:01.DI:V+ BB1GS602 | RIO01:07.DI:01 BB1GS602 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 07 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS602 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | 01 | 02 | 24VDC | DI | BB1GS602 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  | GATE SWITCH | BB1GS602/01
BB1GS603 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-350_.L0 | RIO:01.DI:V+ BB1GS603 | RIO01:07.DI:02 BB1GS603 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 07 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS603 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | 01 | 03 | 24VDC | DI | BB1GS603 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  | GATE SWITCH | BB1GS603/01
BB1GS604 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-351_.L0 | RIO:01.DI:V+ BB1GS604 | RIO01:07.DI:03 BB1GS604 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 07 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS604 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | 01 | 04 | 24VDC | DI | BB1GS604 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  | GATE SWITCH | BB1GS604/01
BB1GS605 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-352_.L0 | RIO:01.DI:V+ BB1GS605 | RIO01:07.DI:04 BB1GS605 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 07 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS605 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | 01 | 05 | 24VDC | DI | BB1GS605 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  | GATE SWITCH | BB1GS605/01
BB1GS606 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-353_.L0 | RIO:01.DI:V+ BB1GS606 | RIO01:07.DI:05 BB1GS606 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 07 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS606 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | 01 | 06 | 24VDC | DI | BB1GS606 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  | GATE SWITCH | BB1GS606/01
BB1GS607 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-354_.L0 | RIO:01.DI:V+ BB1GS607 | RIO01:07.DI:06 BB1GS607 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 07 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS607 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | 01 | 07 | 24VDC | DI | BB1GS607 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  | GATE SWITCH | BB1GS607/01
BB1GS608 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-355_.L0 | RIO:01.DI:V+ BB1GS608 | RIO01:07.DI:07 BB1GS608 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 07 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS608 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | 01 | 08 | 24VDC | DI | BB1GS608 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  | GATE SWITCH | BB1GS608/01
BB1GS609 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-356_.L0 | RIO:01.DI:V+ BB1GS609 | RIO01:08.DI:00 BB1GS609 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 08 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS609 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | 01 | 01 | 24VDC | DI | BB1GS609 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  | GATE SWITCH | BB1GS609/01
BB1GS610 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-357_.L0 | RIO:01.DI:V+ BB1GS610 | RIO01:08.DI:01 BB1GS610 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 08 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS610 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | 01 | 02 | 24VDC | DI | BB1GS610 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  | GATE SWITCH | BB1GS610/01
BB1GS611 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-358_.L0 | RIO:01.DI:V+ BB1GS611 | RIO01:08.DI:02 BB1GS611 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 08 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS611 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | 01 | 03 | 24VDC | DI | BB1GS611 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  | GATE SWITCH | BB1GS611/01
BB1GS612 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-359_.L0 | RIO:01.DI:V+ BB1GS612 | RIO01:08.DI:03 BB1GS612 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 08 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS612 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | 01 | 04 | 24VDC | DI | BB1GS612 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  | GATE SWITCH | BB1GS612/01
BB1GS613 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-360_.L0 | RIO:01.DI:V+ BB1GS613 | RIO01:08.DI:04 BB1GS613 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 08 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS613 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | 01 | 05 | 24VDC | DI | BB1GS613 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  | GATE SWITCH | BB1GS613/01
BB1GS614 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-361_.L0 | RIO:01.DI:V+ BB1GS614 | RIO01:08.DI:05 BB1GS614 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 08 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS614 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | 01 | 06 | 24VDC | DI | BB1GS614 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  | GATE SWITCH | BB1GS614/01
BB1GS615 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-362_.L0 | RIO:01.DI:V+ BB1GS615 | RIO01:08.DI:06 BB1GS615 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 08 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS615 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | 01 | 07 | 24VDC | DI | BB1GS615 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  | GATE SWITCH | BB1GS615/01
BB1GS616 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-363_.L0 | RIO:01.DI:V+ BB1GS616 | RIO01:08.DI:07 BB1GS616 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 08 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS616 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | 01 | 08 | 24VDC | DI | BB1GS616 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  | GATE SWITCH | BB1GS616/01
BB1GS617 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-364_.L0 | RIO:01.DI:V+ BB1GS617 | RIO01:09.DI:00 BB1GS617 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 09 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS617 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | 01 | 01 | 24VDC | DI | BB1GS617 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  | GATE SWITCH | BB1GS617/01
BB1GS618 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-365_.L0 | RIO:01.DI:V+ BB1GS618 | RIO01:09.DI:01 BB1GS618 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 09 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS618 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | 01 | 02 | 24VDC | DI | BB1GS618 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  | GATE SWITCH | BB1GS618/01
BB1GS619 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-366_.L0 | RIO:01.DI:V+ BB1GS619 | RIO01:09.DI:02 BB1GS619 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 09 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS619 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | 01 | 03 | 24VDC | DI | BB1GS619 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  | GATE SWITCH | BB1GS619/01
BB1GS620 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-367_.L0 | RIO:01.DI:V+ BB1GS620 | RIO01:09.DI:03 BB1GS620 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 09 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS620 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | 01 | 04 | 24VDC | DI | BB1GS620 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  | GATE SWITCH | BB1GS620/01
BB1GS621 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-368_.L0 | RIO:01.DI:V+ BB1GS621 | RIO01:09.DI:04 BB1GS621 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 09 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS621 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | 01 | 05 | 24VDC | DI | BB1GS621 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  | GATE SWITCH | BB1GS621/01
BB1GS622 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-369_.L0 | RIO:01.DI:V+ BB1GS622 | RIO01:09.DI:05 BB1GS622 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 09 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS622 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | 01 | 06 | 24VDC | DI | BB1GS622 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  | GATE SWITCH | BB1GS622/01
BB1GS623 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-370_.L0 | RIO:01.DI:V+ BB1GS623 | RIO01:09.DI:06 BB1GS623 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 09 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS623 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | 01 | 07 | 24VDC | DI | BB1GS623 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  | GATE SWITCH | BB1GS623/01
BB1GS650 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-371_.L0 | RIO:01.DI:V+ BB1GS650 | RIO01:09.DI:07 BB1GS650 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 09 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS650 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | 01 | 08 | 24VDC | DI | BB1GS650 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. | GATE SWITCH | BB1GS650/01
BB1GS651 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-372_.L0 | RIO:01.DI:V+ BB1GS651 | RIO01:10.DI:00 BB1GS651 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 10 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS651 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | 01 | 01 | 24VDC | DI | BB1GS651 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN | GATE SWITCH | BB1GS651/01
BB1GS652 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-373_.L0 | RIO:01.DI:V+ BB1GS652 | RIO01:10.DI:01 BB1GS652 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 10 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS652 | EXPLOSION HATCH | LIMIT SWITCH 1 |  | 01 | 02 | 24VDC | DI | BB1GS652 | EXPLOSION HATCH | LIMIT SWITCH 1 |  | GATE SWITCH | BB1GS652/01
BB1GS653 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-374_.L0 | RIO:01.DI:V+ BB1GS653 | RIO01:10.DI:02 BB1GS653 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 10 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS653 | EXPLOSION HATCH | LIMIT SWITCH 2 |  | 01 | 03 | 24VDC | DI | BB1GS653 | EXPLOSION HATCH | LIMIT SWITCH 2 |  | GATE SWITCH | BB1GS653/01
BB1GS654 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-375_.L0 | RIO:01.DI:V+ BB1GS654 | RIO01:10.DI:03 BB1GS654 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 10 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS654 | EXPLOSION HATCH | LIMIT SWITCH 3 |  | 01 | 04 | 24VDC | DI | BB1GS654 | EXPLOSION HATCH | LIMIT SWITCH 3 |  | GATE SWITCH | BB1GS654/01
BB1GS655 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-376_.L0 | RIO:01.DI:V+ BB1GS655 | RIO01:10.DI:04 BB1GS655 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 10 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS655 | EXPLOSION HATCH | LIMIT SWITCH 4 |  | 01 | 05 | 24VDC | DI | BB1GS655 | EXPLOSION HATCH | LIMIT SWITCH 4 |  | GATE SWITCH | BB1GS655/01
BB1GS656 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-377_.L0 | RIO:01.DI:V+ BB1GS656 | RIO01:10.DI:05 BB1GS656 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 10 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS656 | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | 01 | 06 | 24VDC | DI | BB1GS656 | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  | GATE SWITCH | BB1GS656/01
BB1GS659 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-378_.L0 | RIO:01.DI:V+ BB1GS659 | RIO01:10.DI:06 BB1GS659 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 10 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS659 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | 01 | 07 | 24VDC | DI | BB1GS659 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  | GATE SWITCH | BB1GS659/01
BB1GS660 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-379_.L0 | RIO:01.DI:V+ BB1GS660 | RIO01:10.DI:07 BB1GS660 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 10 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS660 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | 01 | 08 | 24VDC | DI | BB1GS660 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  | GATE SWITCH | BB1GS660/01
BB1GS661 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-380_.L0 | RIO:01.DI:V+ BB1GS661 | RIO01:11.DI:00 BB1GS661 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 11 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS661 | BELT MAGNET | DEVIATION DETECTOR 1 |  | 01 | 01 | 24VDC | DI | BB1GS661 | BELT MAGNET | DEVIATION DETECTOR 1 |  | GATE SWITCH | BB1GS661/01
BB1GS662 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-381_.L0 | RIO:01.DI:V+ BB1GS662 | RIO01:11.DI:01 BB1GS662 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 11 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS662 | BELT MAGNET | DEVIATION DETECTOR 2 |  | 01 | 02 | 24VDC | DI | BB1GS662 | BELT MAGNET | DEVIATION DETECTOR 2 |  | GATE SWITCH | BB1GS662/01
BB1GS663 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-382_.L0 | RIO:01.DI:V+ BB1GS663 | RIO01:11.DI:02 BB1GS663 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 11 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS663 | BELT CONVEYOR | OVERSIZE DETECTOR |  | 01 | 03 | 24VDC | DI | BB1GS663 | BELT CONVEYOR | OVERSIZE DETECTOR |  | GATE SWITCH | BB1GS663/01
BB1GS800 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-383_.L0 | RIO:01.DI:V+ BB1GS800 | RIO01:11.DI:03 BB1GS800 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 11 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS800 | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | 01 | 04 | 24VDC | DI | BB1GS800 | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH | GATE SWITCH | BB1GS800/01
BB1GS801 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-384_.L0 | RIO:01.DI:V+ BB1GS801 | RIO01:11.DI:04 BB1GS801 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 11 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS801 | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | 01 | 05 | 24VDC | DI | BB1GS801 | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH | GATE SWITCH | BB1GS801/01
BB1GS802 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-385_.L0 | RIO:01.DI:V+ BB1GS802 | RIO01:11.DI:05 BB1GS802 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 11 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS802 | BOTTOM ASH VALVE | LIMIT SWITCH |  | 01 | 06 | 24VDC | DI | BB1GS802 | BOTTOM ASH VALVE | LIMIT SWITCH |  | GATE SWITCH | BB1GS802/01
BB1GS803 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-386_.L0 | RIO:01.DI:V+ BB1GS803 | RIO01:11.DI:06 BB1GS803 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 11 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS803 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | 01 | 07 | 24VDC | DI | BB1GS803 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | GATE SWITCH | BB1GS803/01
BB1GS850 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-387_.L0 | RIO:01.DI:V+ BB1GS850 | RIO01:11.DI:07 BB1GS850 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 11 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS850 | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | 01 | 08 | 24VDC | DI | BB1GS850 | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  | GATE SWITCH | BB1GS850/01
BB1GS851 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-388_.L0 | RIO:01.DI:V+ BB1GS851 | RIO01:12.DI:00 BB1GS851 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 12 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS851 | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | 01 | 01 | 24VDC | DI | BB1GS851 | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  | GATE SWITCH | BB1GS851/01
BB1GS852 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-389_.L0 | RIO:01.DI:V+ BB1GS852 | RIO01:12.DI:01 BB1GS852 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 12 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS852 | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | 01 | 02 | 24VDC | DI | BB1GS852 | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  | GATE SWITCH | BB1GS852/01
BB1GS853 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-390_.L0 | RIO:01.DI:V+ BB1GS853 | RIO01:12.DI:02 BB1GS853 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 12 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS853 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | 01 | 03 | 24VDC | DI | BB1GS853 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH | GATE SWITCH | BB1GS853/01
BB1GS854 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-391_.L0 | RIO:01.DI:V+ BB1GS854 | RIO01:12.DI:03 BB1GS854 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 12 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS854 | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | 01 | 04 | 24VDC | DI | BB1GS854 | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  | GATE SWITCH | BB1GS854/01
BB1GS855 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-392_.L0 | RIO:01.DI:V+ BB1GS855 | RIO01:12.DI:04 BB1GS855 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 12 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS855 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | 01 | 05 | 24VDC | DI | BB1GS855 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | GATE SWITCH | BB1GS855/01
BB1GS856 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-393_.L0 | RIO:01.DI:V+ BB1GS856 | RIO01:12.DI:05 BB1GS856 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 12 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS856 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | 01 | 06 | 24VDC | DI | BB1GS856 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | GATE SWITCH | BB1GS856/01
BB1GS857 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-394_.L0 | RIO:01.DI:V+ BB1GS857 | RIO01:12.DI:06 BB1GS857 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 12 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS857 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | 01 | 07 | 24VDC | DI | BB1GS857 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  | GATE SWITCH | BB1GS857/01
BB1GS858 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-395_.L0 | RIO:01.DI:V+ BB1GS858 | RIO01:12.DI:07 BB1GS858 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 12 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1GS858 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | 01 | 08 | 24VDC | DI | BB1GS858 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  | GATE SWITCH | BB1GS858/01
BB1GS859 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1GS859 | BOTTOM ASH TO CONTAINER | IN PLACE |  |  | #N/A |  | #N/A | BB1GS859 | BOTTOM ASH TO CONTAINER | IN PLACE |  |  | BB1GS859/01
BB1HS101 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS101 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  |  | #N/A |  | #N/A | BB1HS101 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  |  | BB1HS101/01
BB1HS102 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS102 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  |  | #N/A |  | #N/A | BB1HS102 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  |  | BB1HS102/01
BB1HS103 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS103 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  |  | #N/A |  | #N/A | BB1HS103 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  |  | BB1HS103/01
BB1HS104 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS104 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  |  | #N/A |  | #N/A | BB1HS104 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  |  | BB1HS104/01
BB1HS105 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS105 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  |  | #N/A |  | #N/A | BB1HS105 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  |  | BB1HS105/01
BB1HS106 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS106 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  |  | #N/A |  | #N/A | BB1HS106 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  |  | BB1HS106/01
BB1HS107 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS107 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  |  | #N/A |  | #N/A | BB1HS107 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  |  | BB1HS107/01
BB1HS108 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS108 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  |  | #N/A |  | #N/A | BB1HS108 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  |  | BB1HS108/01
BB1HS109 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS109 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  |  | #N/A |  | #N/A | BB1HS109 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  |  | BB1HS109/01
BB1HS110 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS110 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  |  | #N/A |  | #N/A | BB1HS110 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  |  | BB1HS110/01
BB1HS111 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS111 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  |  | #N/A |  | #N/A | BB1HS111 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  |  | BB1HS111/01
BB1HS112 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS112 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  |  | #N/A |  | #N/A | BB1HS112 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  |  | BB1HS112/01
BB1HS601 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS601 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  |  | #N/A |  | #N/A | BB1HS601 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  |  | BB1HS601/01
BB1HS602 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS602 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  |  | #N/A |  | #N/A | BB1HS602 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  |  | BB1HS602/01
BB1HS603 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS603 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  |  | #N/A |  | #N/A | BB1HS603 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  |  | BB1HS603/01
BB1HS604 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1HS604 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  |  | #N/A |  | #N/A | BB1HS604 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  |  | BB1HS604/01
BB1IJ001 | ALM_HORN |  | #N/A | #N/A | S:\Elecdes\prototypes\v6\INSTRUMENTATION\ALM_HORN | BMCC |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IJ001 | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  |  | #N/A |  | #N/A | BB1IJ001 | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  |  | BB1IJ001/01
BB1IJ002 | ALM_HORN |  | #N/A | #N/A | S:\Elecdes\prototypes\v6\INSTRUMENTATION\ALM_HORN | BMCC |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IJ002 | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  |  | #N/A |  | #N/A | BB1IJ002 | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  |  | BB1IJ002/01
BB1IJ004 | ALM_HORN |  | #N/A | #N/A | S:\Elecdes\prototypes\v6\INSTRUMENTATION\BELIMO_VLV | BMCC |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IJ004 | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  |  | #N/A |  | #N/A | BB1IJ004 | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  |  | BB1IJ004/01
BB1IL001 | ALM_HORN |  | #N/A | #N/A | S:\Elecdes\prototypes\v6\INSTRUMENTATION\ALM_HORN | BMCC |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IL001 | ALARM HORN AND LIGHT | CO ALARM |  |  | #N/A |  | #N/A | BB1IL001 | ALARM HORN AND LIGHT | CO ALARM |  |  | BB1IL001/01
BB1IV002 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV002 | FEEDWATER PUMP 1 ON-OFF | VALVE |  |  | #N/A |  | #N/A | BB1IV002 | FEEDWATER PUMP 1 ON-OFF | VALVE |  |  | BB1IV002/01
BB1IV003 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV003 | FEED WATER PUMP 2 ON-OFF | VALVE |  |  | #N/A |  | #N/A | BB1IV003 | FEED WATER PUMP 2 ON-OFF | VALVE |  |  | BB1IV003/01
BB1IV004 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV004 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  |  | #N/A |  | #N/A | BB1IV004 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  |  | BB1IV004/01
BB1IV200 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV200 | START-UP CHECK VALVE |  |  |  | #N/A |  | #N/A | BB1IV200 | START-UP CHECK VALVE |  |  |  | BB1IV200/01
BB1IV201 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV201 | MAIN STEAM VALVE |  |  |  | #N/A |  | #N/A | BB1IV201 | MAIN STEAM VALVE |  |  |  | BB1IV201/01
BB1IV202 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV202 | MAIN STEAM VALVE BY-PASS | VALVE |  |  | #N/A |  | #N/A | BB1IV202 | MAIN STEAM VALVE BY-PASS | VALVE |  |  | BB1IV202/01
BB1IV203 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV203 | SOOTBLOWING LINE ON-OFF | VALVE |  |  | #N/A |  | #N/A | BB1IV203 | SOOTBLOWING LINE ON-OFF | VALVE |  |  | BB1IV203/01
BB1IV204 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV204 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE |  | #N/A |  | #N/A | BB1IV204 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE |  | BB1IV204/01
BB1IV205 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV205 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE |  |  | #N/A |  | #N/A | BB1IV205 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE |  |  | BB1IV205/01
BB1IV206 | MTR_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV206 | PRIMARY AIR PREHEATER | ON-OFF VALVE |  |  | #N/A |  | #N/A | BB1IV206 | PRIMARY AIR PREHEATER | ON-OFF VALVE |  |  | BB1IV206/01
BB1IV650 | DOL_REVH_BUS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1IV650 | SLIDE GATE VALVE |  |  |  | #N/A |  | #N/A | BB1IV650 | SLIDE GATE VALVE |  |  |  | BB1IV650/01
BB1LS103 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LS103 | STEAM DRUM LEVEL SWITCH 1 |  |  |  | #N/A |  | #N/A | BB1LS103 | STEAM DRUM LEVEL SWITCH 1 |  |  |  | BB1LS103/01
BB1LS104 | MEAS_BIN_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LS104 | STEAM DRUM LEVEL SWITCH 2 |  |  |  | #N/A |  | #N/A | BB1LS104 | STEAM DRUM LEVEL SWITCH 2 |  |  |  | BB1LS104/01
BB1LS600 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-396_.L0 | RIO:01.DI:V+ BB1LS600 | RIO01:13.DI:00 BB1LS600 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 13 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS600 | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | 01 | 01 | 24VDC | DI | BB1LS600 | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH | LEVEL SWITCH | BB1LS600/01
BB1LS608 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-397_.L0 | RIO:01.DI:V+ BB1LS608 | RIO01:13.DI:01 BB1LS608 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 13 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS608 | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | 01 | 02 | 24VDC | DI | BB1LS608 | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  | LEVEL SWITCH | BB1LS608/01
BB1LS650 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-398_.L0 | RIO:01.DI:V+ BB1LS650 | RIO01:13.DI:02 BB1LS650 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 13 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS650 | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | 01 | 03 | 24VDC | DI | BB1LS650 | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  | LEVEL SWITCH | BB1LS650/01
BB1LS651 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-399_.L0 | RIO:01.DI:V+ BB1LS651 | RIO01:13.DI:03 BB1LS651 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 13 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS651 | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | 01 | 04 | 24VDC | DI | BB1LS651 | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  | LEVEL SWITCH | BB1LS651/01
BB1LS652 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-400_.L0 | RIO:01.DI:V+ BB1LS652 | RIO01:13.DI:04 BB1LS652 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 13 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS652 | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | 01 | 05 | 24VDC | DI | BB1LS652 | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  | LEVEL SWITCH | BB1LS652/01
BB1LS653 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-401_.L0 | RIO:01.DI:V+ BB1LS653 | RIO01:13.DI:05 BB1LS653 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 13 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS653 | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | 01 | 06 | 24VDC | DI | BB1LS653 | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  | LEVEL SWITCH | BB1LS653/01
BB1LS654 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-402_.L0 | RIO:01.DI:V+ BB1LS654 | RIO01:13.DI:06 BB1LS654 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 13 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS654 | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | 01 | 07 | 24VDC | DI | BB1LS654 | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  | LEVEL SWITCH | BB1LS654/01
BB1LS655 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-403_.L0 | RIO:01.DI:V+ BB1LS655 | RIO01:13.DI:07 BB1LS655 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 13 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS655 | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | 01 | 08 | 24VDC | DI | BB1LS655 | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD | LEVEL SWITCH | BB1LS655/01
BB1LS656 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-404_.L0 | RIO:01.DI:V+ BB1LS656 | RIO01:14.DI:00 BB1LS656 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS656 | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | 01 | 01 | 24VDC | DI | BB1LS656 | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD | LEVEL SWITCH | BB1LS656/01
BB1LS657 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-405_.L0 | RIO:01.DI:V+ BB1LS657 | RIO01:14.DI:01 BB1LS657 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS657 | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | 01 | 02 | 24VDC | DI | BB1LS657 | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  | LEVEL SWITCH | BB1LS657/01
BB1LS658 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-406_.L0 | RIO:01.DI:V+ BB1LS658 | RIO01:14.DI:02 BB1LS658 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS658 | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | 01 | 03 | 24VDC | DI | BB1LS658 | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  | LEVEL SWITCH | BB1LS658/01
BB1LS659 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-407_.L0 | RIO:01.DI:V+ BB1LS659 | RIO01:14.DI:03 BB1LS659 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS659 | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | 01 | 04 | 24VDC | DI | BB1LS659 | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  | LEVEL SWITCH | BB1LS659/01
BB1LS660 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-408_.L0 | RIO:01.DI:V+ BB1LS660 | RIO01:14.DI:04 BB1LS660 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS660 | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | 01 | 05 | 24VDC | DI | BB1LS660 | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  | LEVEL SWITCH | BB1LS660/01
BB1LS661 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-409_.L0 | RIO:01.DI:V+ BB1LS661 | RIO01:14.DI:05 BB1LS661 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS661 | LUBRICATION ALARM | SCREW DISCHARGER |  | 01 | 06 | 24VDC | DI | BB1LS661 | LUBRICATION ALARM | SCREW DISCHARGER |  | LEVEL SWITCH | BB1LS661/01
BB1LS700 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-410_.L0 | RIO:01.DI:V+ BB1LS700 | RIO01:14.DI:06 BB1LS700 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS700 | CHEMICAL TANK 1 | LEVEL SWITCH |  | 01 | 07 | 24VDC | DI | BB1LS700 | CHEMICAL TANK 1 | LEVEL SWITCH |  | LEVEL SWITCH | BB1LS700/01
BB1LS701 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-411_.L0 | RIO:01.DI:V+ BB1LS701 | RIO01:14.DI:07 BB1LS701 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS701 | CHEMICAL TANK 2 | LEVEL SWITCH |  | 01 | 08 | 24VDC | DI | BB1LS701 | CHEMICAL TANK 2 | LEVEL SWITCH |  | LEVEL SWITCH | BB1LS701/01
BB1LS850 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-412_.L0 | RIO:01.DI:V+ BB1LS850 | RIO01:14.DI:00 BB1LS850 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 14 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS850 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | 01 | 01 | 24VDC | DI | BB1LS850 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | LEVEL SWITCH | BB1LS850/01
BB1LS851 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-413_.L0 | RIO:01.DI:V+ BB1LS851 | RIO01:15.DI:01 BB1LS851 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 15 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1LS851 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | 01 | 02 | 24VDC | DI | BB1LS851 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  | LEVEL SWITCH | BB1LS851/01
BB1LS852 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LS852 | FLY ASH CONTAINER | LEVEL SWITCH |  |  | #N/A |  | #N/A | BB1LS852 | FLY ASH CONTAINER | LEVEL SWITCH |  |  | BB1LS852/01
BB1LT001 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT001 | FEED WATER TANK LEVEL 1 |  |  |  | #N/A |  | #N/A | BB1LT001 | FEED WATER TANK LEVEL 1 |  |  |  | BB1LT001/01
BB1LT002 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT002 | FEED WATER TANK LEVEL 2 |  |  |  | #N/A |  | #N/A | BB1LT002 | FEED WATER TANK LEVEL 2 |  |  |  | BB1LT002/01
BB1LT003 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT003 | STEAM ACCUMULATOR LEVEL 1 |  |  |  | #N/A |  | #N/A | BB1LT003 | STEAM ACCUMULATOR LEVEL 1 |  |  |  | BB1LT003/01
BB1LT004 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT004 | STEAM ACCUMULATOR LEVEL 2 |  |  |  | #N/A |  | #N/A | BB1LT004 | STEAM ACCUMULATOR LEVEL 2 |  |  |  | BB1LT004/01
BB1LT101 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT101 | STEAM DRUM LEVEL 1 |  |  |  | #N/A |  | #N/A | BB1LT101 | STEAM DRUM LEVEL 1 |  |  |  | BB1LT101/01
BB1LT102 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT102 | STEAM DRUM LEVEL 2 |  |  |  | #N/A |  | #N/A | BB1LT102 | STEAM DRUM LEVEL 2 |  |  |  | BB1LT102/01
BB1LT103 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT103 | STEAM DRUM LEVEL 3 |  |  |  | #N/A |  | #N/A | BB1LT103 | STEAM DRUM LEVEL 3 |  |  |  | BB1LT103/01
BB1LT611 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT611 | UNLOADING STATION 1 LEVEL |  |  |  | #N/A |  | #N/A | BB1LT611 | UNLOADING STATION 1 LEVEL |  |  |  | BB1LT611/01
BB1LT612 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT612 | UNLOADING STATION 3 LEVEL |  |  |  | #N/A |  | #N/A | BB1LT612 | UNLOADING STATION 3 LEVEL |  |  |  | BB1LT612/01
BB1LT613 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT613 | UNLOADING STATION 2 LEVEL |  |  |  | #N/A |  | #N/A | BB1LT613 | UNLOADING STATION 2 LEVEL |  |  |  | BB1LT613/01
BB1LT650 | MEAS_ANA_240V |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT650 | FUEL SILO LEVEL RADAR 1 |  |  |  | #N/A |  | #N/A | BB1LT650 | FUEL SILO LEVEL RADAR 1 |  |  |  | BB1LT650/01
BB1LT651 | MEAS_ANA_240V |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT651 | FUEL SILO LEVEL RADAR 2 |  |  |  | #N/A |  | #N/A | BB1LT651 | FUEL SILO LEVEL RADAR 2 |  |  |  | BB1LT651/01
BB1LT652 | MEAS_ANA_240V |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT652 | FUEL POCKET LEVEL |  |  |  | #N/A |  | #N/A | BB1LT652 | FUEL POCKET LEVEL |  |  |  | BB1LT652/01
BB1LT800 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT800 | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  |  | #N/A |  | #N/A | BB1LT800 | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  |  | BB1LT800/01
BB1LT802 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1LT802 | SAND SILO LEVEL | MEASUREMENT |  |  | #N/A |  | #N/A | BB1LT802 | SAND SILO LEVEL | MEASUREMENT |  |  | BB1LT802/01
BB1PS600 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-414_.L0 | RIO:01.DI:V+ BB1PS600 | RIO01:15.DI:02 BB1PS600 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 15 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1PS600 | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | 01 | 03 | 24VDC | DI | BB1PS600 | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  | PRESSURE SWITCH | BB1PS600/01
BB1PS601 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-415_.L0 | RIO:01.DI:V+ BB1PS601 | RIO01:15.DI:03 BB1PS601 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 15 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1PS601 | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | 01 | 04 | 24VDC | DI | BB1PS601 | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  | PRESSURE SWITCH | BB1PS601/01
BB1PS602 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-416_.L0 | RIO:01.DI:V+ BB1PS602 | RIO01:15.DI:04 BB1PS602 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 15 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1PS602 | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | 01 | 05 | 24VDC | DI | BB1PS602 | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  | PRESSURE SWITCH | BB1PS602/01
BB1PS603 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-417_.L0 | RIO:01.DI:V+ BB1PS603 | RIO01:15.DI:05 BB1PS603 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 15 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1PS603 | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | 01 | 06 | 24VDC | DI | BB1PS603 | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH | PRESSURE SWITCH | BB1PS603/01
BB1PS604 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-418_.L0 | RIO:01.DI:V+ BB1PS604 | RIO01:15.DI:06 BB1PS604 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 15 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1PS604 | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | 01 | 07 | 24VDC | DI | BB1PS604 | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH | PRESSURE SWITCH | BB1PS604/01
BB1PS605 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-419_.L0 | RIO:01.DI:V+ BB1PS605 | RIO01:15.DI:07 BB1PS605 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 15 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1PS605 | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | 01 | 08 | 24VDC | DI | BB1PS605 | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH | PRESSURE SWITCH | BB1PS605/01
BB1PT001 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT001 | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  |  | #N/A |  | #N/A | BB1PT001 | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  |  | BB1PT001/01
BB1PT002 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT002 | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  |  | #N/A |  | #N/A | BB1PT002 | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  |  | BB1PT002/01
BB1PT004 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT004 | FEED WATER PRESSURE | BEFORE VALVE |  |  | #N/A |  | #N/A | BB1PT004 | FEED WATER PRESSURE | BEFORE VALVE |  |  | BB1PT004/01
BB1PT005 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT005 | FEED WATER PRESSURE | AFTER VALVE |  |  | #N/A |  | #N/A | BB1PT005 | FEED WATER PRESSURE | AFTER VALVE |  |  | BB1PT005/01
BB1PT006 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT006 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  |  | #N/A |  | #N/A | BB1PT006 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  |  | BB1PT006/01
BB1PT007 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT007 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  |  | #N/A |  | #N/A | BB1PT007 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  |  | BB1PT007/01
BB1PT009 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT009 | COOLING WATER PRESSURE | BEFORE PUMP |  |  | #N/A |  | #N/A | BB1PT009 | COOLING WATER PRESSURE | BEFORE PUMP |  |  | BB1PT009/01
BB1PT200 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT200 | FEED WATER TANK PRESSURE |  |  |  | #N/A |  | #N/A | BB1PT200 | FEED WATER TANK PRESSURE |  |  |  | BB1PT200/01
BB1PT201 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT201 | STEAM DRUM PRESSURE 1 |  |  |  | #N/A |  | #N/A | BB1PT201 | STEAM DRUM PRESSURE 1 |  |  |  | BB1PT201/01
BB1PT203 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT203 | STEAM DRUM PRESSURE 2 |  |  |  | #N/A |  | #N/A | BB1PT203 | STEAM DRUM PRESSURE 2 |  |  |  | BB1PT203/01
BB1PT204 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT204 | MAIN STEAM PRESSURE |  |  |  | #N/A |  | #N/A | BB1PT204 | MAIN STEAM PRESSURE |  |  |  | BB1PT204/01
BB1PT205 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT205 | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  |  | #N/A |  | #N/A | BB1PT205 | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  |  | BB1PT205/01
BB1PT207 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT207 | ACCUMULATOR PRESSURE |  |  |  | #N/A |  | #N/A | BB1PT207 | ACCUMULATOR PRESSURE |  |  |  | BB1PT207/01
BB1PT208 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT208 | ACCUMULATOR PRESSURE |  |  |  | #N/A |  | #N/A | BB1PT208 | ACCUMULATOR PRESSURE |  |  |  | BB1PT208/01
BB1PT400 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT400 | PRIMARY AIR PRESSURE |  |  |  | #N/A |  | #N/A | BB1PT400 | PRIMARY AIR PRESSURE |  |  |  | BB1PT400/01
BB1PT401 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT401 | SECONDARY AIR PRESSURE |  |  |  | #N/A |  | #N/A | BB1PT401 | SECONDARY AIR PRESSURE |  |  |  | BB1PT401/01
BB1PT402 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT402 | INSTRUMENT AIR PRESSURE | AFTER DRYER |  |  | #N/A |  | #N/A | BB1PT402 | INSTRUMENT AIR PRESSURE | AFTER DRYER |  |  | BB1PT402/01
BB1PT403 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT403 | SECONDARY AIR PRESSURE | INNER BACK WALL |  |  | #N/A |  | #N/A | BB1PT403 | SECONDARY AIR PRESSURE | INNER BACK WALL |  |  | BB1PT403/01
BB1PT404 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT404 | BOILER UPPER PART | PRESSURE 1 |  |  | #N/A |  | #N/A | BB1PT404 | BOILER UPPER PART | PRESSURE 1 |  |  | BB1PT404/01
BB1PT405 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT405 | BOILER UPPER PART | PRESSURE 2 |  |  | #N/A |  | #N/A | BB1PT405 | BOILER UPPER PART | PRESSURE 2 |  |  | BB1PT405/01
BB1PT406 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT406 | BOILER UPPER PART | PRESSURE |  |  | #N/A |  | #N/A | BB1PT406 | BOILER UPPER PART | PRESSURE |  |  | BB1PT406/01
BB1PT407 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT407 | TERTIARY AIR PRESSURE | RIGHT WALL |  |  | #N/A |  | #N/A | BB1PT407 | TERTIARY AIR PRESSURE | RIGHT WALL |  |  | BB1PT407/01
BB1PT408 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT408 | TERTIARY AIR PRESSURE | LEFT WALL |  |  | #N/A |  | #N/A | BB1PT408 | TERTIARY AIR PRESSURE | LEFT WALL |  |  | BB1PT408/01
BB1PT409 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT409 | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  |  | #N/A |  | #N/A | BB1PT409 | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  |  | BB1PT409/01
BB1PT410 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT410 | SECONDARY AIR PRESSURE | INNER FRONT WALL |  |  | #N/A |  | #N/A | BB1PT410 | SECONDARY AIR PRESSURE | INNER FRONT WALL |  |  | BB1PT410/01
BB1PT411 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT411 | SECONDARY AIR PRESSURE | OUTER BACK WALL |  |  | #N/A |  | #N/A | BB1PT411 | SECONDARY AIR PRESSURE | OUTER BACK WALL |  |  | BB1PT411/01
BB1PT478 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT478 | INSTRUMENT AIR PRESSURE |  |  |  | #N/A |  | #N/A | BB1PT478 | INSTRUMENT AIR PRESSURE |  |  |  | BB1PT478/01
BB1PT550 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT550 | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  |  | #N/A |  | #N/A | BB1PT550 | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  |  | BB1PT550/01
BB1PT552 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT552 | ESP INLET PRESSURE | TRANSMITTER |  |  | #N/A |  | #N/A | BB1PT552 | ESP INLET PRESSURE | TRANSMITTER |  |  | BB1PT552/01
BB1PT553 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT553 | ESP OUTLET PRESSURE | TRANSMITTER |  |  | #N/A |  | #N/A | BB1PT553 | ESP OUTLET PRESSURE | TRANSMITTER |  |  | BB1PT553/01
BB1PT800 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PT800 | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  |  | #N/A |  | #N/A | BB1PT800 | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  |  | BB1PT800/01
BB1PU800 | CHEMICAL_PUMP |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PU800 | CHEMICAL DOSING PUMP 1 |  |  |  | #N/A |  | #N/A | BB1PU800 | CHEMICAL DOSING PUMP 1 |  |  |  | BB1PU800/01
BB1PU801 | CHEMICAL_PUMP |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1PU801 | CHEMICAL DOSING PUMP 2 |  |  |  | #N/A |  | #N/A | BB1PU801 | CHEMICAL DOSING PUMP 2 |  |  |  | BB1PU801/01
BB1QT001 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT001 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  |  | #N/A |  | #N/A | BB1QT001 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  |  | BB1QT001/01
BB1QT002 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT002 | PH MEASUREMENT FROM FEED | WATER TANK |  |  | #N/A |  | #N/A | BB1QT002 | PH MEASUREMENT FROM FEED | WATER TANK |  |  | BB1QT002/01
BB1QT003 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT003 | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  |  | #N/A |  | #N/A | BB1QT003 | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  |  | BB1QT003/01
BB1QT004 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT004 | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  |  | #N/A |  | #N/A | BB1QT004 | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  |  | BB1QT004/01
BB1QT005 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT005 | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  |  | #N/A |  | #N/A | BB1QT005 | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  |  | BB1QT005/01
BB1QT006 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT006 | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  |  | #N/A |  | #N/A | BB1QT006 | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  |  | BB1QT006/01
BB1QT007 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT007 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  |  | #N/A |  | #N/A | BB1QT007 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  |  | BB1QT007/01
BB1QT550 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT550 | FLUEGAS OXYGEN | MEASUREMENT 1 |  |  | #N/A |  | #N/A | BB1QT550 | FLUEGAS OXYGEN | MEASUREMENT 1 |  |  | BB1QT550/01
BB1QT551 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT551 | FLUEGAS OXYGEN | MEASUREMENT 2 |  |  | #N/A |  | #N/A | BB1QT551 | FLUEGAS OXYGEN | MEASUREMENT 2 |  |  | BB1QT551/01
BB1QT552 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT552 | FLUEGAS CO MEASUREMENT |  |  |  | #N/A |  | #N/A | BB1QT552 | FLUEGAS CO MEASUREMENT |  |  |  | BB1QT552/01
BB1QT553 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT553 | BOILER ROOM GAS DETECTOR |  |  |  | #N/A |  | #N/A | BB1QT553 | BOILER ROOM GAS DETECTOR |  |  |  | BB1QT553/01
BB1QT554 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1QT554 | OPACITY AFTER ESP |  |  |  | #N/A |  | #N/A | BB1QT554 | OPACITY AFTER ESP |  |  |  | BB1QT554/01
BB1SI400 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI400 | PRIMARY AIR FAN | SAFETY INTERLOCK |  |  | #N/A |  | #N/A | BB1SI400 | PRIMARY AIR FAN | SAFETY INTERLOCK |  |  | BB1SI400/01
BB1SI401 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI401 | SECONDARY AIR FAN | SAFETY INTERLOCK |  |  | #N/A |  | #N/A | BB1SI401 | SECONDARY AIR FAN | SAFETY INTERLOCK |  |  | BB1SI401/01
BB1SI550 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI550 | FLUE GAS FAN | SAFETY INTERLOCK |  |  | #N/A |  | #N/A | BB1SI550 | FLUE GAS FAN | SAFETY INTERLOCK |  |  | BB1SI550/01
BB1SI603 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI603 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK |  | #N/A |  | #N/A | BB1SI603 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK |  | BB1SI603/01
BB1SI604 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI604 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK |  | #N/A |  | #N/A | BB1SI604 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK |  | BB1SI604/01
BB1SI605 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI605 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK |  | #N/A |  | #N/A | BB1SI605 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK |  | BB1SI605/01
BB1SI658 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI658 | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  |  | #N/A |  | #N/A | BB1SI658 | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  |  | BB1SI658/01
BB1SI659 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI659 | BELT CONVEYOR | SAFETY INTERLOCK |  |  | #N/A |  | #N/A | BB1SI659 | BELT CONVEYOR | SAFETY INTERLOCK |  |  | BB1SI659/01
BB1SI672 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI672 | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  |  | #N/A |  | #N/A | BB1SI672 | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  |  | BB1SI672/01
BB1SI675 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI675 | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  |  | #N/A |  | #N/A | BB1SI675 | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  |  | BB1SI675/01
BB1SI676 | FAN_SRS_DO |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SI676 | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  |  | #N/A |  | #N/A | BB1SI676 | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  |  | BB1SI676/01
BB1ST649 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-420_.L0 | RIO:01.DI:V+ BB1ST649 | RIO01:15.DI:00 BB1ST649 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 15 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST649 | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | 01 | 01 | 24VDC | DI | BB1ST649 | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  | SPEED SWITCH | BB1ST649/01
BB1ST650 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-421_.L0 | RIO:01.DI:V+ BB1ST650 | RIO01:16.DI:01 BB1ST650 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 16 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST650 | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | 01 | 02 | 24VDC | DI | BB1ST650 | SCRAPER CONVEYOR 1, | ROTATION GUARD |  | SPEED SWITCH | BB1ST650/01
BB1ST651 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-422_.L0 | RIO:01.DI:V+ BB1ST651 | RIO01:16.DI:02 BB1ST651 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 16 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST651 | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | 01 | 03 | 24VDC | DI | BB1ST651 | SCRAPER CONVEYOR 2, | ROTATION GUARD |  | SPEED SWITCH | BB1ST651/01
BB1ST652 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-423_.L0 | RIO:01.DI:V+ BB1ST652 | RIO01:16.DI:03 BB1ST652 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 16 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST652 | BELT CONVEYOR | ROTATION GUARD |  | 01 | 04 | 24VDC | DI | BB1ST652 | BELT CONVEYOR | ROTATION GUARD |  | SPEED SWITCH | BB1ST652/01
BB1ST653 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-424_.L0 | RIO:01.DI:V+ BB1ST653 | RIO01:16.DI:04 BB1ST653 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 16 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST653 | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | 01 | 05 | 24VDC | DI | BB1ST653 | FUEL FEEDING SCREW 2 | ROTATION GUARD |  | SPEED SWITCH | BB1ST653/01
BB1ST654 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-425_.L0 | RIO:01.DI:V+ BB1ST654 | RIO01:16.DI:05 BB1ST654 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 16 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST654 | BELT MAGNET | ROTATION GUARD |  | 01 | 06 | 24VDC | DI | BB1ST654 | BELT MAGNET | ROTATION GUARD |  | SPEED SWITCH | BB1ST654/01
BB1ST655 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-426_.L0 | RIO:01.DI:V+ BB1ST655 | RIO01:16.DI:06 BB1ST655 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 16 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST655 | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | 01 | 07 | 24VDC | DI | BB1ST655 | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  | SPEED SWITCH | BB1ST655/01
BB1ST656 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-427_.L0 | RIO:01.DI:V+ BB1ST656 | RIO01:16.DI:07 BB1ST656 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 16 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST656 | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | 01 | 08 | 24VDC | DI | BB1ST656 | DISC SCREEN DRIVE 1 | ROTATION GUARD |  | SPEED SWITCH | BB1ST656/01
BB1ST657 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-428_.L0 | RIO:01.DI:V+ BB1ST657 | RIO01:16.DI:00 BB1ST657 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 16 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST657 | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | 01 | 01 | 24VDC | DI | BB1ST657 | DISC SCREEN DRIVE 2 | ROTATION GUARD |  | SPEED SWITCH | BB1ST657/01
BB1ST659 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-429_.L0 | RIO:01.DI:V+ BB1ST659 | RIO01:17.DI:01 BB1ST659 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 17 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST659 | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | 01 | 02 | 24VDC | DI | BB1ST659 | FUEL FEEDING SCREW 1 | ROTATION GUARD |  | SPEED SWITCH | BB1ST659/01
BB1ST673 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-430_.L0 | RIO:01.DI:V+ BB1ST673 | RIO01:17.DI:02 BB1ST673 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 17 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST673 | LEVELING ROLLER 1 | SPEED SWITCH |  | 01 | 03 | 24VDC | DI | BB1ST673 | LEVELING ROLLER 1 | SPEED SWITCH |  | SPEED SWITCH | BB1ST673/01
BB1ST674 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-431_.L0 | RIO:01.DI:V+ BB1ST674 | RIO01:17.DI:03 BB1ST674 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 17 | 03 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST674 | LEVELING ROLLER 2 | SPEED SWITCH |  | 01 | 04 | 24VDC | DI | BB1ST674 | LEVELING ROLLER 2 | SPEED SWITCH |  | SPEED SWITCH | BB1ST674/01
BB1ST675 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-432_.L0 | RIO:01.DI:V+ BB1ST675 | RIO01:17.DI:04 BB1ST675 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 17 | 04 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST675 | LEVELING ROLLER 3 | SPEED SWITCH |  | 01 | 05 | 24VDC | DI | BB1ST675 | LEVELING ROLLER 3 | SPEED SWITCH |  | SPEED SWITCH | BB1ST675/01
BB1ST804 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1ST804 | ESP ROTARY VALVE | ROTATION GUARD |  |  | #N/A |  | #N/A | BB1ST804 | ESP ROTARY VALVE | ROTATION GUARD |  |  | BB1ST804/01
BB1ST805 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1ST805 | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  |  | #N/A |  | #N/A | BB1ST805 | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  |  | BB1ST805/01
BB1ST808 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1ST808 | ESP HOPPER 2 SCREW | ROTATION GUARD |  |  | #N/A |  | #N/A | BB1ST808 | ESP HOPPER 2 SCREW | ROTATION GUARD |  |  | BB1ST808/01
BB1ST809 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1ST809 | ESP HOPPER 1 SCREW | ROTATION GUARD |  |  | #N/A |  | #N/A | BB1ST809 | ESP HOPPER 1 SCREW | ROTATION GUARD |  |  | BB1ST809/01
BB1ST850 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-433_.L0 | RIO:01.DI:V+ BB1ST850 | RIO01:17.DI:05 BB1ST850 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 17 | 05 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST850 | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | 01 | 06 | 24VDC | DI | BB1ST850 | BOTTOM ASH CONVEYOR | ROTATION GUARD |  | SPEED SWITCH | BB1ST850/01
BB1ST852 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-434_.L0 | RIO:01.DI:V+ BB1ST852 | RIO01:17.DI:06 BB1ST852 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 17 | 06 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST852 | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 01 | 07 | 24VDC | DI | BB1ST852 | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | SPEED SWITCH | BB1ST852/01
BB1ST853 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-435_.L0 | RIO:01.DI:V+ BB1ST853 | RIO01:17.DI:07 BB1ST853 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 17 | 07 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST853 | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | 01 | 08 | 24VDC | DI | BB1ST853 | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  | SPEED SWITCH | BB1ST853/01
BB1ST856 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-436_.L0 | RIO:01.DI:V+ BB1ST856 | RIO01:17.DI:00 BB1ST856 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 17 | 00 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1ST856 | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | 01 | 01 | 24VDC | DI | BB1ST856 | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  | SPEED SWITCH | BB1ST856/01
BB1SV001 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV001 | BLOW DOWN TANK COOLING | ON/OFF VALVE |  |  | #N/A |  | #N/A | BB1SV001 | BLOW DOWN TANK COOLING | ON/OFF VALVE |  |  | BB1SV001/01
BB1SV400 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV400 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  |  | #N/A |  | #N/A | BB1SV400 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  |  | BB1SV400/01
BB1SV401 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV401 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  |  | #N/A |  | #N/A | BB1SV401 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  |  | BB1SV401/01
BB1SV402 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV402 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  |  | #N/A |  | #N/A | BB1SV402 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  |  | BB1SV402/01
BB1SV405 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV405 | SAND FILLING VALVE | SOLENOID VALVE |  |  | #N/A |  | #N/A | BB1SV405 | SAND FILLING VALVE | SOLENOID VALVE |  |  | BB1SV405/01
BB1SV406 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV406 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  |  | #N/A |  | #N/A | BB1SV406 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  |  | BB1SV406/01
BB1SV410 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV410 | FEED WATER TANK | OVERFLOW VALVE |  |  | #N/A |  | #N/A | BB1SV410 | FEED WATER TANK | OVERFLOW VALVE |  |  | BB1SV410/01
BB1SV601 | PUSH_FEED |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV601 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 |  | #N/A |  | #N/A | BB1SV601 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 |  | BB1SV601/01
BB1SV602 | PUSH_FEED |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV602 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 |  | #N/A |  | #N/A | BB1SV602 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 |  | BB1SV602/01
BB1SV603 | PUSH_FEED |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV603 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 |  | #N/A |  | #N/A | BB1SV603 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 |  | BB1SV603/01
BB1SV950 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV950 | FUEL SILO FIRE WATER | CONTROL VALVE |  |  | #N/A |  | #N/A | BB1SV950 | FUEL SILO FIRE WATER | CONTROL VALVE |  |  | BB1SV950/01
BB1SV951 | BIN_VLV |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1SV951 | FUEL POCKET FIRE WATER | CONTROL VALVE |  |  | #N/A |  | #N/A | BB1SV951 | FUEL POCKET FIRE WATER | CONTROL VALVE |  |  | BB1SV951/01
BB1TS501 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TS501 | ESP INSULATOR 1 | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TS501 | ESP INSULATOR 1 | TEMPERATURE |  |  | BB1TS501/01
BB1TS508 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TS508 | ESP INSULATOR 2 | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TS508 | ESP INSULATOR 2 | TEMPERATURE |  |  | BB1TS508/01
BB1TS600 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-437_.L0 | RIO:01.DI:V+ BB1TS600 | RIO01:18.DI:01 BB1TS600 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 18 | 01 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1TS600 | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | 01 | 02 | 24VDC | DI | BB1TS600 | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  | TEMPERATURE SWITCH | BB1TS600/01
BB1TS608 | MEAS_BIN | POINTIO_1DO_LOOP24VDC | 38025-ELE | 01-438_.L0 | RIO:01.DI:V+ BB1TS608 | RIO01:18.DI:02 BB1TS608 | KPA_FLOORX_IO | KPA NON ASSIGNED IO |  |  |  |  | RIO | 01 | 18 | 02 | 1734-IB8*1 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | BB1TS608 | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | 01 | 03 | 24VDC | DI | BB1TS608 | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  | TEMPERATURE SWITCH | BB1TS608/01
BB1TS804 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TS804 | ESP ROTARY VALVE | HEATING THERMOSTAT |  |  | #N/A |  | #N/A | BB1TS804 | ESP ROTARY VALVE | HEATING THERMOSTAT |  |  | BB1TS804/01
BB1TS805 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TS805 | ESP COLLECTION SCREW | HEATING THERMOSTAT |  |  | #N/A |  | #N/A | BB1TS805 | ESP COLLECTION SCREW | HEATING THERMOSTAT |  |  | BB1TS805/01
BB1TS808 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TS808 | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  |  | #N/A |  | #N/A | BB1TS808 | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  |  | BB1TS808/01
BB1TS809 | MEAS_BIN_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TS809 | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  |  | #N/A |  | #N/A | BB1TS809 | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  |  | BB1TS809/01
BB1TT001 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT001 | FEED WATER TEMPERATURE |  |  |  | #N/A |  | #N/A | BB1TT001 | FEED WATER TEMPERATURE |  |  |  | BB1TT001/01
BB1TT002 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT002 | FEED WATER PUMP 2 | BEARING TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT002 | FEED WATER PUMP 2 | BEARING TEMPERATURE |  |  | BB1TT002/01
BB1TT003 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT003 | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT003 | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  |  | BB1TT003/01
BB1TT004 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT004 | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT004 | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  |  | BB1TT004/01
BB1TT005 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT005 | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT005 | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  |  | BB1TT005/01
BB1TT006 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT006 | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  |  | #N/A |  | #N/A | BB1TT006 | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  |  | BB1TT006/01
BB1TT007 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT007 | ACCUMULATOR TEMPERATURE |  |  |  | #N/A |  | #N/A | BB1TT007 | ACCUMULATOR TEMPERATURE |  |  |  | BB1TT007/01
BB1TT008 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT008 | TEMPERATURE AFTER | ECONOMIZER |  |  | #N/A |  | #N/A | BB1TT008 | TEMPERATURE AFTER | ECONOMIZER |  |  | BB1TT008/01
BB1TT009 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT009 | TEMPERATURE BEFORE | ECONOMIZER |  |  | #N/A |  | #N/A | BB1TT009 | TEMPERATURE BEFORE | ECONOMIZER |  |  | BB1TT009/01
BB1TT012 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT012 | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R |  | #N/A |  | #N/A | BB1TT012 | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R |  | BB1TT012/01
BB1TT031 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT031 | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  |  | #N/A |  | #N/A | BB1TT031 | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  |  | BB1TT031/01
BB1TT116 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT116 | STEAM TEMPERATURE TO | AIR PREHEATER |  |  | #N/A |  | #N/A | BB1TT116 | STEAM TEMPERATURE TO | AIR PREHEATER |  |  | BB1TT116/01
BB1TT200 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT200 | MAIN STEAM TEMPERATURE |  |  |  | #N/A |  | #N/A | BB1TT200 | MAIN STEAM TEMPERATURE |  |  |  | BB1TT200/01
BB1TT201 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT201 | SOOTBLOWING | LINE TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT201 | SOOTBLOWING | LINE TEMPERATURE |  |  | BB1TT201/01
BB1TT202 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT202 | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  |  | #N/A |  | #N/A | BB1TT202 | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  |  | BB1TT202/01
BB1TT203 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT203 | 18BAR(G) STEAM | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT203 | 18BAR(G) STEAM | TEMPERATURE |  |  | BB1TT203/01
BB1TT308 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT308 | FURNACE TEMPERATURE | CONNECTION |  |  | #N/A |  | #N/A | BB1TT308 | FURNACE TEMPERATURE | CONNECTION |  |  | BB1TT308/01
BB1TT400 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT400 | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  |  | #N/A |  | #N/A | BB1TT400 | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  |  | BB1TT400/01
BB1TT401 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT401 | BOILER ROOM UPPER PART | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT401 | BOILER ROOM UPPER PART | TEMPERATURE |  |  | BB1TT401/01
BB1TT402 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT402 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT402 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  |  | BB1TT402/01
BB1TT403 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT403 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT403 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  |  | BB1TT403/01
BB1TT404 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT404 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT404 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | BB1TT404/01
BB1TT404 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT404 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT404 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | BB1TT404/01
BB1TT405 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT405 | PRIMARY AIR TEMPERATURE |  |  |  | #N/A |  | #N/A | BB1TT405 | PRIMARY AIR TEMPERATURE |  |  |  | BB1TT405/01
BB1TT405 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT405 | PRIMARY AIR TEMPERATURE |  |  |  | #N/A |  | #N/A | BB1TT405 | PRIMARY AIR TEMPERATURE |  |  |  | BB1TT405/01
BB1TT406 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT406 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT406 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  |  | BB1TT406/01
BB1TT406 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT406 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT406 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  |  | BB1TT406/01
BB1TT407 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT407 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT407 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  |  | BB1TT407/01
BB1TT407 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT407 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT407 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  |  | BB1TT407/01
BB1TT408 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT408 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT408 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | BB1TT408/01
BB1TT408 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT408 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT408 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | BB1TT408/01
BB1TT409 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT409 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT409 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | BB1TT409/01
BB1TT409 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT409 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT409 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | BB1TT409/01
BB1TT410 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT410 | BOILER 1ST DRAFT | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT410 | BOILER 1ST DRAFT | TEMPERATURE |  |  | BB1TT410/01
BB1TT410 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT410 | BOILER 1ST DRAFT | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT410 | BOILER 1ST DRAFT | TEMPERATURE |  |  | BB1TT410/01
BB1TT411 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT411 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  |  | #N/A |  | #N/A | BB1TT411 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  |  | BB1TT411/01
BB1TT411 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT411 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  |  | #N/A |  | #N/A | BB1TT411 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  |  | BB1TT411/01
BB1TT412 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT412 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  |  | #N/A |  | #N/A | BB1TT412 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  |  | BB1TT412/01
BB1TT412 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT412 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  |  | #N/A |  | #N/A | BB1TT412 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  |  | BB1TT412/01
BB1TT413 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT413 | BED TEMPERATURE 1 |  |  |  | #N/A |  | #N/A | BB1TT413 | BED TEMPERATURE 1 |  |  |  | BB1TT413/01
BB1TT413 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT413 | BED TEMPERATURE 1 |  |  |  | #N/A |  | #N/A | BB1TT413 | BED TEMPERATURE 1 |  |  |  | BB1TT413/01
BB1TT414 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT414 | BED TEMPERATURE 2 |  |  |  | #N/A |  | #N/A | BB1TT414 | BED TEMPERATURE 2 |  |  |  | BB1TT414/01
BB1TT414 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT414 | BED TEMPERATURE 2 |  |  |  | #N/A |  | #N/A | BB1TT414 | BED TEMPERATURE 2 |  |  |  | BB1TT414/01
BB1TT415 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT415 | BOILER BED TEMPERATURE | MIDDLE LEVEL |  |  | #N/A |  | #N/A | BB1TT415 | BOILER BED TEMPERATURE | MIDDLE LEVEL |  |  | BB1TT415/01
BB1TT415 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT415 | BOILER BED TEMPERATURE | MIDDLE LEVEL |  |  | #N/A |  | #N/A | BB1TT415 | BOILER BED TEMPERATURE | MIDDLE LEVEL |  |  | BB1TT415/01
BB1TT416 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT416 | BOILER BED TEMPERATURE | LOWER LEVEL |  |  | #N/A |  | #N/A | BB1TT416 | BOILER BED TEMPERATURE | LOWER LEVEL |  |  | BB1TT416/01
BB1TT416 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT416 | BOILER BED TEMPERATURE | LOWER LEVEL |  |  | #N/A |  | #N/A | BB1TT416 | BOILER BED TEMPERATURE | LOWER LEVEL |  |  | BB1TT416/01
BB1TT417 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT417 | BED TEMPERATURE 3 |  |  |  | #N/A |  | #N/A | BB1TT417 | BED TEMPERATURE 3 |  |  |  | BB1TT417/01
BB1TT417 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT417 | BED TEMPERATURE 3 |  |  |  | #N/A |  | #N/A | BB1TT417 | BED TEMPERATURE 3 |  |  |  | BB1TT417/01
BB1TT418 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT418 | BED TEMPERATURE 4 |  |  |  | #N/A |  | #N/A | BB1TT418 | BED TEMPERATURE 4 |  |  |  | BB1TT418/01
BB1TT418 | MEAS_ANA_SRS |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT418 | BED TEMPERATURE 4 |  |  |  | #N/A |  | #N/A | BB1TT418 | BED TEMPERATURE 4 |  |  |  | BB1TT418/01
BB1TT421 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT421 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | #N/A |  | #N/A | BB1TT421 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT421/01
BB1TT421 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT421 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | #N/A |  | #N/A | BB1TT421 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT421/01
BB1TT422 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT422 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | #N/A |  | #N/A | BB1TT422 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT422/01
BB1TT422 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT422 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | #N/A |  | #N/A | BB1TT422 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT422/01
BB1TT423 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT423 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT423 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | BB1TT423/01
BB1TT423 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT423 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT423 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | BB1TT423/01
BB1TT430 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT430 | INSTRUMENT AIR TANK | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT430 | INSTRUMENT AIR TANK | TEMPERATURE |  |  | BB1TT430/01
BB1TT430 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT430 | INSTRUMENT AIR TANK | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT430 | INSTRUMENT AIR TANK | TEMPERATURE |  |  | BB1TT430/01
BB1TT550 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT550 | FLUE GAS TEMPERATURE 1 |  |  |  | #N/A |  | #N/A | BB1TT550 | FLUE GAS TEMPERATURE 1 |  |  |  | BB1TT550/01
BB1TT550 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT550 | FLUE GAS TEMPERATURE 1 |  |  |  | #N/A |  | #N/A | BB1TT550 | FLUE GAS TEMPERATURE 1 |  |  |  | BB1TT550/01
BB1TT551 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT551 | FLUE GAS TEMPERATURE 2 |  |  |  | #N/A |  | #N/A | BB1TT551 | FLUE GAS TEMPERATURE 2 |  |  |  | BB1TT551/01
BB1TT551 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT551 | FLUE GAS TEMPERATURE 2 |  |  |  | #N/A |  | #N/A | BB1TT551 | FLUE GAS TEMPERATURE 2 |  |  |  | BB1TT551/01
BB1TT552 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT552 | FLUE GAS TEMPERATURE | BEFORE ESP |  |  | #N/A |  | #N/A | BB1TT552 | FLUE GAS TEMPERATURE | BEFORE ESP |  |  | BB1TT552/01
BB1TT552 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT552 | FLUE GAS TEMPERATURE | BEFORE ESP |  |  | #N/A |  | #N/A | BB1TT552 | FLUE GAS TEMPERATURE | BEFORE ESP |  |  | BB1TT552/01
BB1TT553 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT553 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT553 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  |  | BB1TT553/01
BB1TT553 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT553 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  |  | #N/A |  | #N/A | BB1TT553 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  |  | BB1TT553/01
BB1TT554 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT554 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT554 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | BB1TT554/01
BB1TT554 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT554 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT554 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | BB1TT554/01
BB1TT555 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT555 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT555 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | BB1TT555/01
BB1TT555 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT555 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT555 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | BB1TT555/01
BB1TT556 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT556 | FLUE GAS TEMPERATURE | BEFORE STACK |  |  | #N/A |  | #N/A | BB1TT556 | FLUE GAS TEMPERATURE | BEFORE STACK |  |  | BB1TT556/01
BB1TT556 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT556 | FLUE GAS TEMPERATURE | BEFORE STACK |  |  | #N/A |  | #N/A | BB1TT556 | FLUE GAS TEMPERATURE | BEFORE STACK |  |  | BB1TT556/01
BB1TT557 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT557 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT557 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  |  | BB1TT557/01
BB1TT557 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT557 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  |  | #N/A |  | #N/A | BB1TT557 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  |  | BB1TT557/01
BB1TT558 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT558 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  |  | #N/A |  | #N/A | BB1TT558 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT558/01
BB1TT558 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT558 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  |  | #N/A |  | #N/A | BB1TT558 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT558/01
BB1TT650 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT650 | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  |  | #N/A |  | #N/A | BB1TT650 | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  |  | BB1TT650/01
BB1TT650 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT650 | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  |  | #N/A |  | #N/A | BB1TT650 | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  |  | BB1TT650/01
BB1TT652 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT652 | FUEL SILO TEMPERATURE | MEASUREMENT |  |  | #N/A |  | #N/A | BB1TT652 | FUEL SILO TEMPERATURE | MEASUREMENT |  |  | BB1TT652/01
BB1TT652 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT652 | FUEL SILO TEMPERATURE | MEASUREMENT |  |  | #N/A |  | #N/A | BB1TT652 | FUEL SILO TEMPERATURE | MEASUREMENT |  |  | BB1TT652/01
BB1TT653 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT653 | FUEL POCKET TEMPERATURE |  |  |  | #N/A |  | #N/A | BB1TT653 | FUEL POCKET TEMPERATURE |  |  |  | BB1TT653/01
BB1TT653 | MEAS_ANA |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT653 | FUEL POCKET TEMPERATURE |  |  |  | #N/A |  | #N/A | BB1TT653 | FUEL POCKET TEMPERATURE |  |  |  | BB1TT653/01
BB1TT850 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT850 | ESP ASH HOPPER 1 | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT850 | ESP ASH HOPPER 1 | TEMPERATURE |  |  | BB1TT850/01
BB1TT850 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT850 | ESP ASH HOPPER 1 | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT850 | ESP ASH HOPPER 1 | TEMPERATURE |  |  | BB1TT850/01
BB1TT851 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT851 | ESP ASH HOPPER 2 | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT851 | ESP ASH HOPPER 2 | TEMPERATURE |  |  | BB1TT851/01
BB1TT851 | MEAS_ANA_DETAIL |  | #N/A | #N/A |  |  |  | #N/A |  |  |  |  | #N/A |  | #N/A |  |  |  |  | BB1TT851 | ESP ASH HOPPER 2 | TEMPERATURE |  |  | #N/A |  | #N/A | BB1TT851 | ESP ASH HOPPER 2 | TEMPERATURE |  |  | BB1TT851/01

## PROTOTYPE_FIELDS
Default values for prototypes. Blank fields will not be included when given prototype dbf is generated. Values containing "@" will receive tag-specific values
Field | POINTIO_1DO_LOOP24VDC | ALM_HORN2
DWGPREFIX | ##DWGPREFIX##
DWGNUMBER | ##DWGNUMBER##
PROTOTYPE | S:\Elecdes\prototypes\v6\INSTRUMENTATION\POINTIO_1DO_LOOP24VDC
W1NAME | ##W1NAME##
W2NAME | ##W2NAME##
X1NAME | ##X1NAME##
X1DESC | ##X1DESC##
X1VDC24
X1VDC0
X1XIO
X1XIOFI
P1NAME | ##P1NAME##
P1RACK | ##P1RACK##
P1SLOT | ##P1SLOT##
P1CHAN | ##P1CHAN##
P1MFG | 2
P1CATN | ##P1CATN##
P1CATD | ##P1CATD##
P1CATD2 | ##P1CATD2##
P1TAG | ##P1TAG##
P1DESC2 | ##P1DESC2##
P1DESC3 | ##P1DESC3##
P1DESC4 | ##P1DESC4##
P1T1 | ##P1T1##
P1T2 | ##P1T2##
P1T1TYPE | ##P1T1TYPE##
P1T2TYPE | ##P1T2TYPE##
D1TAG | ##D1TAG##
D1DESC2 | ##D1DESC2##
D1DESC3 | ##D1DESC3##
D1DESC4 | ##D1DESC4##
D1TYPE | ##D1TYPE##
D1T1 | +
D1T2 | -
C1CATN | 0P-2C-F-1
C1CATD | PVC 2 Core Flex 1mm^2
C1TAG | ##C1TAG##
C1COR1 | BN
C1COR2 | BU

## Z_DRAWING
Tag Info | Drawing Filename
Tag | Type | Prefix | SubProject | Base | Index | Number | Suffix | Short_Desc_1
<004> | ELE | 38025-ELE | 1 | 300 | 0 | 300 | 01-300_.L0 | #REF!
BB1FS003 | ELE | 38025-ELE | 1 | 300 | 1 | 301 | 01-301_.L0 | #REF!
BB1GS001 | ELE | 38025-ELE | 1 | 300 | 2 | 302 | 01-302_.L0 | #REF!
BB1GS002 | ELE | 38025-ELE | 1 | 300 | 3 | 303 | 01-303_.L0 | #REF!
BB1GS003 | ELE | 38025-ELE | 1 | 300 | 4 | 304 | 01-304_.L0 | #REF!
BB1GS004 | ELE | 38025-ELE | 1 | 300 | 5 | 305 | 01-305_.L0 | #REF!
BB1GS005 | ELE | 38025-ELE | 1 | 300 | 6 | 306 | 01-306_.L0 | #REF!
BB1GS006 | ELE | 38025-ELE | 1 | 300 | 7 | 307 | 01-307_.L0 | #REF!
BB1GS007 | ELE | 38025-ELE | 1 | 300 | 8 | 308 | 01-308_.L0 | #REF!
BB1GS008 | ELE | 38025-ELE | 1 | 300 | 9 | 309 | 01-309_.L0 | #REF!
BB1GS009 | ELE | 38025-ELE | 1 | 300 | 10 | 310 | 01-310_.L0 | #REF!
BB1GS010 | ELE | 38025-ELE | 1 | 300 | 11 | 311 | 01-311_.L0 | #REF!
BB1GS011 | ELE | 38025-ELE | 1 | 300 | 12 | 312 | 01-312_.L0 | #REF!
BB1GS012 | ELE | 38025-ELE | 1 | 300 | 13 | 313 | 01-313_.L0 | #REF!
BB1GS020 | ELE | 38025-ELE | 1 | 300 | 14 | 314 | 01-314_.L0 | #REF!
BB1GS200 | ELE | 38025-ELE | 1 | 300 | 15 | 315 | 01-315_.L0 | #REF!
BB1GS201 | ELE | 38025-ELE | 1 | 300 | 16 | 316 | 01-316_.L0 | #REF!
BB1GS203 | ELE | 38025-ELE | 1 | 300 | 17 | 317 | 01-317_.L0 | #REF!
BB1GS204 | ELE | 38025-ELE | 1 | 300 | 18 | 318 | 01-318_.L0 | #REF!
BB1GS205 | ELE | 38025-ELE | 1 | 300 | 19 | 319 | 01-319_.L0 | #REF!
BB1GS206 | ELE | 38025-ELE | 1 | 300 | 20 | 320 | 01-320_.L0 | #REF!
BB1GS207 | ELE | 38025-ELE | 1 | 300 | 21 | 321 | 01-321_.L0 | #REF!
BB1GS208 | ELE | 38025-ELE | 1 | 300 | 22 | 322 | 01-322_.L0 | #REF!
BB1GS209 | ELE | 38025-ELE | 1 | 300 | 23 | 323 | 01-323_.L0 | #REF!
BB1GS210 | ELE | 38025-ELE | 1 | 300 | 24 | 324 | 01-324_.L0 | #REF!
BB1GS211 | ELE | 38025-ELE | 1 | 300 | 25 | 325 | 01-325_.L0 | #REF!
BB1GS212 | ELE | 38025-ELE | 1 | 300 | 26 | 326 | 01-326_.L0 | #REF!
BB1GS213 | ELE | 38025-ELE | 1 | 300 | 27 | 327 | 01-327_.L0 | #REF!
BB1GS214 | ELE | 38025-ELE | 1 | 300 | 28 | 328 | 01-328_.L0 | #REF!
BB1GS215 | ELE | 38025-ELE | 1 | 300 | 29 | 329 | 01-329_.L0 | #REF!
BB1GS216 | ELE | 38025-ELE | 1 | 300 | 30 | 330 | 01-330_.L0 | #REF!
BB1GS217 | ELE | 38025-ELE | 1 | 300 | 31 | 331 | 01-331_.L0 | #REF!
BB1GS218 | ELE | 38025-ELE | 1 | 300 | 32 | 332 | 01-332_.L0 | #REF!
BB1GS219 | ELE | 38025-ELE | 1 | 300 | 33 | 333 | 01-333_.L0 | #REF!
BB1GS220 | ELE | 38025-ELE | 1 | 300 | 34 | 334 | 01-334_.L0 | #REF!
BB1GS221 | ELE | 38025-ELE | 1 | 300 | 35 | 335 | 01-335_.L0 | #REF!
BB1GS222 | ELE | 38025-ELE | 1 | 300 | 36 | 336 | 01-336_.L0 | #REF!
BB1GS223 | ELE | 38025-ELE | 1 | 300 | 37 | 337 | 01-337_.L0 | #REF!
BB1GS224 | ELE | 38025-ELE | 1 | 300 | 38 | 338 | 01-338_.L0 | #REF!
BB1GS225 | ELE | 38025-ELE | 1 | 300 | 39 | 339 | 01-339_.L0 | #REF!
BB1GS226 | ELE | 38025-ELE | 1 | 300 | 40 | 340 | 01-340_.L0 | #REF!
BB1GS227 | ELE | 38025-ELE | 1 | 300 | 41 | 341 | 01-341_.L0 | #REF!
BB1GS228 | ELE | 38025-ELE | 1 | 300 | 42 | 342 | 01-342_.L0 | #REF!
BB1GS230 | ELE | 38025-ELE | 1 | 300 | 43 | 343 | 01-343_.L0 | #REF!
BB1GS231 | ELE | 38025-ELE | 1 | 300 | 44 | 344 | 01-344_.L0 | #REF!
BB1GS232 | ELE | 38025-ELE | 1 | 300 | 45 | 345 | 01-345_.L0 | #REF!
BB1GS233 | ELE | 38025-ELE | 1 | 300 | 46 | 346 | 01-346_.L0 | #REF!
BB1GS600 | ELE | 38025-ELE | 1 | 300 | 47 | 347 | 01-347_.L0 | #REF!
BB1GS601 | ELE | 38025-ELE | 1 | 300 | 48 | 348 | 01-348_.L0 | #REF!
BB1GS602 | ELE | 38025-ELE | 1 | 300 | 49 | 349 | 01-349_.L0 | #REF!
BB1GS603 | ELE | 38025-ELE | 1 | 300 | 50 | 350 | 01-350_.L0 | #REF!
BB1GS604 | ELE | 38025-ELE | 1 | 300 | 51 | 351 | 01-351_.L0 | #REF!
BB1GS605 | ELE | 38025-ELE | 1 | 300 | 52 | 352 | 01-352_.L0 | #REF!
BB1GS606 | ELE | 38025-ELE | 1 | 300 | 53 | 353 | 01-353_.L0 | #REF!
BB1GS607 | ELE | 38025-ELE | 1 | 300 | 54 | 354 | 01-354_.L0 | #REF!
BB1GS608 | ELE | 38025-ELE | 1 | 300 | 55 | 355 | 01-355_.L0 | #REF!
BB1GS609 | ELE | 38025-ELE | 1 | 300 | 56 | 356 | 01-356_.L0 | #REF!
BB1GS610 | ELE | 38025-ELE | 1 | 300 | 57 | 357 | 01-357_.L0 | #REF!
BB1GS611 | ELE | 38025-ELE | 1 | 300 | 58 | 358 | 01-358_.L0 | #REF!
BB1GS612 | ELE | 38025-ELE | 1 | 300 | 59 | 359 | 01-359_.L0 | #REF!
BB1GS613 | ELE | 38025-ELE | 1 | 300 | 60 | 360 | 01-360_.L0 | #REF!
BB1GS614 | ELE | 38025-ELE | 1 | 300 | 61 | 361 | 01-361_.L0 | #REF!
BB1GS615 | ELE | 38025-ELE | 1 | 300 | 62 | 362 | 01-362_.L0 | #REF!
BB1GS616 | ELE | 38025-ELE | 1 | 300 | 63 | 363 | 01-363_.L0 | #REF!
BB1GS617 | ELE | 38025-ELE | 1 | 300 | 64 | 364 | 01-364_.L0 | #REF!
BB1GS618 | ELE | 38025-ELE | 1 | 300 | 65 | 365 | 01-365_.L0 | #REF!
BB1GS619 | ELE | 38025-ELE | 1 | 300 | 66 | 366 | 01-366_.L0 | #REF!
BB1GS620 | ELE | 38025-ELE | 1 | 300 | 67 | 367 | 01-367_.L0 | #REF!
BB1GS621 | ELE | 38025-ELE | 1 | 300 | 68 | 368 | 01-368_.L0 | #REF!
BB1GS622 | ELE | 38025-ELE | 1 | 300 | 69 | 369 | 01-369_.L0 | #REF!
BB1GS623 | ELE | 38025-ELE | 1 | 300 | 70 | 370 | 01-370_.L0 | #REF!
BB1GS650 | ELE | 38025-ELE | 1 | 300 | 71 | 371 | 01-371_.L0 | #REF!
BB1GS651 | ELE | 38025-ELE | 1 | 300 | 72 | 372 | 01-372_.L0 | #REF!
BB1GS652 | ELE | 38025-ELE | 1 | 300 | 73 | 373 | 01-373_.L0 | #REF!
BB1GS653 | ELE | 38025-ELE | 1 | 300 | 74 | 374 | 01-374_.L0 | #REF!
BB1GS654 | ELE | 38025-ELE | 1 | 300 | 75 | 375 | 01-375_.L0 | #REF!
BB1GS655 | ELE | 38025-ELE | 1 | 300 | 76 | 376 | 01-376_.L0 | #REF!
BB1GS656 | ELE | 38025-ELE | 1 | 300 | 77 | 377 | 01-377_.L0 | #REF!
BB1GS659 | ELE | 38025-ELE | 1 | 300 | 78 | 378 | 01-378_.L0 | #REF!
BB1GS660 | ELE | 38025-ELE | 1 | 300 | 79 | 379 | 01-379_.L0 | #REF!
BB1GS661 | ELE | 38025-ELE | 1 | 300 | 80 | 380 | 01-380_.L0 | #REF!
BB1GS662 | ELE | 38025-ELE | 1 | 300 | 81 | 381 | 01-381_.L0 | #REF!
BB1GS663 | ELE | 38025-ELE | 1 | 300 | 82 | 382 | 01-382_.L0 | #REF!
BB1GS800 | ELE | 38025-ELE | 1 | 300 | 83 | 383 | 01-383_.L0 | #REF!
BB1GS801 | ELE | 38025-ELE | 1 | 300 | 84 | 384 | 01-384_.L0 | #REF!
BB1GS802 | ELE | 38025-ELE | 1 | 300 | 85 | 385 | 01-385_.L0 | #REF!
BB1GS803 | ELE | 38025-ELE | 1 | 300 | 86 | 386 | 01-386_.L0 | #REF!
BB1GS850 | ELE | 38025-ELE | 1 | 300 | 87 | 387 | 01-387_.L0 | #REF!
BB1GS851 | ELE | 38025-ELE | 1 | 300 | 88 | 388 | 01-388_.L0 | #REF!
BB1GS852 | ELE | 38025-ELE | 1 | 300 | 89 | 389 | 01-389_.L0 | #REF!
BB1GS853 | ELE | 38025-ELE | 1 | 300 | 90 | 390 | 01-390_.L0 | #REF!
BB1GS854 | ELE | 38025-ELE | 1 | 300 | 91 | 391 | 01-391_.L0 | #REF!
BB1GS855 | ELE | 38025-ELE | 1 | 300 | 92 | 392 | 01-392_.L0 | #REF!
BB1GS856 | ELE | 38025-ELE | 1 | 300 | 93 | 393 | 01-393_.L0 | #REF!
BB1GS857 | ELE | 38025-ELE | 1 | 300 | 94 | 394 | 01-394_.L0 | #REF!
BB1GS858 | ELE | 38025-ELE | 1 | 300 | 95 | 395 | 01-395_.L0 | #REF!
BB1LS600 | ELE | 38025-ELE | 1 | 300 | 96 | 396 | 01-396_.L0 | #REF!
BB1LS608 | ELE | 38025-ELE | 1 | 300 | 97 | 397 | 01-397_.L0 | #REF!
BB1LS650 | ELE | 38025-ELE | 1 | 300 | 98 | 398 | 01-398_.L0 | #REF!
BB1LS651 | ELE | 38025-ELE | 1 | 300 | 99 | 399 | 01-399_.L0 | #REF!
BB1LS652 | ELE | 38025-ELE | 1 | 300 | 100 | 400 | 01-400_.L0 | #REF!
BB1LS653 | ELE | 38025-ELE | 1 | 300 | 101 | 401 | 01-401_.L0 | #REF!
BB1LS654 | ELE | 38025-ELE | 1 | 300 | 102 | 402 | 01-402_.L0 | #REF!
BB1LS655 | ELE | 38025-ELE | 1 | 300 | 103 | 403 | 01-403_.L0 | #REF!
BB1LS656 | ELE | 38025-ELE | 1 | 300 | 104 | 404 | 01-404_.L0 | #REF!
BB1LS657 | ELE | 38025-ELE | 1 | 300 | 105 | 405 | 01-405_.L0 | #REF!
BB1LS658 | ELE | 38025-ELE | 1 | 300 | 106 | 406 | 01-406_.L0 | #REF!
BB1LS659 | ELE | 38025-ELE | 1 | 300 | 107 | 407 | 01-407_.L0 | #REF!
BB1LS660 | ELE | 38025-ELE | 1 | 300 | 108 | 408 | 01-408_.L0 | #REF!
BB1LS661 | ELE | 38025-ELE | 1 | 300 | 109 | 409 | 01-409_.L0 | #REF!
BB1LS700 | ELE | 38025-ELE | 1 | 300 | 110 | 410 | 01-410_.L0 | #REF!
BB1LS701 | ELE | 38025-ELE | 1 | 300 | 111 | 411 | 01-411_.L0 | #REF!
BB1LS850 | ELE | 38025-ELE | 1 | 300 | 112 | 412 | 01-412_.L0 | #REF!
BB1LS851 | ELE | 38025-ELE | 1 | 300 | 113 | 413 | 01-413_.L0 | #REF!
BB1PS600 | ELE | 38025-ELE | 1 | 300 | 114 | 414 | 01-414_.L0 | #REF!
BB1PS601 | ELE | 38025-ELE | 1 | 300 | 115 | 415 | 01-415_.L0 | #REF!
BB1PS602 | ELE | 38025-ELE | 1 | 300 | 116 | 416 | 01-416_.L0 | #REF!
BB1PS603 | ELE | 38025-ELE | 1 | 300 | 117 | 417 | 01-417_.L0 | #REF!
BB1PS604 | ELE | 38025-ELE | 1 | 300 | 118 | 418 | 01-418_.L0 | #REF!
BB1PS605 | ELE | 38025-ELE | 1 | 300 | 119 | 419 | 01-419_.L0 | #REF!
BB1ST649 | ELE | 38025-ELE | 1 | 300 | 120 | 420 | 01-420_.L0 | #REF!
BB1ST650 | ELE | 38025-ELE | 1 | 300 | 121 | 421 | 01-421_.L0 | #REF!
BB1ST651 | ELE | 38025-ELE | 1 | 300 | 122 | 422 | 01-422_.L0 | #REF!
BB1ST652 | ELE | 38025-ELE | 1 | 300 | 123 | 423 | 01-423_.L0 | #REF!
BB1ST653 | ELE | 38025-ELE | 1 | 300 | 124 | 424 | 01-424_.L0 | #REF!
BB1ST654 | ELE | 38025-ELE | 1 | 300 | 125 | 425 | 01-425_.L0 | #REF!
BB1ST655 | ELE | 38025-ELE | 1 | 300 | 126 | 426 | 01-426_.L0 | #REF!
BB1ST656 | ELE | 38025-ELE | 1 | 300 | 127 | 427 | 01-427_.L0 | #REF!
BB1ST657 | ELE | 38025-ELE | 1 | 300 | 128 | 428 | 01-428_.L0 | #REF!
BB1ST659 | ELE | 38025-ELE | 1 | 300 | 129 | 429 | 01-429_.L0 | #REF!
BB1ST673 | ELE | 38025-ELE | 1 | 300 | 130 | 430 | 01-430_.L0 | #REF!
BB1ST674 | ELE | 38025-ELE | 1 | 300 | 131 | 431 | 01-431_.L0 | #REF!
BB1ST675 | ELE | 38025-ELE | 1 | 300 | 132 | 432 | 01-432_.L0 | #REF!
BB1ST850 | ELE | 38025-ELE | 1 | 300 | 133 | 433 | 01-433_.L0 | #REF!
BB1ST852 | ELE | 38025-ELE | 1 | 300 | 134 | 434 | 01-434_.L0 | #REF!
BB1ST853 | ELE | 38025-ELE | 1 | 300 | 135 | 435 | 01-435_.L0 | #REF!
BB1ST856 | ELE | 38025-ELE | 1 | 300 | 136 | 436 | 01-436_.L0 | #REF!
BB1TS600 | ELE | 38025-ELE | 1 | 300 | 137 | 437 | 01-437_.L0 | #REF!
BB1TS608 | ELE | 38025-ELE | 1 | 300 | 138 | 438 | 01-438_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 139 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 140 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 141 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 142 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 143 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 144 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 145 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 146 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 147 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 148 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 149 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 150 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 151 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 152 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 153 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 154 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 155 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 156 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 157 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 158 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 159 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 160 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 161 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 162 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 163 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 164 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 165 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 166 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 167 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 168 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 169 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 170 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 171 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 172 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 173 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 174 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 175 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 176 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 177 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 178 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 179 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 180 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 181 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 182 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 183 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 184 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 185 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 186 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 187 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 188 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 189 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 190 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 191 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 192 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 193 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 194 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 195 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 196 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 197 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 198 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 199 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 200 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 201 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 202 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 203 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 204 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 205 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 206 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 207 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 208 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 209 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 210 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 211 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 212 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 213 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 214 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 215 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 216 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 217 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 218 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 219 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 220 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 221 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 222 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 223 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 224 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 225 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 226 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 227 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 228 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 229 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 230 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 231 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 232 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 233 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 234 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 235 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 236 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 237 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 238 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 239 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 240 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 241 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 242 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 243 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 244 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 245 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 246 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 247 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 248 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 249 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 250 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 251 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 252 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 253 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 254 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 255 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 256 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 257 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 258 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 259 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 260 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 261 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 262 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 263 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 264 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 265 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 266 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 267 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 268 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 269 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 270 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 271 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 272 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 273 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 274 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 275 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 276 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 277 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 278 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 279 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 280 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 281 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 282 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 283 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 284 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 285 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 286 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 287 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 288 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 289 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 290 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 291 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 292 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 293 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 294 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 295 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 296 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 297 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 298 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 299 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 300 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 301 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 302 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 303 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 304 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 305 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 306 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 307 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 308 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 309 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 310 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 311 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 312 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 313 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 314 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 315 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 316 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 317 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 318 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 319 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 320 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 321 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 322 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 323 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 324 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 325 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 326 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 327 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 328 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 329 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 330 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 331 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 332 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 333 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 334 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 335 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 336 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 337 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 338 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 339 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 340 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 341 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 342 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 343 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 344 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 345 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 346 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 347 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 348 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 349 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 350 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 351 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 352 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 353 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 354 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 355 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 356 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 357 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 358 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 359 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 360 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 361 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 362 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 363 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 364 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 365 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 366 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 367 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 368 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 369 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 370 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 371 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 372 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 373 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 374 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 375 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 376 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 377 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 378 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 379 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 380 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 381 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 382 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 383 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 384 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 385 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 386 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 387 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 388 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 389 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 390 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 391 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 392 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 393 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 394 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 395 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 396 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 397 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 398 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 399 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 400 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 401 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 402 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 403 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 404 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 405 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 406 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 407 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 408 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 409 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 410 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 411 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 412 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 413 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 414 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 415 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 416 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 417 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 418 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 419 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 420 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 421 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 422 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 423 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 424 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 425 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 426 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 427 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 428 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 429 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 430 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 431 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 432 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 433 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 434 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 435 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 436 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 437 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 438 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 439 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 440 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 441 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 442 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 443 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 444 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 445 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 446 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 447 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 448 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 449 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 450 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 451 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 452 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 453 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 454 |  | 01-_.L0 | #REF!
| ELE | 38025-ELE | 1 |  | 455 |  | 01-_.L0 | #REF!

## X_PANEL
IO_CABINETS
TAG | DESCRIPTION | DEVICE_COUNT | DO | DI | AO | AI | SDO | SDI | SAO | SAI
KPA_FLOORX_IO | KPA NON ASSIGNED IO | 485 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR0_IO | KPA LEVEL 0 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR1_IO | KPA LEVEL 1 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR2_IO | KPA LEVEL 2 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR3_IO | KPA LEVEL 3 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FLOOR4_IO | KPA LEVEL 4 REMOTE IO CABINET | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_FUEL_STATION_IO | KPA FUEL STATION REMOTE IO CABINET | 132 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_MCC | KPA REMOTE IO INTERNAL TO MCC | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
KPA_PLC | KPA PLC CABINET | 87 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
ESP_PLC | ESP PLC CABINET | 8 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
ESP_MCC | ESP REMOTE IO INTERNAL TO MCC | 0 | TBA | TBA | TBA | TBA | TBA | TBA | TBA | TBA
0

## P_IO
| Index | Addressing | [9 empty] | Description |  | Catalog
| Index | Panel | PLC | RackRaw | SlotRaw | ChannelRaw | Type | Rack | Slot | Channel | Address | IO_Tag | Pin | CatalogDesc1 | CatalogDesc2 | CatalogNo
| 1 | KPA_FLOORX_IO | RIO | 1 | 1 | 0 | DI | 01 | 01 | 00 | RIO01:01.DI:00 | <004> | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 2 | KPA_FLOORX_IO | RIO | 1 | 1 | 1 | DI | 01 | 01 | 01 | RIO01:01.DI:01 | BB1FS003 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 3 | KPA_FLOORX_IO | RIO | 1 | 1 | 2 | DI | 01 | 01 | 02 | RIO01:01.DI:02 | BB1GS001 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 4 | KPA_FLOORX_IO | RIO | 1 | 1 | 3 | DI | 01 | 01 | 03 | RIO01:01.DI:03 | BB1GS002 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 5 | KPA_FLOORX_IO | RIO | 1 | 1 | 4 | DI | 01 | 01 | 04 | RIO01:01.DI:04 | BB1GS003 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 6 | KPA_FLOORX_IO | RIO | 1 | 1 | 5 | DI | 01 | 01 | 05 | RIO01:01.DI:05 | BB1GS004 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 7 | KPA_FLOORX_IO | RIO | 1 | 1 | 6 | DI | 01 | 01 | 06 | RIO01:01.DI:06 | BB1GS005 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 8 | KPA_FLOORX_IO | RIO | 1 | 1 | 7 | DI | 01 | 01 | 07 | RIO01:01.DI:07 | BB1GS006 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 9 | KPA_FLOORX_IO | RIO | 1 | 2 | 0 | DI | 01 | 02 | 00 | RIO01:02.DI:00 | BB1GS007 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 10 | KPA_FLOORX_IO | RIO | 1 | 2 | 1 | DI | 01 | 02 | 01 | RIO01:02.DI:01 | BB1GS008 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
`` | 11 | KPA_FLOORX_IO | RIO | 1 | 2 | 2 | DI | 01 | 02 | 02 | RIO01:02.DI:02 | BB1GS009 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 12 | KPA_FLOORX_IO | RIO | 1 | 2 | 3 | DI | 01 | 02 | 03 | RIO01:02.DI:03 | BB1GS010 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 13 | KPA_FLOORX_IO | RIO | 1 | 2 | 4 | DI | 01 | 02 | 04 | RIO01:02.DI:04 | BB1GS011 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 14 | KPA_FLOORX_IO | RIO | 1 | 2 | 5 | DI | 01 | 02 | 05 | RIO01:02.DI:05 | BB1GS012 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 15 | KPA_FLOORX_IO | RIO | 1 | 2 | 6 | DI | 01 | 02 | 06 | RIO01:02.DI:06 | BB1GS020 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 16 | KPA_FLOORX_IO | RIO | 1 | 2 | 7 | DI | 01 | 02 | 07 | RIO01:02.DI:07 | BB1GS200 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 17 | KPA_FLOORX_IO | RIO | 1 | 3 | 0 | DI | 01 | 03 | 00 | RIO01:03.DI:00 | BB1GS201 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 18 | KPA_FLOORX_IO | RIO | 1 | 3 | 1 | DI | 01 | 03 | 01 | RIO01:03.DI:01 | BB1GS203 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 19 | KPA_FLOORX_IO | RIO | 1 | 3 | 2 | DI | 01 | 03 | 02 | RIO01:03.DI:02 | BB1GS204 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 20 | KPA_FLOORX_IO | RIO | 1 | 3 | 3 | DI | 01 | 03 | 03 | RIO01:03.DI:03 | BB1GS205 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 21 | KPA_FLOORX_IO | RIO | 1 | 3 | 4 | DI | 01 | 03 | 04 | RIO01:03.DI:04 | BB1GS206 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 22 | KPA_FLOORX_IO | RIO | 1 | 3 | 5 | DI | 01 | 03 | 05 | RIO01:03.DI:05 | BB1GS207 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 23 | KPA_FLOORX_IO | RIO | 1 | 3 | 6 | DI | 01 | 03 | 06 | RIO01:03.DI:06 | BB1GS208 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 24 | KPA_FLOORX_IO | RIO | 1 | 3 | 7 | DI | 01 | 03 | 07 | RIO01:03.DI:07 | BB1GS209 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 25 | KPA_FLOORX_IO | RIO | 1 | 4 | 0 | DI | 01 | 04 | 00 | RIO01:04.DI:00 | BB1GS210 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 26 | KPA_FLOORX_IO | RIO | 1 | 4 | 1 | DI | 01 | 04 | 01 | RIO01:04.DI:01 | BB1GS211 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 27 | KPA_FLOORX_IO | RIO | 1 | 4 | 2 | DI | 01 | 04 | 02 | RIO01:04.DI:02 | BB1GS212 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 28 | KPA_FLOORX_IO | RIO | 1 | 4 | 3 | DI | 01 | 04 | 03 | RIO01:04.DI:03 | BB1GS213 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 29 | KPA_FLOORX_IO | RIO | 1 | 4 | 4 | DI | 01 | 04 | 04 | RIO01:04.DI:04 | BB1GS214 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 30 | KPA_FLOORX_IO | RIO | 1 | 4 | 5 | DI | 01 | 04 | 05 | RIO01:04.DI:05 | BB1GS215 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 31 | KPA_FLOORX_IO | RIO | 1 | 4 | 6 | DI | 01 | 04 | 06 | RIO01:04.DI:06 | BB1GS216 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 32 | KPA_FLOORX_IO | RIO | 1 | 4 | 7 | DI | 01 | 04 | 07 | RIO01:04.DI:07 | BB1GS217 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 33 | KPA_FLOORX_IO | RIO | 1 | 5 | 0 | DI | 01 | 05 | 00 | RIO01:05.DI:00 | BB1GS218 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 34 | KPA_FLOORX_IO | RIO | 1 | 5 | 1 | DI | 01 | 05 | 01 | RIO01:05.DI:01 | BB1GS219 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 35 | KPA_FLOORX_IO | RIO | 1 | 5 | 2 | DI | 01 | 05 | 02 | RIO01:05.DI:02 | BB1GS220 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 36 | KPA_FLOORX_IO | RIO | 1 | 5 | 3 | DI | 01 | 05 | 03 | RIO01:05.DI:03 | BB1GS221 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 37 | KPA_FLOORX_IO | RIO | 1 | 5 | 4 | DI | 01 | 05 | 04 | RIO01:05.DI:04 | BB1GS222 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 38 | KPA_FLOORX_IO | RIO | 1 | 5 | 5 | DI | 01 | 05 | 05 | RIO01:05.DI:05 | BB1GS223 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 39 | KPA_FLOORX_IO | RIO | 1 | 5 | 6 | DI | 01 | 05 | 06 | RIO01:05.DI:06 | BB1GS224 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 40 | KPA_FLOORX_IO | RIO | 1 | 5 | 7 | DI | 01 | 05 | 07 | RIO01:05.DI:07 | BB1GS225 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 41 | KPA_FLOORX_IO | RIO | 1 | 6 | 0 | DI | 01 | 06 | 00 | RIO01:06.DI:00 | BB1GS226 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 42 | KPA_FLOORX_IO | RIO | 1 | 6 | 1 | DI | 01 | 06 | 01 | RIO01:06.DI:01 | BB1GS227 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 43 | KPA_FLOORX_IO | RIO | 1 | 6 | 2 | DI | 01 | 06 | 02 | RIO01:06.DI:02 | BB1GS228 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 44 | KPA_FLOORX_IO | RIO | 1 | 6 | 3 | DI | 01 | 06 | 03 | RIO01:06.DI:03 | BB1GS230 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 45 | KPA_FLOORX_IO | RIO | 1 | 6 | 4 | DI | 01 | 06 | 04 | RIO01:06.DI:04 | BB1GS231 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 46 | KPA_FLOORX_IO | RIO | 1 | 6 | 5 | DI | 01 | 06 | 05 | RIO01:06.DI:05 | BB1GS232 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 47 | KPA_FLOORX_IO | RIO | 1 | 6 | 6 | DI | 01 | 06 | 06 | RIO01:06.DI:06 | BB1GS233 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 48 | KPA_FLOORX_IO | RIO | 1 | 6 | 7 | DI | 01 | 06 | 07 | RIO01:06.DI:07 | BB1GS600 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 49 | KPA_FLOORX_IO | RIO | 1 | 7 | 0 | DI | 01 | 07 | 00 | RIO01:07.DI:00 | BB1GS601 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 50 | KPA_FLOORX_IO | RIO | 1 | 7 | 1 | DI | 01 | 07 | 01 | RIO01:07.DI:01 | BB1GS602 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 51 | KPA_FLOORX_IO | RIO | 1 | 7 | 2 | DI | 01 | 07 | 02 | RIO01:07.DI:02 | BB1GS603 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 52 | KPA_FLOORX_IO | RIO | 1 | 7 | 3 | DI | 01 | 07 | 03 | RIO01:07.DI:03 | BB1GS604 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 53 | KPA_FLOORX_IO | RIO | 1 | 7 | 4 | DI | 01 | 07 | 04 | RIO01:07.DI:04 | BB1GS605 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 54 | KPA_FLOORX_IO | RIO | 1 | 7 | 5 | DI | 01 | 07 | 05 | RIO01:07.DI:05 | BB1GS606 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 55 | KPA_FLOORX_IO | RIO | 1 | 7 | 6 | DI | 01 | 07 | 06 | RIO01:07.DI:06 | BB1GS607 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 56 | KPA_FLOORX_IO | RIO | 1 | 7 | 7 | DI | 01 | 07 | 07 | RIO01:07.DI:07 | BB1GS608 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 57 | KPA_FLOORX_IO | RIO | 1 | 8 | 0 | DI | 01 | 08 | 00 | RIO01:08.DI:00 | BB1GS609 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 58 | KPA_FLOORX_IO | RIO | 1 | 8 | 1 | DI | 01 | 08 | 01 | RIO01:08.DI:01 | BB1GS610 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 59 | KPA_FLOORX_IO | RIO | 1 | 8 | 2 | DI | 01 | 08 | 02 | RIO01:08.DI:02 | BB1GS611 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 60 | KPA_FLOORX_IO | RIO | 1 | 8 | 3 | DI | 01 | 08 | 03 | RIO01:08.DI:03 | BB1GS612 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 61 | KPA_FLOORX_IO | RIO | 1 | 8 | 4 | DI | 01 | 08 | 04 | RIO01:08.DI:04 | BB1GS613 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 62 | KPA_FLOORX_IO | RIO | 1 | 8 | 5 | DI | 01 | 08 | 05 | RIO01:08.DI:05 | BB1GS614 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 63 | KPA_FLOORX_IO | RIO | 1 | 8 | 6 | DI | 01 | 08 | 06 | RIO01:08.DI:06 | BB1GS615 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 64 | KPA_FLOORX_IO | RIO | 1 | 8 | 7 | DI | 01 | 08 | 07 | RIO01:08.DI:07 | BB1GS616 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 65 | KPA_FLOORX_IO | RIO | 1 | 9 | 0 | DI | 01 | 09 | 00 | RIO01:09.DI:00 | BB1GS617 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 66 | KPA_FLOORX_IO | RIO | 1 | 9 | 1 | DI | 01 | 09 | 01 | RIO01:09.DI:01 | BB1GS618 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 67 | KPA_FLOORX_IO | RIO | 1 | 9 | 2 | DI | 01 | 09 | 02 | RIO01:09.DI:02 | BB1GS619 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 68 | KPA_FLOORX_IO | RIO | 1 | 9 | 3 | DI | 01 | 09 | 03 | RIO01:09.DI:03 | BB1GS620 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 69 | KPA_FLOORX_IO | RIO | 1 | 9 | 4 | DI | 01 | 09 | 04 | RIO01:09.DI:04 | BB1GS621 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 70 | KPA_FLOORX_IO | RIO | 1 | 9 | 5 | DI | 01 | 09 | 05 | RIO01:09.DI:05 | BB1GS622 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 71 | KPA_FLOORX_IO | RIO | 1 | 9 | 6 | DI | 01 | 09 | 06 | RIO01:09.DI:06 | BB1GS623 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 72 | KPA_FLOORX_IO | RIO | 1 | 9 | 7 | DI | 01 | 09 | 07 | RIO01:09.DI:07 | BB1GS650 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 73 | KPA_FLOORX_IO | RIO | 1 | 10 | 0 | DI | 01 | 10 | 00 | RIO01:10.DI:00 | BB1GS651 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 74 | KPA_FLOORX_IO | RIO | 1 | 10 | 1 | DI | 01 | 10 | 01 | RIO01:10.DI:01 | BB1GS652 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 75 | KPA_FLOORX_IO | RIO | 1 | 10 | 2 | DI | 01 | 10 | 02 | RIO01:10.DI:02 | BB1GS653 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 76 | KPA_FLOORX_IO | RIO | 1 | 10 | 3 | DI | 01 | 10 | 03 | RIO01:10.DI:03 | BB1GS654 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 77 | KPA_FLOORX_IO | RIO | 1 | 10 | 4 | DI | 01 | 10 | 04 | RIO01:10.DI:04 | BB1GS655 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 78 | KPA_FLOORX_IO | RIO | 1 | 10 | 5 | DI | 01 | 10 | 05 | RIO01:10.DI:05 | BB1GS656 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 79 | KPA_FLOORX_IO | RIO | 1 | 10 | 6 | DI | 01 | 10 | 06 | RIO01:10.DI:06 | BB1GS659 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 80 | KPA_FLOORX_IO | RIO | 1 | 10 | 7 | DI | 01 | 10 | 07 | RIO01:10.DI:07 | BB1GS660 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 81 | KPA_FLOORX_IO | RIO | 1 | 11 | 0 | DI | 01 | 11 | 00 | RIO01:11.DI:00 | BB1GS661 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 82 | KPA_FLOORX_IO | RIO | 1 | 11 | 1 | DI | 01 | 11 | 01 | RIO01:11.DI:01 | BB1GS662 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 83 | KPA_FLOORX_IO | RIO | 1 | 11 | 2 | DI | 01 | 11 | 02 | RIO01:11.DI:02 | BB1GS663 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 84 | KPA_FLOORX_IO | RIO | 1 | 11 | 3 | DI | 01 | 11 | 03 | RIO01:11.DI:03 | BB1GS800 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 85 | KPA_FLOORX_IO | RIO | 1 | 11 | 4 | DI | 01 | 11 | 04 | RIO01:11.DI:04 | BB1GS801 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 86 | KPA_FLOORX_IO | RIO | 1 | 11 | 5 | DI | 01 | 11 | 05 | RIO01:11.DI:05 | BB1GS802 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 87 | KPA_FLOORX_IO | RIO | 1 | 11 | 6 | DI | 01 | 11 | 06 | RIO01:11.DI:06 | BB1GS803 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 88 | KPA_FLOORX_IO | RIO | 1 | 11 | 7 | DI | 01 | 11 | 07 | RIO01:11.DI:07 | BB1GS850 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 89 | KPA_FLOORX_IO | RIO | 1 | 12 | 0 | DI | 01 | 12 | 00 | RIO01:12.DI:00 | BB1GS851 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 90 | KPA_FLOORX_IO | RIO | 1 | 12 | 1 | DI | 01 | 12 | 01 | RIO01:12.DI:01 | BB1GS852 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 91 | KPA_FLOORX_IO | RIO | 1 | 12 | 2 | DI | 01 | 12 | 02 | RIO01:12.DI:02 | BB1GS853 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 92 | KPA_FLOORX_IO | RIO | 1 | 12 | 3 | DI | 01 | 12 | 03 | RIO01:12.DI:03 | BB1GS854 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 93 | KPA_FLOORX_IO | RIO | 1 | 12 | 4 | DI | 01 | 12 | 04 | RIO01:12.DI:04 | BB1GS855 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 94 | KPA_FLOORX_IO | RIO | 1 | 12 | 5 | DI | 01 | 12 | 05 | RIO01:12.DI:05 | BB1GS856 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 95 | KPA_FLOORX_IO | RIO | 1 | 12 | 6 | DI | 01 | 12 | 06 | RIO01:12.DI:06 | BB1GS857 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 96 | KPA_FLOORX_IO | RIO | 1 | 12 | 7 | DI | 01 | 12 | 07 | RIO01:12.DI:07 | BB1GS858 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 97 | KPA_FLOORX_IO | RIO | 1 | 13 | 0 | DI | 01 | 13 | 00 | RIO01:13.DI:00 | BB1LS600 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 98 | KPA_FLOORX_IO | RIO | 1 | 13 | 1 | DI | 01 | 13 | 01 | RIO01:13.DI:01 | BB1LS608 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 99 | KPA_FLOORX_IO | RIO | 1 | 13 | 2 | DI | 01 | 13 | 02 | RIO01:13.DI:02 | BB1LS650 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 100 | KPA_FLOORX_IO | RIO | 1 | 13 | 3 | DI | 01 | 13 | 03 | RIO01:13.DI:03 | BB1LS651 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 101 | KPA_FLOORX_IO | RIO | 1 | 13 | 4 | DI | 01 | 13 | 04 | RIO01:13.DI:04 | BB1LS652 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 102 | KPA_FLOORX_IO | RIO | 1 | 13 | 5 | DI | 01 | 13 | 05 | RIO01:13.DI:05 | BB1LS653 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 103 | KPA_FLOORX_IO | RIO | 1 | 13 | 6 | DI | 01 | 13 | 06 | RIO01:13.DI:06 | BB1LS654 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 104 | KPA_FLOORX_IO | RIO | 1 | 13 | 7 | DI | 01 | 13 | 07 | RIO01:13.DI:07 | BB1LS655 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 105 | KPA_FLOORX_IO | RIO | 1 | 14 | 0 | DI | 01 | 14 | 00 | RIO01:14.DI:00 | BB1LS656 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 106 | KPA_FLOORX_IO | RIO | 1 | 14 | 1 | DI | 01 | 14 | 01 | RIO01:14.DI:01 | BB1LS657 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 107 | KPA_FLOORX_IO | RIO | 1 | 14 | 2 | DI | 01 | 14 | 02 | RIO01:14.DI:02 | BB1LS658 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 108 | KPA_FLOORX_IO | RIO | 1 | 14 | 3 | DI | 01 | 14 | 03 | RIO01:14.DI:03 | BB1LS659 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 109 | KPA_FLOORX_IO | RIO | 1 | 14 | 4 | DI | 01 | 14 | 04 | RIO01:14.DI:04 | BB1LS660 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 110 | KPA_FLOORX_IO | RIO | 1 | 14 | 5 | DI | 01 | 14 | 05 | RIO01:14.DI:05 | BB1LS661 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 111 | KPA_FLOORX_IO | RIO | 1 | 14 | 6 | DI | 01 | 14 | 06 | RIO01:14.DI:06 | BB1LS700 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 112 | KPA_FLOORX_IO | RIO | 1 | 14 | 7 | DI | 01 | 14 | 07 | RIO01:14.DI:07 | BB1LS701 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 113 | KPA_FLOORX_IO | RIO | 1 | 14 | 0 | DI | 01 | 14 | 00 | RIO01:14.DI:00 | BB1LS850 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 114 | KPA_FLOORX_IO | RIO | 1 | 15 | 1 | DI | 01 | 15 | 01 | RIO01:15.DI:01 | BB1LS851 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 115 | KPA_FLOORX_IO | RIO | 1 | 15 | 2 | DI | 01 | 15 | 02 | RIO01:15.DI:02 | BB1PS600 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 116 | KPA_FLOORX_IO | RIO | 1 | 15 | 3 | DI | 01 | 15 | 03 | RIO01:15.DI:03 | BB1PS601 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 117 | KPA_FLOORX_IO | RIO | 1 | 15 | 4 | DI | 01 | 15 | 04 | RIO01:15.DI:04 | BB1PS602 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 118 | KPA_FLOORX_IO | RIO | 1 | 15 | 5 | DI | 01 | 15 | 05 | RIO01:15.DI:05 | BB1PS603 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 119 | KPA_FLOORX_IO | RIO | 1 | 15 | 6 | DI | 01 | 15 | 06 | RIO01:15.DI:06 | BB1PS604 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 120 | KPA_FLOORX_IO | RIO | 1 | 15 | 7 | DI | 01 | 15 | 07 | RIO01:15.DI:07 | BB1PS605 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 121 | KPA_FLOORX_IO | RIO | 1 | 15 | 0 | DI | 01 | 15 | 00 | RIO01:15.DI:00 | BB1ST649 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 122 | KPA_FLOORX_IO | RIO | 1 | 16 | 1 | DI | 01 | 16 | 01 | RIO01:16.DI:01 | BB1ST650 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 123 | KPA_FLOORX_IO | RIO | 1 | 16 | 2 | DI | 01 | 16 | 02 | RIO01:16.DI:02 | BB1ST651 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 124 | KPA_FLOORX_IO | RIO | 1 | 16 | 3 | DI | 01 | 16 | 03 | RIO01:16.DI:03 | BB1ST652 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 125 | KPA_FLOORX_IO | RIO | 1 | 16 | 4 | DI | 01 | 16 | 04 | RIO01:16.DI:04 | BB1ST653 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 126 | KPA_FLOORX_IO | RIO | 1 | 16 | 5 | DI | 01 | 16 | 05 | RIO01:16.DI:05 | BB1ST654 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 127 | KPA_FLOORX_IO | RIO | 1 | 16 | 6 | DI | 01 | 16 | 06 | RIO01:16.DI:06 | BB1ST655 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 128 | KPA_FLOORX_IO | RIO | 1 | 16 | 7 | DI | 01 | 16 | 07 | RIO01:16.DI:07 | BB1ST656 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 129 | KPA_FLOORX_IO | RIO | 1 | 16 | 0 | DI | 01 | 16 | 00 | RIO01:16.DI:00 | BB1ST657 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 130 | KPA_FLOORX_IO | RIO | 1 | 17 | 1 | DI | 01 | 17 | 01 | RIO01:17.DI:01 | BB1ST659 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 131 | KPA_FLOORX_IO | RIO | 1 | 17 | 2 | DI | 01 | 17 | 02 | RIO01:17.DI:02 | BB1ST673 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 132 | KPA_FLOORX_IO | RIO | 1 | 17 | 3 | DI | 01 | 17 | 03 | RIO01:17.DI:03 | BB1ST674 | 04 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 133 | KPA_FLOORX_IO | RIO | 1 | 17 | 4 | DI | 01 | 17 | 04 | RIO01:17.DI:04 | BB1ST675 | 05 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 134 | KPA_FLOORX_IO | RIO | 1 | 17 | 5 | DI | 01 | 17 | 05 | RIO01:17.DI:05 | BB1ST850 | 06 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 135 | KPA_FLOORX_IO | RIO | 1 | 17 | 6 | DI | 01 | 17 | 06 | RIO01:17.DI:06 | BB1ST852 | 07 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 136 | KPA_FLOORX_IO | RIO | 1 | 17 | 7 | DI | 01 | 17 | 07 | RIO01:17.DI:07 | BB1ST853 | 08 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 137 | KPA_FLOORX_IO | RIO | 1 | 17 | 0 | DI | 01 | 17 | 00 | RIO01:17.DI:00 | BB1ST856 | 01 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 138 | KPA_FLOORX_IO | RIO | 1 | 18 | 1 | DI | 01 | 18 | 01 | RIO01:18.DI:01 | BB1TS600 | 02 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 139 | KPA_FLOORX_IO | RIO | 1 | 18 | 2 | DI | 01 | 18 | 02 | RIO01:18.DI:02 | BB1TS608 | 03 | AB 1734-IB8 | 24VDC 8-Point Sink Input Module | 1734-IB8*1
| 140 | KPA_FLOORX_IO | RIO | 1 | 18 | 3 |  | 01 | 18 | 03 | RIO01:18.:03 |  | 04
| 141 | KPA_FLOORX_IO | RIO | 1 | 18 | 4 |  | 01 | 18 | 04 | RIO01:18.:04 |  | 05
| 142 | KPA_FLOORX_IO | RIO | 1 | 18 | 5 |  | 01 | 18 | 05 | RIO01:18.:05 |  | 06
| 143 | KPA_FLOORX_IO | RIO | 1 | 18 | 6 |  | 01 | 18 | 06 | RIO01:18.:06 |  | 07
| 144 | KPA_FLOORX_IO | RIO | 1 | 18 | 7 |  | 01 | 18 | 07 | RIO01:18.:07 |  | 08
| 145 | KPA_FLOORX_IO | RIO | 1 | 18 | 0 |  | 01 | 18 | 00 | RIO01:18.:00 |  | 01
| 146 | KPA_FLOORX_IO | RIO | 1 | 19 | 1 |  | 01 | 19 | 01 | RIO01:19.:01 |  | 02
| 147 | KPA_FLOORX_IO | RIO | 1 | 19 | 2 |  | 01 | 19 | 02 | RIO01:19.:02 |  | 03
| 148 | KPA_FLOORX_IO | RIO | 1 | 19 | 3 |  | 01 | 19 | 03 | RIO01:19.:03 |  | 04
| 149 | KPA_FLOORX_IO | RIO | 1 | 19 | 4 |  | 01 | 19 | 04 | RIO01:19.:04 |  | 05
| 150 | KPA_FLOORX_IO | RIO | 1 | 19 | 5 |  | 01 | 19 | 05 | RIO01:19.:05 |  | 06
| 151 | KPA_FLOORX_IO | RIO | 1 | 19 | 6 |  | 01 | 19 | 06 | RIO01:19.:06 |  | 07
| 152 | KPA_FLOORX_IO | RIO | 1 | 19 | 7 |  | 01 | 19 | 07 | RIO01:19.:07 |  | 08
| 153 | KPA_FLOORX_IO | RIO | 1 | 19 | 0 |  | 01 | 19 | 00 | RIO01:19.:00 |  | 01
| 154 | KPA_FLOORX_IO | RIO | 1 | 20 | 1 |  | 01 | 20 | 01 | RIO01:20.:01 |  | 02
| 155 | KPA_FLOORX_IO | RIO | 1 | 20 | 2 |  | 01 | 20 | 02 | RIO01:20.:02 |  | 03
| 156 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 157 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 158 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 159 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 160 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 161 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 162 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 163 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 164 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 165 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 166 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 167 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 168 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 169 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 170 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 171 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 172 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 173 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 174 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 175 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 176 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 177 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 178 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 179 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 180 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 181 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 182 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 183 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 184 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 185 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 186 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 187 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 188 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 189 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 190 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 191 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 192 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 193 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 194 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 195 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 196 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 197 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 198 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 199 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 200 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 201 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 202 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 203 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 204 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 205 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 206 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 207 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 208 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 209 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 210 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 211 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 212 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 213 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 214 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 215 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 216 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 217 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 218 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 219 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 220 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 221 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 222 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 223 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 224 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 225 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 226 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 227 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 228 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 229 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 230 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 231 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 232 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 233 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 234 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 235 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 236 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 237 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 238 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 239 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 240 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 241 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 242 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 243 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 244 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 245 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 246 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 247 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 248 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 249 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 250 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 251 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 252 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 253 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 254 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 255 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 256 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 257 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 258 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 259 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 260 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 261 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 262 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 263 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 264 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 265 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 266 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 267 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 268 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 269 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 270 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 271 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 272 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 273 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 274 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 275 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 276 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 277 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 278 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 279 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 280 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 281 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 282 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 283 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 284 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 285 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 286 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 287 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 288 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 289 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 290 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 291 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 292 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 293 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 294 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 295 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 296 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 297 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 298 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 299 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 300 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 301 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 302 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 303 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 304 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 305 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 306 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 307 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 308 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 309 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 310 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 311 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 312 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 313 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 314 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 315 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 316 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 317 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 318 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 319 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 320 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 321 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 322 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 323 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 324 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 325 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 326 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 327 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 328 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 329 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 330 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 331 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 332 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 333 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 334 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 335 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 336 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 337 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 338 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 339 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 340 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 341 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 342 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 343 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 344 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 345 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 346 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 347 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 348 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 349 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 350 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 351 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 352 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 353 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 354 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 355 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 356 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 357 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 358 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 359 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 360 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 361 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 362 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 363 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 364 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 365 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 366 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 367 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 368 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 369 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 370 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 371 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 372 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 373 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 374 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 375 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 376 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 377 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 378 | KPA_FLOORX_IO | RIO |  |  | 1 |  | 00 | 00 | 01 | RIO00:00.:01 |  | 02
| 379 | KPA_FLOORX_IO | RIO |  |  | 2 |  | 00 | 00 | 02 | RIO00:00.:02 |  | 03
| 380 | KPA_FLOORX_IO | RIO |  |  | 3 |  | 00 | 00 | 03 | RIO00:00.:03 |  | 04
| 381 | KPA_FLOORX_IO | RIO |  |  | 4 |  | 00 | 00 | 04 | RIO00:00.:04 |  | 05
| 382 | KPA_FLOORX_IO | RIO |  |  | 5 |  | 00 | 00 | 05 | RIO00:00.:05 |  | 06
| 383 | KPA_FLOORX_IO | RIO |  |  | 6 |  | 00 | 00 | 06 | RIO00:00.:06 |  | 07
| 384 | KPA_FLOORX_IO | RIO |  |  | 7 |  | 00 | 00 | 07 | RIO00:00.:07 |  | 08
| 385 | KPA_FLOORX_IO | RIO |  |  | 0 |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 386 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 387 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 388 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 389 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 390 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 391 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 392 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 393 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 394 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 395 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 396 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 397 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 398 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 399 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 400 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 401 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 402 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 403 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 404 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 405 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 406 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 407 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 408 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 409 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 410 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 411 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 412 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 413 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 414 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 415 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 416 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 417 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 418 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 419 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 420 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 421 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 422 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 423 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 424 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 425 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 426 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 427 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 428 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 429 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 430 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 431 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 432 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 433 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 434 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 435 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 436 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 437 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 438 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 439 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 440 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 441 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 442 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 443 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 444 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 445 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 446 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 447 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 448 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 449 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 450 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 451 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 452 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 453 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 454 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 455 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
| 456 | KPA_FLOORX_IO | RIO |  |  |  |  | 00 | 00 | 00 | RIO00:00.:00 |  | 01
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## D_DEVICES
DEVICES
propose we get kpa to split devices in areas / levels etc
TAG | DESCRIPTION | x1 | TYPICAL | x2 | PID | PID_AREA | ROOM | CABINET | NOTES
<001> | ELECTRICAL ROOM TEMPERATURE |  | MEAS_ANA |  | - | - | KPA_PLC | KPA_PLC
<002> | PLC-CABINET TEMPERATURE |  | MEAS_ANA |  | - | - | KPA_PLC | KPA_PLC
<003> | STEAM TO EXISTING HEADER ENERGY CALCULATOR |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
<004> | FUEL SILO CROSS CONVEYOR EXPLOSION HATCH LIMIT SWITCH |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
<005> | SAND TRANSMITTER 230 VAC FEED |  | MCCB_1ph |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1BL200 | SOOTBLOWER 1 |  | DOL_REV_BUS |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL200_ISOLATOR | SOOTBLOWER 1 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL201 | SOOTBLOWER 2 |  | DOL_REV_BUS |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL201_ISOLATOR | SOOTBLOWER 2 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL202 | SOOTBLOWER 3 |  | DOL_REV_BUS |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL202_ISOLATOR | SOOTBLOWER 3 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL203 | SOOTBLOWER 4 |  | DOL_REV_BUS |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL203_ISOLATOR | SOOTBLOWER 4 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL204 | SOOTBLOWER 5 |  | DOL_REV_BUS |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL204_ISOLATOR | SOOTBLOWER 5 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL205 | SOOTBLOWER 6 |  | DOL_REV_BUS |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL205_ISOLATOR | SOOTBLOWER 6 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL206 | SOOTBLOWER 7 |  | DOL_REV_BUS |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BL206_ISOLATOR | SOOTBLOWER 7 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1BU500_AI_IF1 | BURNER ANALOGUE INPUT INTERFACE 1 |  | BURNER_M11 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_AI_IF2 | BURNER ANALOGUE INPUT INTERFACE 2 |  | BURNER_M12 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_AO_IF1 | BURNER ANALOGUE OUTPUT INTERFACE 1 |  | BURNER_M9 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_AO_IF2 | BURNER ANALOGUE OUTPUT INTERFACE 2 |  | BURNER_M10 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DI_IF1 | BURNER DIGITAL INPUT INTERFACE 1 |  | BURNER_M4 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DI_IF2 | BURNER DIGITAL INPUT INTERFACE 2 |  | BURNER_M5 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DI_IF3 | BURNER DIGITAL INPUT INTERFACE 3 |  | BURNER_M6 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DI_IF4 | BURNER DIGITAL INPUT INTERFACE 4 |  | BURNER_M7 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DI_IF5 | BURNER DIGITAL INPUT INTERFACE 5 |  | BURNER_M8 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DO_IF1 | BURNER DIGITAL OUTPUT INTERFACE 1 |  | BURNER |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DO_IF2 | BURNER DIGITAL OUTPUT INTERFACE 2 |  | BURNER_M0 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DO_IF3 | BURNER DIGITAL OUTPUT INTERFACE 3 |  | BURNER_M1 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DO_IF4 | BURNER DIGITAL OUTPUT INTERFACE 4 |  | BURNER_M2 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1BU500_DO_IF5 | BURNER DIGITAL OUTPUT INTERFACE 5 |  | BURNER_M3 |  | 4013 | GAS FEEDING SYSTEM | RESERVATION_IO | KPA_FLOORX_IO
BB1CP002 | SMOKE EXHAUST CABINET |  | MCCB_1ph |  | - | -
BB1CV001_POSITION | MAKE-UP WATER CONTROL VALVE POSITION |  | CONT_VLV_M0 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV001_SETPOINT | MAKE-UP WATER CONTROL VALVE SETPOINT |  | CONT_VLV |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV002_POSITION | FEED WATER CONTROL VALVE POSITION |  | CONT_VLV_M0 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV002_SETPOINT | FEED WATER CONTROL VALVE SETPOINT |  | CONT_VLV |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV003 | CONTINUOUS BLOW DOWN VALVE |  | MTR_VLV_DETAIL |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV003_CLOSE | CONTINUOUS BLOW DOWN VALVE CLOSE |  | MTR_VLV_DETAIL |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV003_CLOSED | CONTINUOUS BLOW DOWN VALVE CLOSED |  | MTR_VLV_DETAIL |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV003_FAULT | CONTINUOUS BLOW DOWN VALVE FAULT |  | MTR_VLV_DETAIL |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV003_OPEN | CONTINUOUS BLOW DOWN VALVE OPEN |  | MTR_VLV_DETAIL |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV003_OPENED | CONTINUOUS BLOW DOWN VALVE OPENED |  | MTR_VLV_DETAIL |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV003_POSITION | CONTINUOUS BLOW DOWN VALVE POSITION |  | MTR_VLV_DETAIL |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV004_POSITION | PRIMARY AIR PREHEATER CONTROL VALVE POSITION |  | CONT_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1CV004_SETPOINT | PRIMARY AIR PREHEATER CONTROL VALVE SETPOINT |  | CONT_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1CV200_POSITION | STEAM FROM DRUM CONTROL VALVE POSITION |  | CONT_VLV_M0 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV200_SETPOINT | STEAM FROM DRUM CONTROL VALVE SETPOINT |  | CONT_VLV |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV201 | START-UP VALVE |  | MTR_VLV |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1CV201_CLOSE | START-UP VALVE CLOSE |  | MTR_VLV_M1 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1CV201_CLOSED | START-UP VALVE CLOSED |  | MTR_VLV_M3 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1CV201_FAULT | START-UP VALVE FAULT |  | MTR_VLV_M4 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1CV201_OPEN | START-UP VALVE OPEN |  | MTR_VLV_M0 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1CV201_OPENED | START-UP VALVE OPENED |  | MTR_VLV_M2 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1CV201_POSITION | START-UP VALVE POSITION |  | MTR_VLV_M5 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1CV202 | STEAM PRESSURE REDUCTION VALVE |  | MTR_VLV |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV202_CLOSE | STEAM PRESSURE REDUCTION VALVE CLOSE |  | MTR_VLV_M1 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV202_CLOSED | STEAM PRESSURE REDUCTION VALVE CLOSED |  | MTR_VLV_M3 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV202_FAULT | STEAM PRESSURE REDUCTION VALVE FAULT |  | MTR_VLV_M4 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV202_OPEN | STEAM PRESSURE REDUCTION VALVE OPEN |  | MTR_VLV_M0 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV202_OPENED | STEAM PRESSURE REDUCTION VALVE OPENED |  | MTR_VLV_M2 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV202_POSITION | STEAM PRESSURE REDUCTION VALVE POSITION |  | MTR_VLV_M5 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV203 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE |  | MTR_VLV |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV203_CLOSE | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE |  | MTR_VLV_M1 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV203_CLOSED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSED |  | MTR_VLV_M3 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV203_FAULT | STEAM ACCUMULATOR PRESSURE CONTROL VALVE FAULT |  | MTR_VLV_M4 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV203_OPEN | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN |  | MTR_VLV_M0 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV203_OPENED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPENED |  | MTR_VLV_M2 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV203_POSITION | STEAM ACCUMULATOR PRESSURE CONTROL VALVE POSITION |  | MTR_VLV_M5 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1CV402_POSITION | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 POSITION |  | CONT_VLV_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1CV402_SETPOINT | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 SETPOINT |  | CONT_VLV |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1CV403_POSITION | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 POSITION |  | CONT_VLV_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1CV403_SETPOINT | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 SETPOINT |  | CONT_VLV |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1CV405 | BOTTOM ASH VALVE SOLENOID VALVE |  | BIN_VLV |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV406 | BOTTOM ASH VALVE SOLENOID VALVE |  | BIN_VLV |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV412 | BOTTOM ASH SIEVE BYPASS SOLENOID VALVE |  | BIN_VLV |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV413_CLOSE | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER CLOSE |  | BIN_VLV_2DO_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV413_OPEN | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER OPEN |  | BIN_VLV_2DO |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1CV414 | WORK AIR TO PNEUMATIC TRANSMITTER PNEUMATIC VAL VE |  | BIN_VLV |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1DM300_POSITION | TERTIARY AIR DAMPER 1 POSITION |  | CONT_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM300_SETPOINT | TERTIARY AIR DAMPER 1 SETPOINT |  | CONT_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM301_POSITION | SECONDARY AIR DAMPER 4 POSITION |  | CONT_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM301_SETPOINT | SECONDARY AIR DAMPER 4 SETPOINT |  | CONT_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM302_POSITION | SECONDARY AIR DAMPER 3 POSITION |  | CONT_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM302_SETPOINT | SECONDARY AIR DAMPER 3 SETPOINT |  | CONT_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM303_POSITION | SECONDARY AIR DAMPER 2 POSITION |  | CONT_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM303_SETPOINT | SECONDARY AIR DAMPER 2 SETPOINT |  | CONT_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM304_POSITION | SECONDARY AIR DAMPER 1 POSITION |  | CONT_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM304_SETPOINT | SECONDARY AIR DAMPER 1 SETPOINT |  | CONT_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM400_POSITION | PRIMARY AIR DAMPER POSITION |  | CONT_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM400_SETPOINT | PRIMARY AIR DAMPER SETPOINT |  | CONT_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM550_POSITION | RECIRCULATION GAS DAMPER POSITION |  | CONT_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DM550_SETPOINT | RECIRCULATION GAS DAMPER SETPOINT |  | CONT_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1DR400 | COMPRESSOR 1 DRYER |  | MCCB_1ph |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1DR401 | COMPRESSOR 2 DRYER |  | MCCB_1ph |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EH600 | ELECTRIC HEATER HYDRAULIC UNIT |  | DOL_DIR_BUS |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EH600_ISOLATOR | ELECTRIC HEATER HYDRAULIC UNIT ISOLATOR |  | DOL_DIR_BUS_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EH662 | HEATER FOR SLIPRING UNIT |  | MCCB_1ph |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM001 | FEED WATER PUMP 1 |  | FRQ_DIR |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM002 | FEED WATER PUMP 2 |  | FRQ_DIR |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM008 | CONVEYOR COOLING PUMP |  | DOL_DIR_BUS |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM008_ISOLATOR | CONVEYOR COOLING PUMP ISOLATOR |  | DOL_DIR_BUS_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM009 | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN |  | DOL_DIR_BUS |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM009_ISOLATOR | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN ISOLAT OR |  | DOL_DIR_BUS_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM400 | PRIMARY AIR FAN |  | FRQ_DIR |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM401 | SECONDARY AIR FAN |  | FRQ_DIR |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM401 | SECONDARY AIR FAN |  | DOL_REV_BUS |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM401_ISOLATOR | EXHAUST FAN 1 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM402 | COMPRESSOR 1 |  | DOL_REV_BUS |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM402_FAULT_ACK_DO | COMPRESSOR 1 FAULT ACKNOWLEDGE |  | COMPR_M3 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM402_FAULT_DI | COMPRESSOR 1 FAULT |  | COMPR |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM402_ISOLATOR | EXHAUST FAN 2 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM402_RESERVE_DI | COMPRESSOR 1 RESERVE |  | COMPR_M1 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM402_RUN_DO | COMPRESSOR 1 REMOTE RUN |  | COMPR_M2 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM402_RUNNING_DI | COMPRESSOR 1 RUNNING |  | COMPR_M0 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM403 | COMPRESSOR 2 |  | DOL_REV_BUS |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM403_FAULT_ACK_DO | COMPRESSOR 2 FAULT ACKNOWLEDGE |  | COMPR_M3 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM403_FAULT_DI | COMPRESSOR 2 FAULT |  | COMPR |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM403_ISOLATOR | EXHAUST FAN 3 ISOLATOR |  | DOL_REV_BUS_M0 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM403_RESERVE_DI | COMPRESSOR 2 RESERVE |  | COMPR_M1 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM403_RUN_DO | COMPRESSOR 2 REMOTE RUN |  | COMPR_M2 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM403_RUNNING_DI | COMPRESSOR 2 RUNNING |  | COMPR_M0 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM405 | AIR INTAKE GRILL 1 OPEN |  | BELIMO_VLV |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM406 | AIR INTAKE GRILL 2 OPEN |  | BELIMO_VLV |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM407 | AIR INTAKE GRILL 3 OPEN |  | BELIMO_VLV |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM408 | BOILER HOUSE HEATER 1 |  | DOL_DIR_BUS |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM408_ISOLATOR | BOILER HOUSE HEATER 1 ISOLATOR |  | DOL_DIR_BUS_M0 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM409 | BOILER HOUSE HEATER 2 |  | DOL_DIR_BUS |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM409_ISOLATOR | BOILER HOUSE HEATER 2 ISOLATOR |  | DOL_DIR_BUS_M0 |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1EM550 | FLUE GAS FAN |  | FRQ_DIR |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM601 | DUST EXTRACTION ROTARY FEEDER |  | DOL_REVH_BUS |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM601_ISOLATOR | DUST EXTRACTION ROTARY FEEDER ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM601_LOCAL_MODE | DUST EXTRACTION ROTARY FEEDER LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM601_LOCAL_RUN_FWD | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_F WD |  | DOL_REVH_BUS_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM601_LOCAL_RUN_REV | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_R EV |  | DOL_REVH_BUS_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM603 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 |  | FRQ_DIRH |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM603_ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 ISOLATOR |  | FRQ_DIRH_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM603_LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_MODE |  | FRQ_DIRH_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM603_LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_RUN |  | FRQ_DIRH_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM604 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 |  | FRQ_DIRH |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM604_ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 ISOLATOR |  | FRQ_DIRH_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM604_LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_MODE |  | FRQ_DIRH_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM604_LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_RUN |  | FRQ_DIRH_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM605 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 |  | FRQ_DIRH |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM605_ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 ISOLATOR |  | FRQ_DIRH_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM605_LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_MODE |  | FRQ_DIRH_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM605_LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_RUN |  | FRQ_DIRH_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM606 | DUST EXTRACTION FAN |  | DOL_DIR_BUS |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM606_ISOLATOR | DUST EXTRACTION FAN ISOLATOR |  | DOL_DIR_BUS_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM650 | SLEWING MOTOR FOR SCREW |  | FRQ_REVH |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM650_ISOLATOR | SLEWING MOTOR FOR SCREW ISOLATOR |  | FRQ_REVH_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM650_LOCAL_MODE | SLEWING MOTOR FOR SCREW LOCAL_MODE |  | FRQ_REVH_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM650_LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM650_LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM651 | FUEL SILO DUST FILTER FAN |  | DOL_DIR_BUS |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM651_ISOLATOR | FUEL SILO DUST FILTER FAN ISOLATOR |  | DOL_DIR_BUS_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM652 | ROTATING FUEL SPREADER |  | DOL_DIRH_BUS |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM652_ISOLATOR | ROTATING FUEL SPREADER ISOLATOR |  | DOL_DIRH_BUS_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM652_LOCAL_MODE | ROTATING FUEL SPREADER LOCAL_MODE |  | DOL_DIRH_BUS_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM652_LOCAL_RUN | ROTATING FUEL SPREADER LOCAL_RUN |  | DOL_DIRH_BUS_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM653 | COOLING FAN FUEL FEEDING SCREW 1 |  | DOL_DIR |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM653_FAULT | COOLING FAN FUEL FEEDING SCREW 1 FAULT |  | DOL_DIR_M1 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM653_ISOLATOR | COOLING FAN FUEL FEEDING SCREW 1 ISOLATOR |  | DOL_DIR_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM653_RUN | COOLING FAN FUEL FEEDING SCREW 1 RUN |  | DOL_DIR_M2 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM653_RUNNING | COOLING FAN FUEL FEEDING SCREW 1 RUNNING |  | DOL_DIR_M0 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM654 | LUBRICATION UNIT |  | DOL_DIR |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM654_FAULT | LUBRICATION UNIT FAULT |  | DOL_DIR_M1 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM654_ISOLATOR | LUBRICATION UNIT ISOLATOR |  | DOL_DIR_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM654_RUN | LUBRICATION UNIT RUN |  | DOL_DIR_M2 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM654_RUNNING | LUBRICATION UNIT RUNNING |  | DOL_DIR_M0 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM655 | COOLING FAN FUEL FEEDING SCREW 2 |  | DOL_DIR |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM655_FAULT | COOLING FAN FUEL FEEDING SCREW 2 FAULT |  | DOL_DIR_M1 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM655_ISOLATOR | COOLING FAN FUEL FEEDING SCREW 2 ISOLATOR |  | DOL_DIR_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM655_RUN | COOLING FAN FUEL FEEDING SCREW 2 RUN |  | DOL_DIR_M2 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM655_RUNNING | COOLING FAN FUEL FEEDING SCREW 2 RUNNING |  | DOL_DIR_M0 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM656 | FUEL FEEDING ROTARY VALVE 2 |  | DOL_REVH_BUS |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM656_ISOLATOR | FUEL FEEDING ROTARY VALVE 2 ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM656_LOCAL_MODE | FUEL FEEDING ROTARY VALVE 2 LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM656_LOCAL_RUN_FWD | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ FWD |  | DOL_REVH_BUS_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM656_LOCAL_RUN_REV | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ REV |  | DOL_REVH_BUS_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM657 | FUEL FEEDING ROTARY VALVE 1 |  | DOL_REVH_BUS |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM657_ISOLATOR | FUEL FEEDING ROTARY VALVE 1 ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM657_LOCAL_MODE | FUEL FEEDING ROTARY VALVE 1 LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM657_LOCAL_RUN_FWD | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ FWD |  | DOL_REVH_BUS_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM657_LOCAL_RUN_REV | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ REV |  | DOL_REVH_BUS_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM658 | SCRAPER CONVEYOR 1 |  | FRQ_REVH |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM658_ISOLATOR | SCRAPER CONVEYOR 1 ISOLATOR |  | FRQ_REVH_M3 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM658_LOCAL_MODE | SCRAPER CONVEYOR 1 LOCAL_MODE |  | FRQ_REVH_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM658_LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM658_LOCAL_RUN_REV | SCRAPER CONVEYOR 1 LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM659 | BELT CONVEYOR |  | FRQ_REVH |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM659_ISOLATOR | BELT CONVEYOR ISOLATOR |  | FRQ_REVH_M3 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM659_LOCAL_MODE | BELT CONVEYOR LOCAL_MODE |  | FRQ_REVH_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM659_LOCAL_RUN_FWD | BELT CONVEYOR LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM659_LOCAL_RUN_REV | BELT CONVEYOR LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM660 | COOLING FAN FOR SLEWING MOTOR |  | DOL_DIR |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM660_FAULT | COOLING FAN FOR SLEWING MOTOR FAULT |  | DOL_DIR_M1 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM660_ISOLATOR | COOLING FAN FOR SLEWING MOTOR ISOLATOR |  | DOL_DIR_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM660_RUN | COOLING FAN FOR SLEWING MOTOR RUN |  | DOL_DIR_M2 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM660_RUNNING | COOLING FAN FOR SLEWING MOTOR RUNNING |  | DOL_DIR_M0 |  | 4010 | FUEL FEED | KPA_MCC | KPA_PLC
BB1EM662 | FUEL SILO SCREW DISCHARGE |  | FRQ_REVH |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM662_ISOLATOR | FUEL SILO SCREW DISCHARGE ISOLATOR |  | FRQ_REVH_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM662_LOCAL_MODE | FUEL SILO SCREW DISCHARGE LOCAL_MODE |  | FRQ_REVH_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM662_LOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM662_LOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM663 | FUEL SILO CROSS CONVEYOR |  | FRQ_REVH |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM663_ISOLATOR | FUEL SILO CROSS CONVEYOR ISOLATOR |  | FRQ_REVH_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM663_LOCAL_MODE | FUEL SILO CROSS CONVEYOR LOCAL_MODE |  | FRQ_REVH_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM663_LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM663_LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM664 | FUEL FEEDING SCREW 1 |  | FRQ_REVH |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM664_ISOLATOR | FUEL FEEDING SCREW 1 ISOLATOR |  | FRQ_REVH_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM664_LOCAL_MODE | FUEL FEEDING SCREW 1 LOCAL_MODE |  | FRQ_REVH_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM664_LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM664_LOCAL_RUN_REV | FUEL FEEDING SCREW 1 LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM665 | FUEL FEEDING SCREW 2 |  | FRQ_REVH |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM665_ISOLATOR | FUEL FEEDING SCREW 2 ISOLATOR |  | FRQ_REVH_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM665_LOCAL_MODE | FUEL FEEDING SCREW 2 LOCAL_MODE |  | FRQ_REVH_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM665_LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM665_LOCAL_RUN_REV | FUEL FEEDING SCREW 2 LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1EM670 | BELT MAGNET |  | DOL_DIRH_BUS |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM670_ISOLATOR | BELT MAGNET ISOLATOR |  | DOL_DIRH_BUS_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM670_LOCAL_MODE | BELT MAGNET LOCAL_MODE |  | DOL_DIRH_BUS_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM670_LOCAL_RUN | BELT MAGNET LOCAL_RUN |  | DOL_DIRH_BUS_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM672 | SCRAPER CONVEYOR 2 |  | FRQ_REVH |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM672_ISOLATOR | SCRAPER CONVEYOR 2 ISOLATOR |  | FRQ_REVH_M3 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM672_LOCAL_MODE | SCRAPER CONVEYOR 2 LOCAL_MODE |  | FRQ_REVH_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM672_LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM672_LOCAL_RUN_REV | SCRAPER CONVEYOR 2 LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM673 | LEVELLING ROLLER 1 |  | DOL_REVH_BUS |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM673_ISOLATOR | LEVELLING ROLLER 1 ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM673_LOCAL_MODE | LEVELLING ROLLER 1 LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM673_LOCAL_RUN_FWD | LEVELLING ROLLER 1 LOCAL_RUN_FWD |  | DOL_REVH_BUS_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM673_LOCAL_RUN_REV | LEVELLING ROLLER 1 LOCAL_RUN_REV |  | DOL_REVH_BUS_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM674 | LEVELLING ROLLER 2 |  | DOL_REVH_BUS |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM674_ISOLATOR | LEVELLING ROLLER 2 ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM674_LOCAL_MODE | LEVELLING ROLLER 2 LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM674_LOCAL_RUN_FWD | LEVELLING ROLLER 2 LOCAL_RUN_FWD |  | DOL_REVH_BUS_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM674_LOCAL_RUN_REV | LEVELLING ROLLER 2 LOCAL_RUN_REV |  | DOL_REVH_BUS_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM675 | DISC SCREEN DRIVE 1 |  | FRQ_REVH |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM675_ISOLATOR | DISC SCREEN DRIVE 1 ISOLATOR |  | FRQ_REVH_M3 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM675_LOCAL_MODE | DISC SCREEN DRIVE 1 LOCAL_MODE |  | FRQ_REVH_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM675_LOCAL_RUN_FWD | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM675_LOCAL_RUN_REV | DISC SCREEN DRIVE 1 LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM676 | DISC SCREEN DRIVE 2 |  | FRQ_REVH |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM676_ISOLATOR | DISC SCREEN DRIVE 2 ISOLATOR |  | FRQ_REVH_M3 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM676_LOCAL_MODE | DISC SCREEN DRIVE 2 LOCAL_MODE |  | FRQ_REVH_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM676_LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM676_LOCAL_RUN_REV | DISC SCREEN DRIVE 2 LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1EM703 | CHEMICAL FILLING PUMP 1 |  | DOL_DIRH |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM703_FAULT | CHEMICAL FILLING PUMP 1 FAULT |  | DOL_DIRH_M1 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM703_ISOLATOR | CHEMICAL FILLING PUMP 1 ISOLATOR |  | DOL_DIRH_M5 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM703_LOCAL_MODE | CHEMICAL FILLING PUMP 1 LOCAL_MODE |  | DOL_DIRH_M3 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM703_LOCAL_RUN | CHEMICAL FILLING PUMP 1 LOCAL_RUN |  | DOL_DIRH_M4 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM703_RUN | CHEMICAL FILLING PUMP 1 RUN |  | DOL_DIRH_M2 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM703_RUNNING | CHEMICAL FILLING PUMP 1 RUNNING |  | DOL_DIRH_M0 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM704 | CHEMICAL FILLING PUMP 2 |  | DOL_DIRH |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM704_FAULT | CHEMICAL FILLING PUMP 2 FAULT |  | DOL_DIRH_M1 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM704_ISOLATOR | CHEMICAL FILLING PUMP 2 ISOLATOR |  | DOL_DIRH_M5 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM704_LOCAL_MODE | CHEMICAL FILLING PUMP 2 LOCAL_MODE |  | DOL_DIRH_M3 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM704_LOCAL_RUN | CHEMICAL FILLING PUMP 2 LOCAL_RUN |  | DOL_DIRH_M4 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM704_RUN | CHEMICAL FILLING PUMP 2 RUN |  | DOL_DIRH_M2 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM704_RUNNING | CHEMICAL FILLING PUMP 2 RUNNING |  | DOL_DIRH_M0 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM815 | FLY ASH CONTAINER SCREW |  | DOL_REV_BUS |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1EM815_ISOLATOR | FLY ASH CONTAINER SCREW I SOLATOR |  | DOL_REV_BUS_M0 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1EM850 | 2ND PASS FLY ASH ROTARY VALVE |  | DOL_REVH_BUS |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM850_ISOLATOR | 2ND PASS FLY ASH ROTARY VALVE ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM850_LOCAL_MODE | 2ND PASS FLY ASH ROTARY VALVE LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM850_LOCAL_RUN_FWD | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD |  | DOL_REVH_BUS_M1 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM850_LOCAL_RUN_REV | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV |  | DOL_REVH_BUS_M2 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM851 | 3RD PASS FLY ASH ROTARY VALVE |  | DOL_REVH_BUS |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM851_ISOLATOR | 3RD PASS FLY ASH ROTARY VALVE ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM851_LOCAL_MODE | 3RD PASS FLY ASH ROTARY VALVE LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM851_LOCAL_RUN_FWD | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD |  | DOL_REVH_BUS_M1 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM851_LOCAL_RUN_REV | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV |  | DOL_REVH_BUS_M2 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM852 | BOTTOM ASH CONVEYOR |  | FRQ_REVH |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM852_ISOLATOR | BOTTOM ASH CONVEYOR ISOLATOR |  | FRQ_REVH_M3 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM852_LOCAL_MODE | BOTTOM ASH CONVEYOR LOCAL_MODE |  | FRQ_REVH_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM852_LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD |  | FRQ_REVH_M1 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM852_LOCAL_RUN_REV | BOTTOM ASH CONVEYOR LOCAL_RUN_REV |  | FRQ_REVH_M2 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM855 | ASH CONTAINER SCREW |  | DOL_REV_BUS |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM855_ISOLATOR | ASH CONTAINER SCREW ISOLA TOR |  | DOL_REV_BUS_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM856 | PURIFIED SAND SCREW CONVEYOR |  | DOL_REVH_BUS |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM856_ISOLATOR | PURIFIED SAND SCREW CONVEYOR ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM856_LOCAL_MODE | PURIFIED SAND SCREW CONVEYOR LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM856_LOCAL_RUN_FWD | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ FWD |  | DOL_REVH_BUS_M1 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1EM856_LOCAL_RUN_REV | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ REV |  | DOL_REVH_BUS_M2 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FG300 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC |  | ESP_DI_DO |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_ALARM |  | ESP_DI_DO_M0 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_WARNING |  | ESP_DI_DO_M1 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_EXT_RELEASE_FILTER |  | ESP_DI_DO_M8 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_IN_OPERATION | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_OPERATION |  | ESP_DI_DO_M3 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_IN_STANDBY | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_STANDBY |  | ESP_DI_DO_M2 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI1 |  | ESP_DI_DO_M4 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI2 |  | ESP_DI_DO_M5 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI3 |  | ESP_DI_DO_M6 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI4 |  | ESP_DI_DO_M7 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO1 |  | ESP_DI_DO_M9 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO2 |  | ESP_DI_DO_M10 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO3 |  | ESP_DI_DO_M11 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO4 |  | ESP_DI_DO_M12 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FG300_ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO5 |  | ESP_DI_DO_M13 |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1FL650 | FUEL SILO DUST FILTER CONTROL BOX FEED |  | MCCB_1ph |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1FM001 | BOTTOM ASH SIEVE FEED |  | OESA_3ph |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FM001_ESTOP | BOTTOM ASH SIEVE FEED ESTOP |  | OESA_3ph_M0 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FM001_FAULT | BOTTOM ASH SIEVE FEED THERMAL FAULT |  | OESA_3ph_M3 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FM001_MAN_AUTO | BOTTOM ASH SIEVE FEED MAN/AUTO |  | OESA_3ph_M2 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FM001_RUNNING | BOTTOM ASH SIEVE FEED RUNNING |  | OESA_3ph_M1 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FM001_START_STOP | BOTTOM ASH SIEVE FEED START/STOP |  | OESA_3ph_M5 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FM001_VOLTAGE_OK | BOTTOM ASH SIEVE FEED VOLTAGE OK |  | OESA_3ph_M4 |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FS003 | BOTTOM ASH COOLING FLOW SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FT001 | FEED WATER FLOW AND CONTROL |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1FT200 | HEATING STEAM TO FEED WATER TANK FLOW MEASUREMENT |  | MEAS_ANA |  | 4002 | BOILER WATER AND STEAM | FIELD_IO | KPA_FLOORX_IO
BB1FT201 | STEAM FLOW TO SOOTBLOWING AND AIR PREHEATER |  | MEAS_ANA |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1FT202 | MAIN STEAM FLOW |  | MEAS_ANA |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1FT203 | STEAM TO EXISTING HEADER FLOW MEASUREMENT |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1FT400 | PRIMARY AIR FLOW |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1FT401 | SECONDARY AIR FLOW |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1FT550 | RECIRCULATION GAS FLOW |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1GS001 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS002 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS003 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS004 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS005 | FW TANK OVERFLOW ON-OFF VALVE POSITION |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS006 | FW TANK OVERFLOW ON-OFF VALVE POSITION |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS007 | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH OPEN |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | KPA_PLC | KPA_PLC
BB1GS008 | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH CLOSE |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | KPA_PLC | KPA_PLC
BB1GS009 | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH OPEN |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | KPA_PLC | KPA_PLC
BB1GS010 | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH CLOSE |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | KPA_PLC | KPA_PLC
BB1GS011 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH OPEN |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS012 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH CLOSE |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS020 | EMERGENCY SHOWER USE SWITCH |  | MEAS_BIN |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1GS200 | SOOTBLOWER 1 IN LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS201 | SOOTBLOWER 1 OUT LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS203 | SOOTBLOWER 2 OUT LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS204 | SOOTBLOWER 2 IN LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS205 | SOOTBLOWER 3 OUT LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS206 | SOOTBLOWER 3 IN LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS207 | SOOTBLOWER 5 OUT LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS208 | SOOTBLOWER 5 IN LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS209 | SOOTBLOWER 6 OUT LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS210 | SOOTBLOWER 6 IN LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS211 | SOOTBLOWER 7 OUT LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS212 | SOOTBLOWER 7 IN LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS213 | SOOTBLOWER 8 OUT LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS214 | SOOTBLOWER 8 IN LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1GS215 | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1GS216 | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1GS217 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS217 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS218 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS218 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS219 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS219 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS220 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS220 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS221 | MAIN STEAM VALVE BY-PASS OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4003 | MAIN STEAM | KPA_PLC | KPA_PLC
BB1GS222 | MAIN STEAM VALVE BY-PASS CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4003 | MAIN STEAM | KPA_PLC | KPA_PLC
BB1GS223 | MAIN STEAM LINE VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4003 | MAIN STEAM | KPA_PLC | KPA_PLC
BB1GS224 | MAIN STEAM LINE VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4003 | MAIN STEAM | KPA_PLC | KPA_PLC
BB1GS225 | START-UP LINE ON-OFF VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4003 | MAIN STEAM | KPA_PLC | KPA_PLC
BB1GS226 | START-UP LINE ON-OFF VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4003 | MAIN STEAM | KPA_PLC | KPA_PLC
BB1GS227 | SOOTBLOWING LINE ON-OFF VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | KPA_PLC | KPA_PLC
BB1GS228 | SOOTBLOWING LINE ON-OFF VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4004 | SOOT BLOWERS | KPA_PLC | KPA_PLC
BB1GS230 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1GS231 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1GS232 | STEAM PRESSURE REDUCTION VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS233 | STEAM PRESSURE REDUCTION VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1GS401 | AIR INTAKE GRILL 1 OPENED LIMIT |  | BELIMO_VLV__ |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1GS412 | AIR INTAKE GRILL 2 OPENED LIMIT |  | BELIMO_VLV__ |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1GS413 | AIR INTAKE GRILL 3 OPENED LIMIT |  | BELIMO_VLV__ |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1GS600 | UNLOADING STATION 1, BLOCK 1, FEEDER 1, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS601 | UNLOADING STATION 1, BLOCK 1, FEEDER 1, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS602 | UNLOADING STATION 1, BLOCK 1, FEEDER 2, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS603 | UNLOADING STATION 1, BLOCK 1, FEEDER 2, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS604 | UNLOADING STATION 1, BLOCK 1, FEEDER 3, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS605 | UNLOADING STATION 1, BLOCK 1, FEEDER 3, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS606 | UNLOADING STATION 1, BLOCK 1, FEEDER 4, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS607 | UNLOADING STATION 1, BLOCK 1, FEEDER 4, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS608 | UNLOADING STATION 2, BLOCK 2, FEEDER 1, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS609 | UNLOADING STATION 2, BLOCK 2, FEEDER 1, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS610 | UNLOADING STATION 2, BLOCK 2, FEEDER 2, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS611 | UNLOADING STATION 2, BLOCK 2, FEEDER 2, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS612 | UNLOADING STATION 2, BLOCK 2, FEEDER 3, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS613 | UNLOADING STATION 2, BLOCK 2, FEEDER 3, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS614 | UNLOADING STATION 2, BLOCK 2, FEEDER 4, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS615 | UNLOADING STATION 2, BLOCK 2, FEEDER 4, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS616 | UNLOADING STATION 3, BLOCK 3, FEEDER 1, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS617 | UNLOADING STATION 3, BLOCK 3, FEEDER 1, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS618 | UNLOADING STATION 3, BLOCK 3, FEEDER 2, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS619 | UNLOADING STATION 3, BLOCK 3, FEEDER 2, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS620 | UNLOADING STATION 3, BLOCK 3, FEEDER 3, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS621 | UNLOADING STATION 3, BLOCK 3, FEEDER 3, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS622 | UNLOADING STATION 3, BLOCK 3, FEEDER 4, IN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS623 | UNLOADING STATION 3, BLOCK 3, FEEDER 4, OUT |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS650 | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH BY-PASS POS. |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS651 | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH TO SCREEN |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS652 | EXPLOSION HATCH LIMIT SWITCH 1 |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1GS653 | EXPLOSION HATCH LIMIT SWITCH 2 |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1GS654 | EXPLOSION HATCH LIMIT SWITCH 3 |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1GS655 | EXPLOSION HATCH LIMIT SWITCH 4 |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1GS655 | EXPLOSION HATCH LIMIT SWITCH 4 |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1GS656 | SLIDE GATE VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1GS659 | BELT CONVEYOR DEVIATION DETECTOR 1 |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS660 | BELT CONVEYOR DEVIATION DETECTOR 2 |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS661 | BELT MAGNET DEVIATION DETECTOR 1 |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS662 | BELT MAGNET DEVIATION DETECTOR 2 |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS663 | BELT CONVEYOR OVERSIZE DETECTOR |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1GS800 | SAND FILLING VALVE POSITION CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS801 | SAND FILLING VALVE POSITION OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS802 | BOTTOM ASH VALVE LIMIT SWITCH |  | MEAS_BIN |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1GS803 | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH |  | MEAS_BIN |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1GS850 | BOTTOM ASH SIEVE BYPASS VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS851 | BOTTOM ASH SIEVE BYPASS VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS852 | BOTTOM ASH CONVEYOR BLOCKAGE DETECTOR |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS853 | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS854 | BOTTOM ASH DROPPING CHUTE LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS855 | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS856 | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS857 | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS858 | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1GS859 | BOTTOM ASH TO CONTAINER IN PLACE |  | MEAS_BIN_DETAIL |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1HS101 | BOILER EMERGENCY SHUTDOWN SWITCH 1 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS102 | BOILER EMERGENCY SHUTDOWN SWITCH 2 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS103 | BOILER EMERGENCY SHUTDOWN SWITCH 3 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS104 | BOILER EMERGENCY SHUTDOWN SWITCH 4 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS105 | BOILER EMERGENCY SHUTDOWN SWITCH 5 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS106 | BOILER EMERGENCY SHUTDOWN SWITCH 6 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS107 | BOILER EMERGENCY SHUTDOWN SWITCH 7 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS108 | BOILER EMERGENCY SHUTDOWN SWITCH 8 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS109 | BOILER EMERGENCY SHUTDOWN SWITCH 9 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS110 | BOILER EMERGENCY SHUTDOWN SWITCH 10 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS111 | BOILER EMERGENCY SHUTDOWN SWITCH 11 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS112 | BOILER EMERGENCY SHUTDOWN SWITCH 12 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1HS601 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 1 |  | MEAS_BIN_SRS |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1HS602 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 2 |  | MEAS_BIN_SRS |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1HS603 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 3 |  | MEAS_BIN_SRS |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1HS604 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 4 |  | MEAS_BIN_SRS |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1IJ001 | SCRAPER CONVEYOR 2 ALARM HORN AND LAMP |  | ALM_HORN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FLOORX_IO
BB1IJ002 | SCRAPER CONVEYOR 1 ALARM HORN AND LAMP |  | ALM_HORN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1IJ004 | BOTTOM ASH CONVEYOR ALARM HORN AND LAMP |  | ALM_HORN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IL001 | ALARM HORN AND LIGHT CO ALARM |  | ALM_HORN |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1IV002 | FEEDWATER PUMP 1 ON-OFF VALVE |  | MTR_VLV |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV002_CLOSE | FEEDWATER PUMP 1 ON-OFF VALVE CLOSE |  | MTR_VLV_M1 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV002_CLOSED | FEEDWATER PUMP 1 ON-OFF VALVE CLOSED |  | MTR_VLV_M3 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV002_FAULT | FEEDWATER PUMP 1 ON-OFF VALVE FAULT |  | MTR_VLV_M4 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV002_OPEN | FEEDWATER PUMP 1 ON-OFF VALVE OPEN |  | MTR_VLV_M0 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV002_OPENED | FEEDWATER PUMP 1 ON-OFF VALVE OPENED |  | MTR_VLV_M2 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV002_POSITION | FEEDWATER PUMP 1 ON-OFF VALVE POSITION |  | MTR_VLV_M5 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV003 | FEED WATER PUMP 2 ON-OFF VALVE |  | MTR_VLV |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV003_CLOSE | FEED WATER PUMP 2 ON-OFF VALVE CLOSE |  | MTR_VLV_M1 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV003_CLOSED | FEED WATER PUMP 2 ON-OFF VALVE CLOSED |  | MTR_VLV_M3 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV003_FAULT | FEED WATER PUMP 2 ON-OFF VALVE FAULT |  | MTR_VLV_M4 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV003_OPEN | FEED WATER PUMP 2 ON-OFF VALVE OPEN |  | MTR_VLV_M0 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV003_OPENED | FEED WATER PUMP 2 ON-OFF VALVE OPENED |  | MTR_VLV_M2 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV003_POSITION | FEED WATER PUMP 2 ON-OFF VALVE POSITION |  | MTR_VLV_M5 |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1IV004 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE |  | BIN_VLV |  | 4002 | BOILER WATER AND STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV200 | START-UP CHECK VALVE |  | MTR_VLV |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV200_CLOSE | START-UP CHECK VALVE CLOSE |  | MTR_VLV_M1 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV200_CLOSED | START-UP CHECK VALVE CLOSED |  | MTR_VLV_M3 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV200_FAULT | START-UP CHECK VALVE FAULT |  | MTR_VLV_M4 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV200_OPEN | START-UP CHECK VALVE OPEN |  | MTR_VLV_M0 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV200_OPENED | START-UP CHECK VALVE OPENED |  | MTR_VLV_M2 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV200_POSITION | START-UP CHECK VALVE POSITION |  | MTR_VLV_M5 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV201 | MAIN STEAM VALVE |  | MTR_VLV |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV201_CLOSE | MAIN STEAM VALVE CLOSE |  | MTR_VLV_M1 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV201_CLOSED | MAIN STEAM VALVE CLOSED |  | MTR_VLV_M3 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV201_FAULT | MAIN STEAM VALVE FAULT |  | MTR_VLV_M4 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV201_OPEN | MAIN STEAM VALVE OPEN |  | MTR_VLV_M0 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV201_OPENED | MAIN STEAM VALVE OPENED |  | MTR_VLV_M2 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV201_POSITION | MAIN STEAM VALVE POSITION |  | MTR_VLV_M5 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV202 | MAIN STEAM VALVE BY-PASS VALVE |  | MTR_VLV |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV202_CLOSE | MAIN STEAM VALVE BY-PASS VALVE CLOSE |  | MTR_VLV_M1 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV202_CLOSED | MAIN STEAM VALVE BY-PASS VALVE CLOSED |  | MTR_VLV_M3 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV202_FAULT | MAIN STEAM VALVE BY-PASS VALVE FAULT |  | MTR_VLV_M4 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV202_OPEN | MAIN STEAM VALVE BY-PASS VALVE OPEN |  | MTR_VLV_M0 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV202_OPENED | MAIN STEAM VALVE BY-PASS VALVE OPENED |  | MTR_VLV_M2 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV202_POSITION | MAIN STEAM VALVE BY-PASS VALVE POSITION |  | MTR_VLV_M5 |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1IV203 | SOOTBLOWING LINE ON-OFF VALVE |  | MTR_VLV |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1IV203_CLOSE | SOOTBLOWING LINE ON-OFF VALVE CLOSE |  | MTR_VLV_M1 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1IV203_CLOSED | SOOTBLOWING LINE ON-OFF VALVE CLOSED |  | MTR_VLV_M3 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1IV203_FAULT | SOOTBLOWING LINE ON-OFF VALVE FAULT |  | MTR_VLV_M4 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1IV203_OPEN | SOOTBLOWING LINE ON-OFF VALVE OPEN |  | MTR_VLV_M0 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1IV203_OPENED | SOOTBLOWING LINE ON-OFF VALVE OPENED |  | MTR_VLV_M2 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1IV203_POSITION | SOOTBLOWING LINE ON-OFF VALVE POSITION |  | MTR_VLV_M5 |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1IV204 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE |  | MTR_VLV |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV204_CLOSE | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE |  | MTR_VLV_M1 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV204_CLOSED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSED |  | MTR_VLV_M3 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV204_FAULT | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE FAULT |  | MTR_VLV_M4 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV204_OPEN | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN |  | MTR_VLV_M0 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV204_OPENED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPENED |  | MTR_VLV_M2 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV204_POSITION | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE POSITION |  | MTR_VLV_M5 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV205 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE |  | MTR_VLV |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV205_CLOSE | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE |  | MTR_VLV_M1 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV205_CLOSED | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSED |  | MTR_VLV_M3 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV205_FAULT | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE FAULT |  | MTR_VLV_M4 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV205_OPEN | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN |  | MTR_VLV_M0 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV205_OPENED | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPENED |  | MTR_VLV_M2 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV205_POSITION | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE POSITION |  | MTR_VLV_M5 |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1IV206 | PRIMARY AIR PREHEATER ON-OFF VALVE |  | MTR_VLV |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1IV206_CLOSE | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE |  | MTR_VLV_M1 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1IV206_CLOSED | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSED |  | MTR_VLV_M3 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1IV206_FAULT | PRIMARY AIR PREHEATER ON-OFF VALVE FAULT |  | MTR_VLV_M4 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1IV206_OPEN | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN |  | MTR_VLV_M0 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1IV206_OPENED | PRIMARY AIR PREHEATER ON-OFF VALVE OPENED |  | MTR_VLV_M2 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1IV206_POSITION | PRIMARY AIR PREHEATER ON-OFF VALVE POSITION |  | MTR_VLV_M5 |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1IV650 | SLIDE GATE VALVE |  | DOL_REVH_BUS |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1IV650_ISOLATOR | SLIDE GATE VALVE ISOLATOR |  | DOL_REVH_BUS_M3 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1IV650_LOCAL_MODE | SLIDE GATE VALVE LOCAL_MODE |  | DOL_REVH_BUS_M0 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1IV650_LOCAL_RUN_FWD | SLIDE GATE VALVE LOCAL_RUN_FWD |  | DOL_REVH_BUS_M1 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1IV650_LOCAL_RUN_REV | SLIDE GATE VALVE LOCAL_RUN_REV |  | DOL_REVH_BUS_M2 |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LS103 | STEAM DRUM LEVEL SWITCH 1 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1LS104 | STEAM DRUM LEVEL SWITCH 2 |  | MEAS_BIN_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1LS600 | HYDRAULICS UNIT 1, LEAKING POOL LIMIT SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS608 | HYDRAULICS UNIT 1, LOW OIL LEVEL ALARM |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS650 | SCRAPER CONVEYOR 1 BED HEIGHT LEVEL SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS651 | UNLOADING STATION 3, BLOCK 3, BLOCKAGE GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS652 | UNLOADING STATION 2, BLOCK 2, BLOCKAGE GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS653 | UNLOADING STATION 1, BLOCK 1, BLOCKAGE GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS654 | SCRAPER CONVEYOR 1, BLOCKAGE GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS655 | SCRAPER CONVEYOR 2, TURNING POINT BLOCKAGE GU ARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS656 | SCRAPER CONVEYOR 2, FUEL SILO SIDE BLOCKAGE GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1LS657 | FUEL SILO DISCHARGE SCREW BLOCKAGE SWITCH |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LS658 | FUEL SILO CROSS CONVEYOR BLOCKAGE SWITCH |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LS659 | FUEL FEEDING SCREW 1 BLOCKAGE SWITCH |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LS660 | FUEL FEEDING SCREW 2 BLOCKAGE SWITCH |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LS661 | LUBRICATION ALARM SCREW DISCHARGER |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LS700 | CHEMICAL TANK 1 LEVEL SWITCH |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1LS701 | CHEMICAL TANK 2 LEVEL SWITCH |  | MEAS_BIN |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1LS850 | BOTTOM ASH CONTAINER LEVEL SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1LS851 | BOTTOM ASH CONTAINER LEVEL SWITCH |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1LS852 | FLY ASH CONTAINER LEVEL SWITCH |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1LT001 | FEED WATER TANK LEVEL 1 |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1LT002 | FEED WATER TANK LEVEL 2 |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1LT003 | STEAM ACCUMULATOR LEVEL 1 |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1LT004 | STEAM ACCUMULATOR LEVEL 2 |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1LT101 | STEAM DRUM LEVEL 1 |  | MEAS_ANA_SRS |  | 4002 | BOILER WATER AND STEAM | FIELD_IO | KPA_FLOORX_IO
BB1LT102 | STEAM DRUM LEVEL 2 |  | MEAS_ANA_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1LT103 | STEAM DRUM LEVEL 3 |  | MEAS_ANA_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1LT611 | UNLOADING STATION 1 LEVEL |  | MEAS_ANA |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FLOORX_IO
BB1LT612 | UNLOADING STATION 3 LEVEL |  | MEAS_ANA |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FLOORX_IO
BB1LT613 | UNLOADING STATION 2 LEVEL |  | MEAS_ANA |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FLOORX_IO
BB1LT650 | FUEL SILO LEVEL RADAR 1 |  | MEAS_ANA_240V |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LT651 | FUEL SILO LEVEL RADAR 2 |  | MEAS_ANA_240V |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LT652 | FUEL POCKET LEVEL |  | MEAS_ANA_240V |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1LT800 | RECYCLED BED MATERIAL HOPPER LEVEL SWITCH |  | MEAS_ANA_DETAIL |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1LT802 | SAND SILO LEVEL MEASUREMENT |  | MEAS_ANA |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PS600 | HYDRAULICS UNIT 1, BLOCK 1, PRESSURE SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1PS601 | HYDRAULICS UNIT 1, BLOCK 2, PRESSURE SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1PS602 | HYDRAULICS UNIT 1, BLOCK 3, PRESSURE SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1PS603 | HYDRAULIC OIL RETURN BLOCK 1 FILTER PRESSURE SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1PS604 | HYDRAULIC OIL RETURN BLOCK 2 FILTER PRESSURE SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1PS605 | HYDRAULIC OIL RETURN BLOCK 3 FILTER PRESSURE SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1PT001 | FEED WATER PUMP 1 PRESSURE SIDE PRESSURE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PT002 | FEED WATER PUMP 2 PRESSURE SIDE PRESSURE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PT004 | FEED WATER PRESSURE BEFORE VALVE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PT005 | FEED WATER PRESSURE AFTER VALVE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PT006 | FW SUCTION LINE STRAINER PRESSURE DIFF. |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PT007 | FW SUCTION LINE STRAINER PRESSURE DIFF. |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PT009 | COOLING WATER PRESSURE BEFORE PUMP |  | MEAS_ANA |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PT200 | FEED WATER TANK PRESSURE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PT201 | STEAM DRUM PRESSURE 1 |  | MEAS_ANA_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1PT203 | STEAM DRUM PRESSURE 2 |  | MEAS_ANA_SRS |  | 4002 | BOILER WATER AND STEAM | KPA_PLC | KPA_PLC
BB1PT204 | MAIN STEAM PRESSURE |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1PT205 | STEAM OUTLET PRESSURE FROM ACCUMULATOR |  | MEAS_ANA_SRS |  | 4006 | STEAM ACCUMULATOR | KPA_PLC | KPA_PLC
BB1PT207 | ACCUMULATOR PRESSURE |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1PT208 | ACCUMULATOR PRESSURE |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1PT400 | PRIMARY AIR PRESSURE |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1PT401 | SECONDARY AIR PRESSURE |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1PT402 | INSTRUMENT AIR PRESSURE AFTER DRYER |  | MEAS_ANA |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1PT403 | SECONDARY AIR PRESSURE INNER BACK WALL |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1PT404 | BOILER UPPER PART PRESSURE 1 |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1PT405 | BOILER UPPER PART PRESSURE 2 |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1PT406 | BOILER UPPER PART PRESSURE |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1PT407 | TERTIARY AIR PRESSURE RIGHT WALL |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1PT408 | TERTIARY AIR PRESSURE LEFT WALL |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1PT409 | SECONDARY AIR PRESSURE OUTER FRONT WALL |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1PT410 | SECONDARY AIR PRESSURE INNER FRONT WALL |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1PT411 | SECONDARY AIR PRESSURE OUTER BACK WALL |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1PT478 | INSTRUMENT AIR PRESSURE |  | MEAS_ANA |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1PT550 | FLUE GAS PRESSURE AT THE OUTLET OF THE BOILER |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1PT552 | ESP INLET PRESSURE TRANSMITTER |  | MEAS_ANA_DETAIL |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1PT553 | ESP OUTLET PRESSURE TRANSMITTER |  | MEAS_ANA_DETAIL |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1PT800 | RECYCLED BED MATERIAL DAMPER PRESSURE SWITCH |  | MEAS_BIN_DETAIL |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PU800 | CHEMICAL DOSING PUMP 1 |  | CHEMICAL_PUMP |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1PU801 | CHEMICAL DOSING PUMP 2 |  | CHEMICAL_PUMP |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1QT001 | CONDUCTIVITY MEASUREMENT FROM FEED WATER TANK |  | MEAS_ANA |  | 4007 | SAMPLING | FIELD_IO | KPA_FLOORX_IO
BB1QT002 | PH MEASUREMENT FROM FEED WATER TANK |  | MEAS_ANA |  | 4007 | SAMPLING | FIELD_IO | KPA_FLOORX_IO
BB1QT003 | CONDUCTIVITY MEASUREMENT FROM CONDENSATE |  | MEAS_ANA |  | 4007 | SAMPLING | FIELD_IO | KPA_FLOORX_IO
BB1QT004 | CONDUCTIVITY MEASUREMENT FROM BOILER WATER |  | MEAS_ANA |  | 4007 | SAMPLING | FIELD_IO | KPA_FLOORX_IO
BB1QT005 | CONDUCTIVITY MEASUREMENT FROM SATURATED STEAM |  | MEAS_ANA |  | 4007 | SAMPLING | FIELD_IO | KPA_FLOORX_IO
BB1QT006 | CONDUCTIVITY MEASUREMENT FROM MAIN STEAM |  | MEAS_ANA |  | 4007 | SAMPLING | FIELD_IO | KPA_FLOORX_IO
BB1QT007 | CONDUCTIVITY MEASUREMENT FROM FEED WATER LINE |  | MEAS_ANA |  | 4007 | SAMPLING | FIELD_IO | KPA_FLOORX_IO
BB1QT550 | FLUEGAS OXYGEN MEASUREMENT 1 |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1QT551 | FLUEGAS OXYGEN MEASUREMENT 2 |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1QT552 | FLUEGAS CO MEASUREMENT |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1QT553 | BOILER ROOM GAS DETECTOR |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1QT554 | OPACITY AFTER ESP |  | MEAS_ANA |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1SI400 | PRIMARY AIR FAN SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1SI401 | SECONDARY AIR FAN SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1SI550 | FLUE GAS FAN SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1SI603 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1SI604 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1SI605 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1SI658 | SCRAPER CONVEYOR 1 SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1SI659 | BELT CONVEYOR SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1SI672 | SCRAPER CONVEYOR 2 SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1SI675 | DISC SCREEN DRIVE 1 SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1SI676 | DISC SCREEN DRIVE 2 SAFETY INTERLOCK |  | FAN_SRS_DO |  | 4009 | FUEL RECEPTION | KPA_PLC | KPA_PLC
BB1ST649 | FUEL SILO CROSS CONVEYOR ROTATION GUARD |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1ST650 | SCRAPER CONVEYOR 1, ROTATION GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST651 | SCRAPER CONVEYOR 2, ROTATION GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST652 | BELT CONVEYOR ROTATION GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST652 | BELT CONVEYOR ROTATION GUARD |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1ST653 | FUEL FEEDING SCREW 2 ROTATION GUARD |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1ST654 | BELT MAGNET ROTATION GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST654 | BELT MAGNET ROTATION GUARD |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1ST655 | FUEL FEEDING ROTARY FEEDER 2 ROTATION GUARD |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1ST656 | DISC SCREEN DRIVE 1 ROTATION GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST657 | DISC SCREEN DRIVE 2 ROTATION GUARD |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST659 | FUEL FEEDING SCREW 1 ROTATION GUARD |  | MEAS_BIN |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1ST673 | LEVELING ROLLER 1 SPEED SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST674 | LEVELING ROLLER 2 SPEED SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST675 | LEVELING ROLLER 3 SPEED SWITCH |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1ST804 | ESP ROTARY VALVE ROTATION GUARD |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | ESP_PLC | ESP_PLC
BB1ST805 | HEATED ESP COLLECTION SCREW ROTATION GUARD |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | ESP_PLC | ESP_PLC
BB1ST808 | ESP HOPPER 2 SCREW ROTATION GUARD |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | ESP_PLC | ESP_PLC
BB1ST809 | ESP HOPPER 1 SCREW ROTATION GUARD |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | ESP_PLC | ESP_PLC
BB1ST850 | BOTTOM ASH CONVEYOR ROTATION GUARD |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1ST852 | 2ND PASS FLY ASH ROTARY VALVE ROTATION GUARD |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1ST853 | 3RD PASS FLY ASH ROTARY VALVE ROTATION GUARD |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1ST856 | PURIFIED SAND SCREW CONVEYOR ROTATION GUARD |  | MEAS_BIN |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1SV001 | BLOW DOWN TANK COOLING ON/OFF VALVE |  | BIN_VLV |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1SV400 | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE |  | BIN_VLV |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1SV401 | BOTTOM ASH PURGING AIR SOLENOID VALVE |  | BIN_VLV |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1SV402 | BOTTOM ASH PURGING AIR SOLENOID VALVE |  | BIN_VLV |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1SV405 | SAND FILLING VALVE SOLENOID VALVE |  | BIN_VLV |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1SV406 | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE |  | BIN_VLV |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1SV410 | FEED WATER TANK OVERFLOW VALVE |  | BIN_VLV |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1SV601 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 |  | PUSH_FEED |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV601_IN | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 |  | PUSH_FEED_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV601_OUT | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1 |  | PUSH_FEED_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV602 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 |  | PUSH_FEED |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV602_IN | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 |  | PUSH_FEED_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV602_OUT | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2 |  | PUSH_FEED_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV603 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 |  | PUSH_FEED |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV603_IN | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 |  | PUSH_FEED_M1 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV603_OUT | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3 |  | PUSH_FEED_M0 |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1SV950 | FUEL SILO FIRE WATER CONTROL VALVE |  | BIN_VLV |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1SV951 | FUEL POCKET FIRE WATER CONTROL VALVE |  | BIN_VLV |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1TS501 | ESP INSULATOR 1 TEMPERATURE |  | MEAS_ANA_DETAIL |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TS508 | ESP INSULATOR 2 TEMPERATURE |  | MEAS_ANA_DETAIL |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TS600 | HYDRAULICS UNIT, THERMOSTAT FOR HEATER |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1TS608 | HIGH TEMPERATURE SWITCH HYDRAULIC OIL |  | MEAS_BIN |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FUEL_STATION_IO
BB1TS804 | ESP ROTARY VALVE HEATING THERMOSTAT |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | ESP_PLC | ESP_PLC
BB1TS805 | ESP COLLECTION SCREW HEATING THERMOSTAT |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | ESP_PLC | ESP_PLC
BB1TS808 | ESP ASH HOPPER 2 OVERHEAT THERMOSTAT |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | ESP_PLC | ESP_PLC
BB1TS809 | ESP ASH HOPPER 1 OVERHEAT THERMOSTAT |  | MEAS_BIN_DETAIL |  | 4011 | FLUE GAS CLEANING | ESP_PLC | ESP_PLC
BB1TT001 | FEED WATER TEMPERATURE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1TT002 | FEED WATER PUMP 2 BEARING TEMPERATURE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1TT003 | FW PUMP 1 MOTOR BEARING TEMPERATURE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1TT004 | FW PUMP 1 MOTOR WINDING TEMPERATURE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1TT005 | FW PUMP 2 MOTOR WINDING TEMPERATURE |  | MEAS_ANA |  | 4001 | FEED WATER SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1TT006 | BLOW DOWN TANK TEMPERATURE AND CONTROL |  | MEAS_ANA |  | 4005 | BLOWN DOWN SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1TT007 | ACCUMULATOR TEMPERATURE |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1TT008 | TEMPERATURE AFTER ECONOMIZER |  | MEAS_ANA |  | 4002 | BOILER WATER AND STEAM | FIELD_IO | KPA_FLOORX_IO
BB1TT009 | TEMPERATURE BEFORE ECONOMIZER |  | MEAS_ANA |  | 4002 | BOILER WATER AND STEAM | FIELD_IO | KPA_FLOORX_IO
BB1TT012 | CONDENSATE TEMPERATURE FROM PRIMARY AIR PREHEATE R |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT031 | COOLING WATER TEMPERATURE AFTER BOTTOM ASH CONVEYOR |  | MEAS_ANA |  | 4012 | BOTTOM ASH AND SAND SYSTEM | FIELD_IO | KPA_FLOORX_IO
BB1TT116 | STEAM TEMPERATURE TO AIR PREHEATER |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT200 | MAIN STEAM TEMPERATURE |  | MEAS_ANA |  | 4003 | MAIN STEAM | FIELD_IO | KPA_FLOORX_IO
BB1TT201 | SOOTBLOWING LINE TEMPERATURE |  | MEAS_ANA |  | 4004 | SOOT BLOWERS | FIELD_IO | KPA_FLOORX_IO
BB1TT202 | STEAM OUTLET TEMPERATURE FROM ACCUMULATOR |  | MEAS_ANA |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1TT203 | 18BAR(G) STEAM TEMPERATURE |  | MEAS_ANA_DETAIL |  | 4006 | STEAM ACCUMULATOR | FIELD_IO | KPA_FLOORX_IO
BB1TT308 | FURNACE TEMPERATURE CONNECTION |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT400 | PRIMARY AIR TEMPERATURE BEFORE PREHEATER |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT401 | BOILER ROOM UPPER PART TEMPERATURE |  | MEAS_ANA |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1TT402 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 1 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT403 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 2 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT404 | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 1 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT405 | PRIMARY AIR TEMPERATURE |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT406 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 1 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT407 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 2 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT408 | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 1 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT409 | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 2 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT410 | BOILER 1ST DRAFT TEMPERATURE |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT411 | BOILER TEMPERATURE AFTER EMPTY DRAFT 1 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT412 | BOILER TEMPERATURE AFTER EMPTY DRAFT 2 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT413 | BED TEMPERATURE 1 |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1TT414 | BED TEMPERATURE 2 |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1TT415 | BOILER BED TEMPERATURE MIDDLE LEVEL |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT416 | BOILER BED TEMPERATURE LOWER LEVEL |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT417 | BED TEMPERATURE 3 |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1TT418 | BED TEMPERATURE 4 |  | MEAS_ANA_SRS |  | 4008 | BOILER AIR AND FLUE GAS | KPA_PLC | KPA_PLC
BB1TT421 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 3 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT422 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 3 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT423 | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 2 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT430 | INSTRUMENT AIR TANK TEMPERATURE |  | MEAS_ANA |  | 4014 | COMPRESSED AIR AND WATER DISTRIBUTION | FIELD_IO | KPA_FLOORX_IO
BB1TT550 | FLUE GAS TEMPERATURE 1 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT551 | FLUE GAS TEMPERATURE 2 |  | MEAS_ANA |  | 4008 | BOILER AIR AND FLUE GAS | FIELD_IO | KPA_FLOORX_IO
BB1TT552 | FLUE GAS TEMPERATURE BEFORE ESP |  | MEAS_ANA_DETAIL |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TT553 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 1 |  | MEAS_ANA |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TT554 | FLUE GAS FAN BEARING TEMPERATURE |  | MEAS_ANA |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TT555 | FLUE GAS FAN BEARING TEMPERATURE |  | MEAS_ANA |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TT556 | FLUE GAS TEMPERATURE BEFORE STACK |  | MEAS_ANA |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TT557 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 2 |  | MEAS_ANA |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TT558 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 3 |  | MEAS_ANA |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TT650 | SCRAPER CONVEYOR 1 TEMPERATURE MEASUREMENT |  | MEAS_ANA |  | 4009 | FUEL RECEPTION | FIELD_IO | KPA_FLOORX_IO
BB1TT652 | FUEL SILO TEMPERATURE MEASUREMENT |  | MEAS_ANA |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1TT653 | FUEL POCKET TEMPERATURE |  | MEAS_ANA |  | 4010 | FUEL FEED | FIELD_IO | KPA_FLOORX_IO
BB1TT850 | ESP ASH HOPPER 1 TEMPERATURE |  | MEAS_ANA_DETAIL |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
BB1TT851 | ESP ASH HOPPER 2 TEMPERATURE |  | MEAS_ANA_DETAIL |  | 4011 | FLUE GAS CLEANING | FIELD_IO | KPA_FLOORX_IO
| <ERROR> |  |  |  |  | <ERROR>

## _DEVICE_TAGS
DEVICE_TAGS
INITIAL_TAG1 | INITIAL_TAG2 | INITIAL_DESC | x1 | TAG1 | DESC1 | DESC2 | DESC3 | x2 | TAG2 | LDESC
BB1IL001 |  | Alarm horn and light CO alarm |  | BB1IL001 | ALARM HORN AND LIGHT | CO ALARM |  |  | BB1IL001 | ALARM HORN AND LIGHT CO ALARM
BB1IJ002 |  | Scraper Conveyor 1 Alarm horn and lamp |  | BB1IJ002 | SCRAPER CONVEYOR 1 | ALARM HORN AND LAMP |  |  | BB1IJ002 | SCRAPER CONVEYOR 1 ALARM HORN AND LAMP
BB1IJ001 |  | Scraper Conveyor 2 Alarm horn and lamp |  | BB1IJ001 | SCRAPER CONVEYOR 2 | ALARM HORN AND LAMP |  |  | BB1IJ001 | SCRAPER CONVEYOR 2 ALARM HORN AND LAMP
BB1IJ004 |  | Bottom ash conveyor Alarm horn and lamp |  | BB1IJ004 | BOTTOM ASH CONVEYOR | ALARM HORN AND LAMP |  |  | BB1IJ004 | BOTTOM ASH CONVEYOR ALARM HORN AND LAMP
BB1EM405 |  | Air intake grill 1 OPEN |  | BB1EM405 | AIR INTAKE GRILL 1 | OPEN |  |  | BB1EM405 | AIR INTAKE GRILL 1 OPEN
BB1GS401 |  | Air intake grill 1 OPENED LIMIT |  | BB1GS401 | AIR INTAKE GRILL 1 | OPENED LIMIT |  |  | BB1GS401 | AIR INTAKE GRILL 1 OPENED LIMIT
BB1EM406 |  | Air intake grill 2 OPEN |  | BB1EM406 | AIR INTAKE GRILL 2 | OPEN |  |  | BB1EM406 | AIR INTAKE GRILL 2 OPEN
BB1GS412 |  | Air intake grill 2 OPENED LIMIT |  | BB1GS412 | AIR INTAKE GRILL 2 | OPENED LIMIT |  |  | BB1GS412 | AIR INTAKE GRILL 2 OPENED LIMIT
BB1EM407 |  | Air intake grill 3 OPEN |  | BB1EM407 | AIR INTAKE GRILL 3 | OPEN |  |  | BB1EM407 | AIR INTAKE GRILL 3 OPEN
BB1GS413 |  | Air intake grill 3 OPENED LIMIT |  | BB1GS413 | AIR INTAKE GRILL 3 | OPENED LIMIT |  |  | BB1GS413 | AIR INTAKE GRILL 3 OPENED LIMIT
BB1SV410 |  | Feed water tank overflow valve |  | BB1SV410 | FEED WATER TANK | OVERFLOW VALVE |  |  | BB1SV410 | FEED WATER TANK OVERFLOW VALVE
BB1IV004 |  | Boiler bottom blow down on-off valve |  | BB1IV004 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE |  |  | BB1IV004 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE
BB1SV001 |  | Blow down tank cooling on/off valve |  | BB1SV001 | BLOW DOWN TANK COOLING | ON/OFF VALVE |  |  | BB1SV001 | BLOW DOWN TANK COOLING ON/OFF VALVE
BB1SV400 |  | Sealing air to rotary feeder solenoid valve |  | BB1SV400 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  |  | BB1SV400 | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE
BB1SV406 |  | Sealing air to rotary feeder solenoid valve |  | BB1SV406 | SEALING AIR TO ROTARY | FEEDER SOLENOID VALVE |  |  | BB1SV406 | SEALING AIR TO ROTARY FEEDER SOLENOID VALVE
BB1SV950 |  | Fuel silo fire water control valve |  | BB1SV950 | FUEL SILO FIRE WATER | CONTROL VALVE |  |  | BB1SV950 | FUEL SILO FIRE WATER CONTROL VALVE
BB1SV951 |  | Fuel pocket fire water control valve |  | BB1SV951 | FUEL POCKET FIRE WATER | CONTROL VALVE |  |  | BB1SV951 | FUEL POCKET FIRE WATER CONTROL VALVE
BB1CV405 |  | Bottom ash valve solenoid valve |  | BB1CV405 | BOTTOM ASH VALVE | SOLENOID VALVE |  |  | BB1CV405 | BOTTOM ASH VALVE SOLENOID VALVE
BB1CV406 |  | Bottom ash valve solenoid valve |  | BB1CV406 | BOTTOM ASH VALVE | SOLENOID VALVE |  |  | BB1CV406 | BOTTOM ASH VALVE SOLENOID VALVE
BB1CV412 |  | Bottom ash sieve bypass solenoid valve |  | BB1CV412 | BOTTOM ASH SIEVE BYPASS | SOLENOID VALVE |  |  | BB1CV412 | BOTTOM ASH SIEVE BYPASS SOLENOID VALVE
BB1CV414 |  | Work air to pneumatic transmitter pneumatic valve |  | BB1CV414 | WORK AIR TO PNEUMATIC | TRANSMITTER PNEUMATIC VAL | VE |  | BB1CV414 | WORK AIR TO PNEUMATIC TRANSMITTER PNEUMATIC VAL VE
BB1SV405 |  | Sand filling valve solenoid valve |  | BB1SV405 | SAND FILLING VALVE | SOLENOID VALVE |  |  | BB1SV405 | SAND FILLING VALVE SOLENOID VALVE
BB1SV401 |  | Bottom ash purging air solenoid valve |  | BB1SV401 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  |  | BB1SV401 | BOTTOM ASH PURGING AIR SOLENOID VALVE
BB1SV402 |  | Bottom ash purging air solenoid valve |  | BB1SV402 | BOTTOM ASH PURGING AIR | SOLENOID VALVE |  |  | BB1SV402 | BOTTOM ASH PURGING AIR SOLENOID VALVE
BB1CV413 |  | Control valve of pneumatic transmitter damper |  | BB1CV413 | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER |  | BB1CV413 | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER
BB1CV413 | _OPEN | Control valve of pneumatic transmitter damper OPEN |  | BB1CV413_OPEN | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER OPEN |  | BB1CV413_OPEN | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER OPEN
BB1CV413 | _CLOSE | Control valve of pneumatic transmitter damper CLOSE |  | BB1CV413_CLOSE | CONTROL VALVE OF | PNEUMATIC TRANSMITTER | DAMPER CLOSE |  | BB1CV413_CLOSE | CONTROL VALVE OF PNEUMATIC TRANSMITTER DAMPER CLOSE
BB1BU500 |  | Burner signals |  | BB1BU500 | BURNER SIGNALS |  |  |  | BB1BU500 | BURNER SIGNALS
BB1BU500 | _DO_IF1 | BURNER DIGITAL OUTPUT INTERFACE 1 |  | BB1BU500_DO_IF1 | BURNER DIGITAL OUTPUT | INTERFACE 1 |  |  | BB1BU500_DO_IF1 | BURNER DIGITAL OUTPUT INTERFACE 1
BB1BU500 | _DO_IF2 | BURNER DIGITAL OUTPUT INTERFACE 2 |  | BB1BU500_DO_IF2 | BURNER DIGITAL OUTPUT | INTERFACE 2 |  |  | BB1BU500_DO_IF2 | BURNER DIGITAL OUTPUT INTERFACE 2
BB1BU500 | _DO_IF3 | BURNER DIGITAL OUTPUT INTERFACE 3 |  | BB1BU500_DO_IF3 | BURNER DIGITAL OUTPUT | INTERFACE 3 |  |  | BB1BU500_DO_IF3 | BURNER DIGITAL OUTPUT INTERFACE 3
BB1BU500 | _DO_IF4 | BURNER DIGITAL OUTPUT INTERFACE 4 |  | BB1BU500_DO_IF4 | BURNER DIGITAL OUTPUT | INTERFACE 4 |  |  | BB1BU500_DO_IF4 | BURNER DIGITAL OUTPUT INTERFACE 4
BB1BU500 | _DO_IF5 | BURNER DIGITAL OUTPUT INTERFACE 5 |  | BB1BU500_DO_IF5 | BURNER DIGITAL OUTPUT | INTERFACE 5 |  |  | BB1BU500_DO_IF5 | BURNER DIGITAL OUTPUT INTERFACE 5
BB1BU500 | _DI_IF1 | BURNER DIGITAL INPUT INTERFACE 1 |  | BB1BU500_DI_IF1 | BURNER DIGITAL INPUT | INTERFACE 1 |  |  | BB1BU500_DI_IF1 | BURNER DIGITAL INPUT INTERFACE 1
BB1BU500 | _DI_IF2 | BURNER DIGITAL INPUT INTERFACE 2 |  | BB1BU500_DI_IF2 | BURNER DIGITAL INPUT | INTERFACE 2 |  |  | BB1BU500_DI_IF2 | BURNER DIGITAL INPUT INTERFACE 2
BB1BU500 | _DI_IF3 | BURNER DIGITAL INPUT INTERFACE 3 |  | BB1BU500_DI_IF3 | BURNER DIGITAL INPUT | INTERFACE 3 |  |  | BB1BU500_DI_IF3 | BURNER DIGITAL INPUT INTERFACE 3
BB1BU500 | _DI_IF4 | BURNER DIGITAL INPUT INTERFACE 4 |  | BB1BU500_DI_IF4 | BURNER DIGITAL INPUT | INTERFACE 4 |  |  | BB1BU500_DI_IF4 | BURNER DIGITAL INPUT INTERFACE 4
BB1BU500 | _DI_IF5 | BURNER DIGITAL INPUT INTERFACE 5 |  | BB1BU500_DI_IF5 | BURNER DIGITAL INPUT | INTERFACE 5 |  |  | BB1BU500_DI_IF5 | BURNER DIGITAL INPUT INTERFACE 5
BB1BU500 | _AO_IF1 | BURNER ANALOGUE OUTPUT INTERFACE 1 |  | BB1BU500_AO_IF1 | BURNER ANALOGUE OUTPUT | INTERFACE 1 |  |  | BB1BU500_AO_IF1 | BURNER ANALOGUE OUTPUT INTERFACE 1
BB1BU500 | _AO_IF2 | BURNER ANALOGUE OUTPUT INTERFACE 2 |  | BB1BU500_AO_IF2 | BURNER ANALOGUE OUTPUT | INTERFACE 2 |  |  | BB1BU500_AO_IF2 | BURNER ANALOGUE OUTPUT INTERFACE 2
BB1BU500 | _AI_IF1 | BURNER ANALOGUE INPUT INTERFACE 1 |  | BB1BU500_AI_IF1 | BURNER ANALOGUE INPUT | INTERFACE 1 |  |  | BB1BU500_AI_IF1 | BURNER ANALOGUE INPUT INTERFACE 1
BB1BU500 | _AI_IF2 | BURNER ANALOGUE INPUT INTERFACE 2 |  | BB1BU500_AI_IF2 | BURNER ANALOGUE INPUT | INTERFACE 2 |  |  | BB1BU500_AI_IF2 | BURNER ANALOGUE INPUT INTERFACE 2
BB1PU800 |  | Chemical dosing pump 1 |  | BB1PU800 | CHEMICAL DOSING PUMP 1 |  |  |  | BB1PU800 | CHEMICAL DOSING PUMP 1
BB1PU801 |  | Chemical dosing pump 2 |  | BB1PU801 | CHEMICAL DOSING PUMP 2 |  |  |  | BB1PU801 | CHEMICAL DOSING PUMP 2
BB1EM402 |  | Compressor 1 |  | BB1EM402 | COMPRESSOR 1 |  |  |  | BB1EM402 | COMPRESSOR 1
BB1EM402 | _FAULT_DI | Compressor 1 Fault |  | BB1EM402_FAULT_DI | COMPRESSOR 1 | FAULT |  |  | BB1EM402_FAULT_DI | COMPRESSOR 1 FAULT
BB1EM402 | _RUNNING_DI | Compressor 1 Running |  | BB1EM402_RUNNING_DI | COMPRESSOR 1 | RUNNING |  |  | BB1EM402_RUNNING_DI | COMPRESSOR 1 RUNNING
BB1EM402 | _RESERVE_DI | Compressor 1 reserve |  | BB1EM402_RESERVE_DI | COMPRESSOR 1 | RESERVE |  |  | BB1EM402_RESERVE_DI | COMPRESSOR 1 RESERVE
BB1EM402 | _RUN_DO | Compressor 1 remote run |  | BB1EM402_RUN_DO | COMPRESSOR 1 | REMOTE RUN |  |  | BB1EM402_RUN_DO | COMPRESSOR 1 REMOTE RUN
BB1EM402 | _FAULT_ACK_DO | Compressor 1 Fault Acknowledge |  | BB1EM402_FAULT_ACK_DO | COMPRESSOR 1 | FAULT ACKNOWLEDGE |  |  | BB1EM402_FAULT_ACK_DO | COMPRESSOR 1 FAULT ACKNOWLEDGE
BB1EM403 |  | Compressor 2 |  | BB1EM403 | COMPRESSOR 2 |  |  |  | BB1EM403 | COMPRESSOR 2
BB1EM403 | _FAULT_DI | Compressor 2 Fault |  | BB1EM403_FAULT_DI | COMPRESSOR 2 | FAULT |  |  | BB1EM403_FAULT_DI | COMPRESSOR 2 FAULT
BB1EM403 | _RUNNING_DI | Compressor 2 Running |  | BB1EM403_RUNNING_DI | COMPRESSOR 2 | RUNNING |  |  | BB1EM403_RUNNING_DI | COMPRESSOR 2 RUNNING
BB1EM403 | _RESERVE_DI | Compressor 2 reserve |  | BB1EM403_RESERVE_DI | COMPRESSOR 2 | RESERVE |  |  | BB1EM403_RESERVE_DI | COMPRESSOR 2 RESERVE
BB1EM403 | _RUN_DO | Compressor 2 remote run |  | BB1EM403_RUN_DO | COMPRESSOR 2 | REMOTE RUN |  |  | BB1EM403_RUN_DO | COMPRESSOR 2 REMOTE RUN
BB1EM403 | _FAULT_ACK_DO | Compressor 2 Fault Acknowledge |  | BB1EM403_FAULT_ACK_DO | COMPRESSOR 2 | FAULT ACKNOWLEDGE |  |  | BB1EM403_FAULT_ACK_DO | COMPRESSOR 2 FAULT ACKNOWLEDGE
BB1CV200 | _SETPOINT | Steam from drum control valve SETPOINT |  | BB1CV200_SETPOINT | STEAM FROM DRUM CONTROL | VALVE SETPOINT |  |  | BB1CV200_SETPOINT | STEAM FROM DRUM CONTROL VALVE SETPOINT
BB1CV200 | _POSITION | Steam from drum control valve POSITION |  | BB1CV200_POSITION | STEAM FROM DRUM CONTROL | VALVE POSITION |  |  | BB1CV200_POSITION | STEAM FROM DRUM CONTROL VALVE POSITION
BB1CV001 | _SETPOINT | Make-up water control valve SETPOINT |  | BB1CV001_SETPOINT | MAKE-UP WATER CONTROL | VALVE SETPOINT |  |  | BB1CV001_SETPOINT | MAKE-UP WATER CONTROL VALVE SETPOINT
BB1CV001 | _POSITION | Make-up water control valve POSITION |  | BB1CV001_POSITION | MAKE-UP WATER CONTROL | VALVE POSITION |  |  | BB1CV001_POSITION | MAKE-UP WATER CONTROL VALVE POSITION
BB1CV002 | _SETPOINT | Feed water control valve SETPOINT |  | BB1CV002_SETPOINT | FEED WATER CONTROL VALVE | SETPOINT |  |  | BB1CV002_SETPOINT | FEED WATER CONTROL VALVE SETPOINT
BB1CV002 | _POSITION | Feed water control valve POSITION |  | BB1CV002_POSITION | FEED WATER CONTROL VALVE | POSITION |  |  | BB1CV002_POSITION | FEED WATER CONTROL VALVE POSITION
BB1DM300 | _SETPOINT | Tertiary air damper 1 SETPOINT |  | BB1DM300_SETPOINT | TERTIARY AIR DAMPER 1 | SETPOINT |  |  | BB1DM300_SETPOINT | TERTIARY AIR DAMPER 1 SETPOINT
BB1DM300 | _POSITION | Tertiary air damper 1 POSITION |  | BB1DM300_POSITION | TERTIARY AIR DAMPER 1 | POSITION |  |  | BB1DM300_POSITION | TERTIARY AIR DAMPER 1 POSITION
BB1DM400 | _SETPOINT | Primary air damper SETPOINT |  | BB1DM400_SETPOINT | PRIMARY AIR DAMPER | SETPOINT |  |  | BB1DM400_SETPOINT | PRIMARY AIR DAMPER SETPOINT
BB1DM400 | _POSITION | Primary air damper POSITION |  | BB1DM400_POSITION | PRIMARY AIR DAMPER | POSITION |  |  | BB1DM400_POSITION | PRIMARY AIR DAMPER POSITION
BB1DM550 | _SETPOINT | Recirculation gas damper SETPOINT |  | BB1DM550_SETPOINT | RECIRCULATION GAS DAMPER | SETPOINT |  |  | BB1DM550_SETPOINT | RECIRCULATION GAS DAMPER SETPOINT
BB1DM550 | _POSITION | Recirculation gas damper POSITION |  | BB1DM550_POSITION | RECIRCULATION GAS DAMPER | POSITION |  |  | BB1DM550_POSITION | RECIRCULATION GAS DAMPER POSITION
BB1DM301 | _SETPOINT | Secondary air damper 4 SETPOINT |  | BB1DM301_SETPOINT | SECONDARY AIR DAMPER 4 | SETPOINT |  |  | BB1DM301_SETPOINT | SECONDARY AIR DAMPER 4 SETPOINT
BB1DM301 | _POSITION | Secondary air damper 4 POSITION |  | BB1DM301_POSITION | SECONDARY AIR DAMPER 4 | POSITION |  |  | BB1DM301_POSITION | SECONDARY AIR DAMPER 4 POSITION
BB1DM302 | _SETPOINT | Secondary air damper 3 SETPOINT |  | BB1DM302_SETPOINT | SECONDARY AIR DAMPER 3 | SETPOINT |  |  | BB1DM302_SETPOINT | SECONDARY AIR DAMPER 3 SETPOINT
BB1DM302 | _POSITION | Secondary air damper 3 POSITION |  | BB1DM302_POSITION | SECONDARY AIR DAMPER 3 | POSITION |  |  | BB1DM302_POSITION | SECONDARY AIR DAMPER 3 POSITION
BB1DM304 | _SETPOINT | Secondary air damper 1 SETPOINT |  | BB1DM304_SETPOINT | SECONDARY AIR DAMPER 1 | SETPOINT |  |  | BB1DM304_SETPOINT | SECONDARY AIR DAMPER 1 SETPOINT
BB1DM304 | _POSITION | Secondary air damper 1 POSITION |  | BB1DM304_POSITION | SECONDARY AIR DAMPER 1 | POSITION |  |  | BB1DM304_POSITION | SECONDARY AIR DAMPER 1 POSITION
BB1DM303 | _SETPOINT | Secondary air damper 2 SETPOINT |  | BB1DM303_SETPOINT | SECONDARY AIR DAMPER 2 | SETPOINT |  |  | BB1DM303_SETPOINT | SECONDARY AIR DAMPER 2 SETPOINT
BB1DM303 | _POSITION | Secondary air damper 2 POSITION |  | BB1DM303_POSITION | SECONDARY AIR DAMPER 2 | POSITION |  |  | BB1DM303_POSITION | SECONDARY AIR DAMPER 2 POSITION
BB1CV004 | _SETPOINT | Primary air preheater control valve SETPOINT |  | BB1CV004_SETPOINT | PRIMARY AIR PREHEATER | CONTROL VALVE SETPOINT |  |  | BB1CV004_SETPOINT | PRIMARY AIR PREHEATER CONTROL VALVE SETPOINT
BB1CV004 | _POSITION | Primary air preheater control valve POSITION |  | BB1CV004_POSITION | PRIMARY AIR PREHEATER | CONTROL VALVE POSITION |  |  | BB1CV004_POSITION | PRIMARY AIR PREHEATER CONTROL VALVE POSITION
BB1CV402 | _SETPOINT | Fuel chute B carrying air control valve 2 SETPOINT |  | BB1CV402_SETPOINT | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | SETPOINT |  | BB1CV402_SETPOINT | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 SETPOINT
BB1CV402 | _POSITION | Fuel chute B carrying air control valve 2 POSITION |  | BB1CV402_POSITION | FUEL CHUTE B CARRYING | AIR CONTROL VALVE 2 | POSITION |  | BB1CV402_POSITION | FUEL CHUTE B CARRYING AIR CONTROL VALVE 2 POSITION
BB1CV403 | _SETPOINT | Fuel chute A carrying air control valve 1 SETPOINT |  | BB1CV403_SETPOINT | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | SETPOINT |  | BB1CV403_SETPOINT | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 SETPOINT
BB1CV403 | _POSITION | Fuel chute A carrying air control valve 1 POSITION |  | BB1CV403_POSITION | FUEL CHUTE A CARRYING | AIR CONTROL VALVE 1 | POSITION |  | BB1CV403_POSITION | FUEL CHUTE A CARRYING AIR CONTROL VALVE 1 POSITION
BB1PT200 |  | Feed water tank pressure |  | BB1PT200 | FEED WATER TANK PRESSURE |  |  |  | BB1PT200 | FEED WATER TANK PRESSURE
BB1LT001 |  | Feed water tank level 1 |  | BB1LT001 | FEED WATER TANK LEVEL 1 |  |  |  | BB1LT001 | FEED WATER TANK LEVEL 1
BB1LT002 |  | Feed water tank level 2 |  | BB1LT002 | FEED WATER TANK LEVEL 2 |  |  |  | BB1LT002 | FEED WATER TANK LEVEL 2
BB1PT005 |  | Feed water pressure after valve |  | BB1PT005 | FEED WATER PRESSURE | AFTER VALVE |  |  | BB1PT005 | FEED WATER PRESSURE AFTER VALVE
BB1FT001 |  | Feed water flow and control |  | BB1FT001 | FEED WATER FLOW | AND CONTROL |  |  | BB1FT001 | FEED WATER FLOW AND CONTROL
BB1TT001 |  | Feed water temperature |  | BB1TT001 | FEED WATER TEMPERATURE |  |  |  | BB1TT001 | FEED WATER TEMPERATURE
BB1TT002 |  | Feed water pump 2 bearing temperature |  | BB1TT002 | FEED WATER PUMP 2 | BEARING TEMPERATURE |  |  | BB1TT002 | FEED WATER PUMP 2 BEARING TEMPERATURE
BB1PT004 |  | Feed water pressure before valve |  | BB1PT004 | FEED WATER PRESSURE | BEFORE VALVE |  |  | BB1PT004 | FEED WATER PRESSURE BEFORE VALVE
BB1PT002 |  | Feed water pump 2 pressure side pressure |  | BB1PT002 | FEED WATER PUMP 2 | PRESSURE SIDE PRESSURE |  |  | BB1PT002 | FEED WATER PUMP 2 PRESSURE SIDE PRESSURE
BB1PT006 |  | FW suction line strainer pressure diff. |  | BB1PT006 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  |  | BB1PT006 | FW SUCTION LINE STRAINER PRESSURE DIFF.
BB1PT007 |  | FW suction line strainer pressure diff. |  | BB1PT007 | FW SUCTION LINE STRAINER | PRESSURE DIFF. |  |  | BB1PT007 | FW SUCTION LINE STRAINER PRESSURE DIFF.
BB1TT005 |  | FW pump 2 motor winding temperature |  | BB1TT005 | FW PUMP 2 MOTOR | WINDING TEMPERATURE |  |  | BB1TT005 | FW PUMP 2 MOTOR WINDING TEMPERATURE
BB1PT001 |  | Feed water pump 1 pressure side pressure |  | BB1PT001 | FEED WATER PUMP 1 | PRESSURE SIDE PRESSURE |  |  | BB1PT001 | FEED WATER PUMP 1 PRESSURE SIDE PRESSURE
BB1TT004 |  | FW pump 1 motor winding temperature |  | BB1TT004 | FW PUMP 1 MOTOR | WINDING TEMPERATURE |  |  | BB1TT004 | FW PUMP 1 MOTOR WINDING TEMPERATURE
BB1TT003 |  | FW pump 1 motor bearing temperature |  | BB1TT003 | FW PUMP 1 MOTOR | BEARING TEMPERATURE |  |  | BB1TT003 | FW PUMP 1 MOTOR BEARING TEMPERATURE
BB1TT008 |  | Temperature after economizer |  | BB1TT008 | TEMPERATURE AFTER | ECONOMIZER |  |  | BB1TT008 | TEMPERATURE AFTER ECONOMIZER
BB1FT200 |  | Heating steam to feed water tank flow measurement |  | BB1FT200 | HEATING STEAM TO FEED | WATER TANK FLOW | MEASUREMENT |  | BB1FT200 | HEATING STEAM TO FEED WATER TANK FLOW MEASUREMENT
BB1TT009 |  | Temperature before economizer |  | BB1TT009 | TEMPERATURE BEFORE | ECONOMIZER |  |  | BB1TT009 | TEMPERATURE BEFORE ECONOMIZER
BB1TT200 |  | Main steam temperature |  | BB1TT200 | MAIN STEAM TEMPERATURE |  |  |  | BB1TT200 | MAIN STEAM TEMPERATURE
BB1FT202 |  | Main steam flow |  | BB1FT202 | MAIN STEAM FLOW |  |  |  | BB1FT202 | MAIN STEAM FLOW
BB1FT201 |  | Steam flow to sootblowing and air preheater |  | BB1FT201 | STEAM FLOW TO SOOTBLOWING | AND AIR PREHEATER |  |  | BB1FT201 | STEAM FLOW TO SOOTBLOWING AND AIR PREHEATER
BB1TT201 |  | Sootblowing line temperature |  | BB1TT201 | SOOTBLOWING | LINE TEMPERATURE |  |  | BB1TT201 | SOOTBLOWING LINE TEMPERATURE
<001> |  | Electrical room temperature |  | <001> | ELECTRICAL ROOM | TEMPERATURE |  |  | <001> | ELECTRICAL ROOM TEMPERATURE
<002> |  | PLC-cabinet temperature |  | <002> | PLC-CABINET | TEMPERATURE |  |  | <002> | PLC-CABINET TEMPERATURE
BB1TT006 |  | Blow down tank temperature and control |  | BB1TT006 | BLOW DOWN TANK | TEMPERATURE AND CONTROL |  |  | BB1TT006 | BLOW DOWN TANK TEMPERATURE AND CONTROL
BB1TT202 |  | Steam outlet temperature from accumulator |  | BB1TT202 | STEAM OUTLET TEMPERATURE | FROM ACCUMULATOR |  |  | BB1TT202 | STEAM OUTLET TEMPERATURE FROM ACCUMULATOR
BB1PT207 |  | Accumulator pressure |  | BB1PT207 | ACCUMULATOR PRESSURE |  |  |  | BB1PT207 | ACCUMULATOR PRESSURE
BB1TT007 |  | Accumulator temperature |  | BB1TT007 | ACCUMULATOR TEMPERATURE |  |  |  | BB1TT007 | ACCUMULATOR TEMPERATURE
BB1TT203 |  | 18bar(g) steam temperature |  | BB1TT203 | 18BAR(G) STEAM | TEMPERATURE |  |  | BB1TT203 | 18BAR(G) STEAM TEMPERATURE
BB1PT204 |  | Main steam pressure |  | BB1PT204 | MAIN STEAM PRESSURE |  |  |  | BB1PT204 | MAIN STEAM PRESSURE
BB1LT004 |  | Steam accumulator level 2 |  | BB1LT004 | STEAM ACCUMULATOR LEVEL 2 |  |  |  | BB1LT004 | STEAM ACCUMULATOR LEVEL 2
BB1PT208 |  | Accumulator pressure |  | BB1PT208 | ACCUMULATOR PRESSURE |  |  |  | BB1PT208 | ACCUMULATOR PRESSURE
BB1FT203 |  | Steam to existing header flow measurement |  | BB1FT203 | STEAM TO EXISTING HEADER | FLOW MEASUREMENT |  |  | BB1FT203 | STEAM TO EXISTING HEADER FLOW MEASUREMENT
<003> |  | Steam to existing header energy calculator |  | <003> | STEAM TO EXISTING HEADER | ENERGY CALCULATOR |  |  | <003> | STEAM TO EXISTING HEADER ENERGY CALCULATOR
BB1LT003 |  | Steam accumulator level 1 |  | BB1LT003 | STEAM ACCUMULATOR LEVEL 1 |  |  |  | BB1LT003 | STEAM ACCUMULATOR LEVEL 1
BB1QT002 |  | pH measurement from feed water tank |  | BB1QT002 | PH MEASUREMENT FROM FEED | WATER TANK |  |  | BB1QT002 | PH MEASUREMENT FROM FEED WATER TANK
BB1QT006 |  | Conductivity measurement from main steam |  | BB1QT006 | CONDUCTIVITY MEASUREMENT | FROM MAIN STEAM |  |  | BB1QT006 | CONDUCTIVITY MEASUREMENT FROM MAIN STEAM
BB1QT005 |  | Conductivity measurement from saturated steam |  | BB1QT005 | CONDUCTIVITY MEASUREMENT | FROM SATURATED STEAM |  |  | BB1QT005 | CONDUCTIVITY MEASUREMENT FROM SATURATED STEAM
BB1QT003 |  | Conductivity measurement from condensate |  | BB1QT003 | CONDUCTIVITY MEASUREMENT | FROM CONDENSATE |  |  | BB1QT003 | CONDUCTIVITY MEASUREMENT FROM CONDENSATE
BB1QT007 |  | Conductivity measurement from feed water line |  | BB1QT007 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER LINE |  |  | BB1QT007 | CONDUCTIVITY MEASUREMENT FROM FEED WATER LINE
BB1QT001 |  | Conductivity measurement from feed water tank |  | BB1QT001 | CONDUCTIVITY MEASUREMENT | FROM FEED WATER TANK |  |  | BB1QT001 | CONDUCTIVITY MEASUREMENT FROM FEED WATER TANK
BB1QT004 |  | Conductivity measurement from boiler water |  | BB1QT004 | CONDUCTIVITY MEASUREMENT | FROM BOILER WATER |  |  | BB1QT004 | CONDUCTIVITY MEASUREMENT FROM BOILER WATER
BB1PT410 |  | Secondary air pressure inner front wall |  | BB1PT410 | SECONDARY AIR PRESSURE | INNER FRONT WALL |  |  | BB1PT410 | SECONDARY AIR PRESSURE INNER FRONT WALL
BB1TT551 |  | Flue gas temperature 2 |  | BB1TT551 | FLUE GAS TEMPERATURE 2 |  |  |  | BB1TT551 | FLUE GAS TEMPERATURE 2
BB1TT400 |  | Primary air temperature before preheater |  | BB1TT400 | PRIMARY AIR TEMPERATURE | BEFORE PREHEATER |  |  | BB1TT400 | PRIMARY AIR TEMPERATURE BEFORE PREHEATER
BB1PT403 |  | Secondary air pressure inner back wall |  | BB1PT403 | SECONDARY AIR PRESSURE | INNER BACK WALL |  |  | BB1PT403 | SECONDARY AIR PRESSURE INNER BACK WALL
BB1PT550 |  | Flue gas pressure at the outlet of the boiler |  | BB1PT550 | FLUE GAS PRESSURE AT THE | OUTLET OF THE BOILER |  |  | BB1PT550 | FLUE GAS PRESSURE AT THE OUTLET OF THE BOILER
BB1TT012 |  | Condensate temperature from primary air preheater |  | BB1TT012 | CONDENSATE TEMPERATURE | FROM PRIMARY AIR PREHEATE | R |  | BB1TT012 | CONDENSATE TEMPERATURE FROM PRIMARY AIR PREHEATE R
BB1TT550 |  | Flue gas temperature 1 |  | BB1TT550 | FLUE GAS TEMPERATURE 1 |  |  |  | BB1TT550 | FLUE GAS TEMPERATURE 1
BB1TT412 |  | Boiler temperature after empty draft 2 |  | BB1TT412 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 2 |  |  | BB1TT412 | BOILER TEMPERATURE AFTER EMPTY DRAFT 2
BB1TT411 |  | Boiler temperature after empty draft 1 |  | BB1TT411 | BOILER TEMPERATURE AFTER | EMPTY DRAFT 1 |  |  | BB1TT411 | BOILER TEMPERATURE AFTER EMPTY DRAFT 1
BB1QT552 |  | Fluegas CO measurement |  | BB1QT552 | FLUEGAS CO MEASUREMENT |  |  |  | BB1QT552 | FLUEGAS CO MEASUREMENT
BB1TT405 |  | Primary air temperature |  | BB1TT405 | PRIMARY AIR TEMPERATURE |  |  |  | BB1TT405 | PRIMARY AIR TEMPERATURE
BB1TT415 |  | Boiler bed temperature middle level |  | BB1TT415 | BOILER BED TEMPERATURE | MIDDLE LEVEL |  |  | BB1TT415 | BOILER BED TEMPERATURE MIDDLE LEVEL
BB1TT416 |  | Boiler bed temperature lower level |  | BB1TT416 | BOILER BED TEMPERATURE | LOWER LEVEL |  |  | BB1TT416 | BOILER BED TEMPERATURE LOWER LEVEL
BB1TT410 |  | Boiler 1st draft temperature |  | BB1TT410 | BOILER 1ST DRAFT | TEMPERATURE |  |  | BB1TT410 | BOILER 1ST DRAFT TEMPERATURE
BB1TT116 |  | Steam temperature to air preheater |  | BB1TT116 | STEAM TEMPERATURE TO | AIR PREHEATER |  |  | BB1TT116 | STEAM TEMPERATURE TO AIR PREHEATER
BB1TT308 |  | Furnace temperature connection |  | BB1TT308 | FURNACE TEMPERATURE | CONNECTION |  |  | BB1TT308 | FURNACE TEMPERATURE CONNECTION
BB1QT553 |  | Boiler room gas detector |  | BB1QT553 | BOILER ROOM GAS DETECTOR |  |  |  | BB1QT553 | BOILER ROOM GAS DETECTOR
BB1TT408 |  | Secondary air fan motor bearing temperature 1 |  | BB1TT408 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | BB1TT408 | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 1
BB1TT423 |  | Secondary air fan motor bearing temperature 2 |  | BB1TT423 | SECONDARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | BB1TT423 | SECONDARY AIR FAN MOTOR BEARING TEMPERATURE 2
BB1TT406 |  | Secondary air fan motor winding temperature 1 |  | BB1TT406 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  |  | BB1TT406 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 1
BB1TT404 |  | Primary air fan motor bearing temperature 1 |  | BB1TT404 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 1 |  |  | BB1TT404 | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 1
BB1TT409 |  | Primary air fan motor bearing temperature 2 |  | BB1TT409 | PRIMARY AIR FAN MOTOR | BEARING TEMPERATURE 2 |  |  | BB1TT409 | PRIMARY AIR FAN MOTOR BEARING TEMPERATURE 2
BB1TT402 |  | Primary air fan motor winding temperature 1 |  | BB1TT402 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 1 |  |  | BB1TT402 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 1
BB1TT403 |  | Primary air fan motor winding temperature 2 |  | BB1TT403 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  |  | BB1TT403 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 2
BB1TT421 |  | Primary air fan motor winding temperature 3 |  | BB1TT421 | PRIMARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT421 | PRIMARY AIR FAN MOTOR WINDING TEMPERATURE 3
BB1TT407 |  | Secondary air fan motor winding temperature 2 |  | BB1TT407 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 2 |  |  | BB1TT407 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 2
BB1TT422 |  | Secondary air fan motor winding temperature 3 |  | BB1TT422 | SECONDARY AIR FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT422 | SECONDARY AIR FAN MOTOR WINDING TEMPERATURE 3
BB1PT409 |  | Secondary air pressure outer front wall |  | BB1PT409 | SECONDARY AIR PRESSURE | OUTER FRONT WALL |  |  | BB1PT409 | SECONDARY AIR PRESSURE OUTER FRONT WALL
BB1PT411 |  | Secondary air pressure outer back wall |  | BB1PT411 | SECONDARY AIR PRESSURE | OUTER BACK WALL |  |  | BB1PT411 | SECONDARY AIR PRESSURE OUTER BACK WALL
BB1PT407 |  | Tertiary air pressure right wall |  | BB1PT407 | TERTIARY AIR PRESSURE | RIGHT WALL |  |  | BB1PT407 | TERTIARY AIR PRESSURE RIGHT WALL
BB1PT408 |  | Tertiary air pressure left wall |  | BB1PT408 | TERTIARY AIR PRESSURE | LEFT WALL |  |  | BB1PT408 | TERTIARY AIR PRESSURE LEFT WALL
BB1TT650 |  | Scraper conveyor 1 temperature measurement |  | BB1TT650 | SCRAPER CONVEYOR 1 | TEMPERATURE MEASUREMENT |  |  | BB1TT650 | SCRAPER CONVEYOR 1 TEMPERATURE MEASUREMENT
BB1LT611 |  | Unloading station 1 level |  | BB1LT611 | UNLOADING STATION 1 LEVEL |  |  |  | BB1LT611 | UNLOADING STATION 1 LEVEL
BB1LT612 |  | Unloading station 3 level |  | BB1LT612 | UNLOADING STATION 3 LEVEL |  |  |  | BB1LT612 | UNLOADING STATION 3 LEVEL
BB1LT613 |  | Unloading station 2 level |  | BB1LT613 | UNLOADING STATION 2 LEVEL |  |  |  | BB1LT613 | UNLOADING STATION 2 LEVEL
BB1LT650 |  | Fuel silo level radar 1 |  | BB1LT650 | FUEL SILO LEVEL RADAR 1 |  |  |  | BB1LT650 | FUEL SILO LEVEL RADAR 1
BB1LT651 |  | Fuel silo level radar 2 |  | BB1LT651 | FUEL SILO LEVEL RADAR 2 |  |  |  | BB1LT651 | FUEL SILO LEVEL RADAR 2
BB1LT652 |  | Fuel pocket level |  | BB1LT652 | FUEL POCKET LEVEL |  |  |  | BB1LT652 | FUEL POCKET LEVEL
BB1TT652 |  | Fuel silo temperature measurement |  | BB1TT652 | FUEL SILO TEMPERATURE | MEASUREMENT |  |  | BB1TT652 | FUEL SILO TEMPERATURE MEASUREMENT
BB1TT653 |  | Fuel pocket temperature |  | BB1TT653 | FUEL POCKET TEMPERATURE |  |  |  | BB1TT653 | FUEL POCKET TEMPERATURE
BB1PT552 |  | ESP inlet pressure transmitter |  | BB1PT552 | ESP INLET PRESSURE | TRANSMITTER |  |  | BB1PT552 | ESP INLET PRESSURE TRANSMITTER
BB1PT553 |  | ESP outlet pressure transmitter |  | BB1PT553 | ESP OUTLET PRESSURE | TRANSMITTER |  |  | BB1PT553 | ESP OUTLET PRESSURE TRANSMITTER
BB1QT554 |  | Opacity after ESP |  | BB1QT554 | OPACITY AFTER ESP |  |  |  | BB1QT554 | OPACITY AFTER ESP
BB1TT553 |  | Flue gas fan motor winding temperature 1 |  | BB1TT553 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 1 |  |  | BB1TT553 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 1
BB1TT557 |  | Flue gas fan motor winding temperature 2 |  | BB1TT557 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 2 |  |  | BB1TT557 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 2
BB1TT558 |  | Flue gas fan motor winding temperature 3 |  | BB1TT558 | FLUE GAS FAN MOTOR | WINDING TEMPERATURE 3 |  |  | BB1TT558 | FLUE GAS FAN MOTOR WINDING TEMPERATURE 3
BB1TT554 |  | Flue gas fan bearing temperature |  | BB1TT554 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | BB1TT554 | FLUE GAS FAN BEARING TEMPERATURE
BB1TT555 |  | Flue gas fan bearing temperature |  | BB1TT555 | FLUE GAS FAN BEARING | TEMPERATURE |  |  | BB1TT555 | FLUE GAS FAN BEARING TEMPERATURE
BB1TT556 |  | Flue gas temperature before stack |  | BB1TT556 | FLUE GAS TEMPERATURE | BEFORE STACK |  |  | BB1TT556 | FLUE GAS TEMPERATURE BEFORE STACK
BB1TT850 |  | ESP Ash hopper 1 temperature |  | BB1TT850 | ESP ASH HOPPER 1 | TEMPERATURE |  |  | BB1TT850 | ESP ASH HOPPER 1 TEMPERATURE
BB1TT851 |  | ESP Ash hopper 2 temperature |  | BB1TT851 | ESP ASH HOPPER 2 | TEMPERATURE |  |  | BB1TT851 | ESP ASH HOPPER 2 TEMPERATURE
BB1TS501 |  | ESP Insulator 1 temperature |  | BB1TS501 | ESP INSULATOR 1 | TEMPERATURE |  |  | BB1TS501 | ESP INSULATOR 1 TEMPERATURE
BB1TS508 |  | ESP Insulator 2 temperature |  | BB1TS508 | ESP INSULATOR 2 | TEMPERATURE |  |  | BB1TS508 | ESP INSULATOR 2 TEMPERATURE
BB1TT552 |  | Flue gas temperature before ESP |  | BB1TT552 | FLUE GAS TEMPERATURE | BEFORE ESP |  |  | BB1TT552 | FLUE GAS TEMPERATURE BEFORE ESP
BB1LT800 |  | Recycled bed material hopper level switch |  | BB1LT800 | RECYCLED BED MATERIAL | HOPPER LEVEL SWITCH |  |  | BB1LT800 | RECYCLED BED MATERIAL HOPPER LEVEL SWITCH
BB1LT802 |  | Sand silo level measurement |  | BB1LT802 | SAND SILO LEVEL | MEASUREMENT |  |  | BB1LT802 | SAND SILO LEVEL MEASUREMENT
BB1PT009 |  | Cooling water pressure before pump |  | BB1PT009 | COOLING WATER PRESSURE | BEFORE PUMP |  |  | BB1PT009 | COOLING WATER PRESSURE BEFORE PUMP
BB1TT031 |  | Cooling water temperatureafter bottom ash conveyor |  | BB1TT031 | COOLING WATER TEMPERATURE | AFTER BOTTOM ASH CONVEYOR |  |  | BB1TT031 | COOLING WATER TEMPERATURE AFTER BOTTOM ASH CONVEYOR
BB1PT478 |  | Instrument air pressure |  | BB1PT478 | INSTRUMENT AIR PRESSURE |  |  |  | BB1PT478 | INSTRUMENT AIR PRESSURE
BB1PT402 |  | Instrument air pressure after dryer |  | BB1PT402 | INSTRUMENT AIR PRESSURE | AFTER DRYER |  |  | BB1PT402 | INSTRUMENT AIR PRESSURE AFTER DRYER
BB1TT430 |  | Instrument air tank temperature |  | BB1TT430 | INSTRUMENT AIR TANK | TEMPERATURE |  |  | BB1TT430 | INSTRUMENT AIR TANK TEMPERATURE
BB1TT401 |  | Boiler room upper part temperature |  | BB1TT401 | BOILER ROOM UPPER PART | TEMPERATURE |  |  | BB1TT401 | BOILER ROOM UPPER PART TEMPERATURE
BB1LT101 |  | Steam drum level 1 |  | BB1LT101 | STEAM DRUM LEVEL 1 |  |  |  | BB1LT101 | STEAM DRUM LEVEL 1
BB1PT203 |  | Steam drum pressure 2 |  | BB1PT203 | STEAM DRUM PRESSURE 2 |  |  |  | BB1PT203 | STEAM DRUM PRESSURE 2
BB1LT102 |  | Steam drum level 2 |  | BB1LT102 | STEAM DRUM LEVEL 2 |  |  |  | BB1LT102 | STEAM DRUM LEVEL 2
BB1PT201 |  | Steam drum pressure 1 |  | BB1PT201 | STEAM DRUM PRESSURE 1 |  |  |  | BB1PT201 | STEAM DRUM PRESSURE 1
BB1LT103 |  | Steam drum level 3 |  | BB1LT103 | STEAM DRUM LEVEL 3 |  |  |  | BB1LT103 | STEAM DRUM LEVEL 3
BB1PT205 |  | Steam outlet pressure from accumulator |  | BB1PT205 | STEAM OUTLET PRESSURE | FROM ACCUMULATOR |  |  | BB1PT205 | STEAM OUTLET PRESSURE FROM ACCUMULATOR
BB1PT400 |  | Primary air pressure |  | BB1PT400 | PRIMARY AIR PRESSURE |  |  |  | BB1PT400 | PRIMARY AIR PRESSURE
BB1TT418 |  | Bed temperature 4 |  | BB1TT418 | BED TEMPERATURE 4 |  |  |  | BB1TT418 | BED TEMPERATURE 4
BB1PT404 |  | Boiler upper part pressure 1 |  | BB1PT404 | BOILER UPPER PART | PRESSURE 1 |  |  | BB1PT404 | BOILER UPPER PART PRESSURE 1
BB1FT400 |  | Primary air flow |  | BB1FT400 | PRIMARY AIR FLOW |  |  |  | BB1FT400 | PRIMARY AIR FLOW
BB1PT401 |  | Secondary air pressure |  | BB1PT401 | SECONDARY AIR PRESSURE |  |  |  | BB1PT401 | SECONDARY AIR PRESSURE
BB1FT401 |  | Secondary air flow |  | BB1FT401 | SECONDARY AIR FLOW |  |  |  | BB1FT401 | SECONDARY AIR FLOW
BB1TT417 |  | Bed temperature 3 |  | BB1TT417 | BED TEMPERATURE 3 |  |  |  | BB1TT417 | BED TEMPERATURE 3
BB1TT413 |  | Bed temperature 1 |  | BB1TT413 | BED TEMPERATURE 1 |  |  |  | BB1TT413 | BED TEMPERATURE 1
BB1TT414 |  | Bed temperature 2 |  | BB1TT414 | BED TEMPERATURE 2 |  |  |  | BB1TT414 | BED TEMPERATURE 2
BB1PT405 |  | Boiler upper part pressure 2 |  | BB1PT405 | BOILER UPPER PART | PRESSURE 2 |  |  | BB1PT405 | BOILER UPPER PART PRESSURE 2
BB1QT550 |  | Fluegas oxygen measurement 1 |  | BB1QT550 | FLUEGAS OXYGEN | MEASUREMENT 1 |  |  | BB1QT550 | FLUEGAS OXYGEN MEASUREMENT 1
BB1FT550 |  | Recirculation gas flow |  | BB1FT550 | RECIRCULATION GAS FLOW |  |  |  | BB1FT550 | RECIRCULATION GAS FLOW
BB1QT551 |  | Fluegas oxygen measurement 2 |  | BB1QT551 | FLUEGAS OXYGEN | MEASUREMENT 2 |  |  | BB1QT551 | FLUEGAS OXYGEN MEASUREMENT 2
BB1PT406 |  | Boiler upper part pressure |  | BB1PT406 | BOILER UPPER PART | PRESSURE |  |  | BB1PT406 | BOILER UPPER PART PRESSURE
BB1LS700 |  | Chemical tank 1 level switch |  | BB1LS700 | CHEMICAL TANK 1 | LEVEL SWITCH |  |  | BB1LS700 | CHEMICAL TANK 1 LEVEL SWITCH
BB1LS701 |  | Chemical tank 2 level switch |  | BB1LS701 | CHEMICAL TANK 2 | LEVEL SWITCH |  |  | BB1LS701 | CHEMICAL TANK 2 LEVEL SWITCH
BB1GS004 |  | Feed water pump suction side shut-off valve limit switch |  | BB1GS004 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH |  | BB1GS004 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH
BB1GS003 |  | Feed water pump suction side shut-off valve limit switch |  | BB1GS003 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH |  | BB1GS003 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH
BB1GS001 |  | Feed water pump suction side shut-off valve limit switch |  | BB1GS001 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH |  | BB1GS001 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH
BB1GS002 |  | Feed water pump suction side shut-off valve limit switch |  | BB1GS002 | FEED WATER PUMP SUCTION | SIDE SHUT-OFF VALVE | LIMIT SWITCH |  | BB1GS002 | FEED WATER PUMP SUCTION SIDE SHUT-OFF VALVE LIMIT SWITCH
BB1GS005 |  | FW tank overflow On-Off valve position |  | BB1GS005 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  |  | BB1GS005 | FW TANK OVERFLOW ON-OFF VALVE POSITION
BB1GS006 |  | FW tank overflow On-Off valve position |  | BB1GS006 | FW TANK OVERFLOW ON-OFF | VALVE POSITION |  |  | BB1GS006 | FW TANK OVERFLOW ON-OFF VALVE POSITION
BB1GS007 |  | Feedwater pump 1 on-off valve limit switch open |  | BB1GS007 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH OPEN |  |  | BB1GS007 | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH OPEN
BB1GS008 |  | Feedwater pump 1 on-off valve limit switch close |  | BB1GS008 | FEEDWATER PUMP 1 ON-OFF | VALVE LIMIT SWITCH CLOSE |  |  | BB1GS008 | FEEDWATER PUMP 1 ON-OFF VALVE LIMIT SWITCH CLOSE
BB1GS009 |  | Feed water pump 2 on-off valve limit switch open |  | BB1GS009 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH OPEN |  |  | BB1GS009 | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH OPEN
BB1GS010 |  | Feed water pump 2 on-off valve limit switch close |  | BB1GS010 | FEED WATER PUMP 2 ON-OFF | VALVE LIMIT SWITCH CLOSE |  |  | BB1GS010 | FEED WATER PUMP 2 ON-OFF VALVE LIMIT SWITCH CLOSE
BB1GS011 |  | Boiler bottom blow down on-off valve limit switch open |  | BB1GS011 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | OPEN |  | BB1GS011 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH OPEN
BB1GS012 |  | Boiler bottom blow down on-off valve limit switch close |  | BB1GS012 | BOILER BOTTOM BLOW DOWN | ON-OFF VALVE LIMIT SWITCH | CLOSE |  | BB1GS012 | BOILER BOTTOM BLOW DOWN ON-OFF VALVE LIMIT SWITCH CLOSE
BB1GS221 |  | Main steam valve by-pass open limit switch |  | BB1GS221 | MAIN STEAM VALVE BY-PASS | OPEN LIMIT SWITCH |  |  | BB1GS221 | MAIN STEAM VALVE BY-PASS OPEN LIMIT SWITCH
BB1GS222 |  | Main steam valve by-pass close limit switch |  | BB1GS222 | MAIN STEAM VALVE BY-PASS | CLOSE LIMIT SWITCH |  |  | BB1GS222 | MAIN STEAM VALVE BY-PASS CLOSE LIMIT SWITCH
BB1GS223 |  | Main steam line valve open limit switch |  | BB1GS223 | MAIN STEAM LINE VALVE | OPEN LIMIT SWITCH |  |  | BB1GS223 | MAIN STEAM LINE VALVE OPEN LIMIT SWITCH
BB1GS224 |  | Main steam line valve close limit switch |  | BB1GS224 | MAIN STEAM LINE VALVE | CLOSE LIMIT SWITCH |  |  | BB1GS224 | MAIN STEAM LINE VALVE CLOSE LIMIT SWITCH
BB1GS225 |  | Start-up line ON-OFF valve open limit switch |  | BB1GS225 | START-UP LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  |  | BB1GS225 | START-UP LINE ON-OFF VALVE OPEN LIMIT SWITCH
BB1GS226 |  | Start-up line ON-OFF valve close limit switch |  | BB1GS226 | START-UP LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  |  | BB1GS226 | START-UP LINE ON-OFF VALVE CLOSE LIMIT SWITCH
BB1GS200 |  | Sootblower 1 IN limit switch |  | BB1GS200 | SOOTBLOWER 1 IN | LIMIT SWITCH |  |  | BB1GS200 | SOOTBLOWER 1 IN LIMIT SWITCH
BB1GS201 |  | Sootblower 1 OUT limit switch |  | BB1GS201 | SOOTBLOWER 1 OUT | LIMIT SWITCH |  |  | BB1GS201 | SOOTBLOWER 1 OUT LIMIT SWITCH
BB1GS203 |  | Sootblower 2 OUT limit switch |  | BB1GS203 | SOOTBLOWER 2 OUT | LIMIT SWITCH |  |  | BB1GS203 | SOOTBLOWER 2 OUT LIMIT SWITCH
BB1GS204 |  | Sootblower 2 IN limit switch |  | BB1GS204 | SOOTBLOWER 2 IN | LIMIT SWITCH |  |  | BB1GS204 | SOOTBLOWER 2 IN LIMIT SWITCH
BB1GS205 |  | Sootblower 3 OUT limit switch |  | BB1GS205 | SOOTBLOWER 3 OUT | LIMIT SWITCH |  |  | BB1GS205 | SOOTBLOWER 3 OUT LIMIT SWITCH
BB1GS206 |  | Sootblower 3 IN limit switch |  | BB1GS206 | SOOTBLOWER 3 IN | LIMIT SWITCH |  |  | BB1GS206 | SOOTBLOWER 3 IN LIMIT SWITCH
BB1GS207 |  | Sootblower 5 OUT limit switch |  | BB1GS207 | SOOTBLOWER 5 OUT | LIMIT SWITCH |  |  | BB1GS207 | SOOTBLOWER 5 OUT LIMIT SWITCH
BB1GS208 |  | Sootblower 5 IN limit switch |  | BB1GS208 | SOOTBLOWER 5 IN | LIMIT SWITCH |  |  | BB1GS208 | SOOTBLOWER 5 IN LIMIT SWITCH
BB1GS209 |  | Sootblower 6 OUT limit switch |  | BB1GS209 | SOOTBLOWER 6 OUT | LIMIT SWITCH |  |  | BB1GS209 | SOOTBLOWER 6 OUT LIMIT SWITCH
BB1GS210 |  | Sootblower 6 IN limit switch |  | BB1GS210 | SOOTBLOWER 6 IN | LIMIT SWITCH |  |  | BB1GS210 | SOOTBLOWER 6 IN LIMIT SWITCH
BB1GS211 |  | Sootblower 7 OUT limit switch |  | BB1GS211 | SOOTBLOWER 7 OUT | LIMIT SWITCH |  |  | BB1GS211 | SOOTBLOWER 7 OUT LIMIT SWITCH
BB1GS212 |  | Sootblower 7 IN limit switch |  | BB1GS212 | SOOTBLOWER 7 IN | LIMIT SWITCH |  |  | BB1GS212 | SOOTBLOWER 7 IN LIMIT SWITCH
BB1GS213 |  | Sootblower 8 OUT limit switch |  | BB1GS213 | SOOTBLOWER 8 OUT | LIMIT SWITCH |  |  | BB1GS213 | SOOTBLOWER 8 OUT LIMIT SWITCH
BB1GS214 |  | Sootblower 8 IN limit switch |  | BB1GS214 | SOOTBLOWER 8 IN | LIMIT SWITCH |  |  | BB1GS214 | SOOTBLOWER 8 IN LIMIT SWITCH
BB1GS227 |  | Sootblowing line on-off valve open limit switch |  | BB1GS227 | SOOTBLOWING LINE ON-OFF | VALVE OPEN LIMIT SWITCH |  |  | BB1GS227 | SOOTBLOWING LINE ON-OFF VALVE OPEN LIMIT SWITCH
BB1GS228 |  | Sootblowing line on-off valve close limit switch |  | BB1GS228 | SOOTBLOWING LINE ON-OFF | VALVE CLOSE LIMIT SWITCH |  |  | BB1GS228 | SOOTBLOWING LINE ON-OFF VALVE CLOSE LIMIT SWITCH
BB1GS231 |  | Steam accumulator pressure control valve open limit switch |  | BB1GS231 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN LIMIT SWITCH |  | BB1GS231 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN LIMIT SWITCH
BB1GS230 |  | Steam accumulator pressure control valve close limit switch |  | BB1GS230 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE LIMIT SWITCH |  | BB1GS230 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE LIMIT SWITCH
BB1GS233 |  | Steam pressure reduction valve open limit switch |  | BB1GS233 | STEAM PRESSURE REDUCTION | VALVE OPEN LIMIT SWITCH |  |  | BB1GS233 | STEAM PRESSURE REDUCTION VALVE OPEN LIMIT SWITCH
BB1GS232 |  | Steam pressure reduction valve close limit switch |  | BB1GS232 | STEAM PRESSURE REDUCTION | VALVE CLOSE LIMIT SWITCH |  |  | BB1GS232 | STEAM PRESSURE REDUCTION VALVE CLOSE LIMIT SWITCH
BB1GS217 |  | Main steam line accumulator bypass on-offvalve open limit switch |  | BB1GS217 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN LIMIT SWITCH |  | BB1GS217 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN LIMIT SWITCH
BB1GS218 |  | Main steam line accumulator bypass on-offvalve close limit switch |  | BB1GS218 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE LIMIT SWITCH |  | BB1GS218 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE LIMIT SWITCH
BB1GS219 |  | Steam accumulator ON-OFF isolating valve open limit switch |  | BB1GS219 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN | LIMIT SWITCH |  | BB1GS219 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN LIMIT SWITCH
BB1GS220 |  | Steam accumulator ON-OFF isolating valve close limit switch |  | BB1GS220 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE | LIMIT SWITCH |  | BB1GS220 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE LIMIT SWITCH
BB1GS217 |  | Steam accumulator by-passvalve open limit switch |  | BB1GS217 | STEAM ACCUMULATOR BY-PASS | VALVE OPEN LIMIT SWITCH |  |  | BB1GS217 | STEAM ACCUMULATOR BY-PASS VALVE OPEN LIMIT SWITCH
BB1GS218 |  | Steam accumulator by-passvalve close limit switch |  | BB1GS218 | STEAM ACCUMULATOR BY-PASS | VALVE CLOSE LIMIT SWITCH |  |  | BB1GS218 | STEAM ACCUMULATOR BY-PASS VALVE CLOSE LIMIT SWITCH
BB1GS220 |  | Steam accumulator ON-OFF valve close limit switch |  | BB1GS220 | STEAM ACCUMULATOR ON-OFF | VALVE CLOSE LIMIT SWITCH |  |  | BB1GS220 | STEAM ACCUMULATOR ON-OFF VALVE CLOSE LIMIT SWITCH
BB1GS219 |  | Steam accumulator ON-OFF valve open limit switch |  | BB1GS219 | STEAM ACCUMULATOR ON-OFF | VALVE OPEN LIMIT SWITCH |  |  | BB1GS219 | STEAM ACCUMULATOR ON-OFF VALVE OPEN LIMIT SWITCH
BB1GS215 |  | Primary air preheater on-off valve open limit switch |  | BB1GS215 | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN | LIMIT SWITCH |  | BB1GS215 | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN LIMIT SWITCH
BB1GS216 |  | Primary air preheater on-off valve close limit switch |  | BB1GS216 | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE | LIMIT SWITCH |  | BB1GS216 | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE LIMIT SWITCH
BB1GS621 |  | Unloading station 3, block 3, feeder 3, out |  | BB1GS621 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, OUT |  |  | BB1GS621 | UNLOADING STATION 3, BLOCK 3, FEEDER 3, OUT
BB1GS611 |  | Unloading station 2, block 2, feeder 2, out |  | BB1GS611 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, OUT |  |  | BB1GS611 | UNLOADING STATION 2, BLOCK 2, FEEDER 2, OUT
BB1GS606 |  | Unloading station 1, block 1, feeder 4, in |  | BB1GS606 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, IN |  |  | BB1GS606 | UNLOADING STATION 1, BLOCK 1, FEEDER 4, IN
BB1GS614 |  | Unloading station 2, block 2, feeder 4, in |  | BB1GS614 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, IN |  |  | BB1GS614 | UNLOADING STATION 2, BLOCK 2, FEEDER 4, IN
BB1GS619 |  | Unloading station 3, block 3, feeder 2, out |  | BB1GS619 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, OUT |  |  | BB1GS619 | UNLOADING STATION 3, BLOCK 3, FEEDER 2, OUT
BB1GS651 |  | Disc screen by-pass damper limit switch to screen |  | BB1GS651 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | TO SCREEN |  | BB1GS651 | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH TO SCREEN
BB1PS602 |  | Hydraulics unit 1, block 3, pressure switch |  | BB1PS602 | HYDRAULICS UNIT 1, | BLOCK 3, PRESSURE SWITCH |  |  | BB1PS602 | HYDRAULICS UNIT 1, BLOCK 3, PRESSURE SWITCH
BB1GS615 |  | Unloading station 2, block 2, feeder 4, out |  | BB1GS615 | UNLOADING STATION 2, | BLOCK 2, FEEDER 4, OUT |  |  | BB1GS615 | UNLOADING STATION 2, BLOCK 2, FEEDER 4, OUT
BB1GS623 |  | Unloading station 3, block 3, feeder 4, out |  | BB1GS623 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, OUT |  |  | BB1GS623 | UNLOADING STATION 3, BLOCK 3, FEEDER 4, OUT
BB1ST651 |  | Scraper conveyor 2, rotation guard |  | BB1ST651 | SCRAPER CONVEYOR 2, | ROTATION GUARD |  |  | BB1ST651 | SCRAPER CONVEYOR 2, ROTATION GUARD
BB1GS603 |  | Unloading station 1, block 1, feeder 2, out |  | BB1GS603 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, OUT |  |  | BB1GS603 | UNLOADING STATION 1, BLOCK 1, FEEDER 2, OUT
BB1PS601 |  | Hydraulics unit 1, block 2, pressure switch |  | BB1PS601 | HYDRAULICS UNIT 1, | BLOCK 2, PRESSURE SWITCH |  |  | BB1PS601 | HYDRAULICS UNIT 1, BLOCK 2, PRESSURE SWITCH
BB1GS650 |  | Disc screen by-pass damper limit switch by-pass pos. |  | BB1GS650 | DISC SCREEN BY-PASS | DAMPER LIMIT SWITCH | BY-PASS POS. |  | BB1GS650 | DISC SCREEN BY-PASS DAMPER LIMIT SWITCH BY-PASS POS.
BB1GS622 |  | Unloading station 3, block 3, feeder 4, in |  | BB1GS622 | UNLOADING STATION 3, | BLOCK 3, FEEDER 4, IN |  |  | BB1GS622 | UNLOADING STATION 3, BLOCK 3, FEEDER 4, IN
BB1GS602 |  | Unloading station 1, block 1, feeder 2, in |  | BB1GS602 | UNLOADING STATION 1, | BLOCK 1, FEEDER 2, IN |  |  | BB1GS602 | UNLOADING STATION 1, BLOCK 1, FEEDER 2, IN
BB1LS655 |  | Scraper conveyor 2, turning point blockage guard |  | BB1LS655 | SCRAPER CONVEYOR 2, | TURNING POINT BLOCKAGE GU | ARD |  | BB1LS655 | SCRAPER CONVEYOR 2, TURNING POINT BLOCKAGE GU ARD
BB1GS607 |  | Unloading station 1, block 1, feeder 4, out |  | BB1GS607 | UNLOADING STATION 1, | BLOCK 1, FEEDER 4, OUT |  |  | BB1GS607 | UNLOADING STATION 1, BLOCK 1, FEEDER 4, OUT
BB1GS605 |  | Unloading station 1, block 1, feeder 3, out |  | BB1GS605 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, OUT |  |  | BB1GS605 | UNLOADING STATION 1, BLOCK 1, FEEDER 3, OUT
BB1LS652 |  | Unloading station 2, block 2, blockage guard |  | BB1LS652 | UNLOADING STATION 2, | BLOCK 2, BLOCKAGE GUARD |  |  | BB1LS652 | UNLOADING STATION 2, BLOCK 2, BLOCKAGE GUARD
BB1GS601 |  | Unloading station 1, block 1, feeder 1, out |  | BB1GS601 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, OUT |  |  | BB1GS601 | UNLOADING STATION 1, BLOCK 1, FEEDER 1, OUT
BB1LS608 |  | Hydraulics unit 1, low oil level alarm |  | BB1LS608 | HYDRAULICS UNIT 1, | LOW OIL LEVEL ALARM |  |  | BB1LS608 | HYDRAULICS UNIT 1, LOW OIL LEVEL ALARM
BB1LS656 |  | Scraper conveyor 2, fuel silo side blockage guard |  | BB1LS656 | SCRAPER CONVEYOR 2, | FUEL SILO SIDE | BLOCKAGE GUARD |  | BB1LS656 | SCRAPER CONVEYOR 2, FUEL SILO SIDE BLOCKAGE GUARD
BB1LS600 |  | Hydraulics unit 1, leaking pool limit switch |  | BB1LS600 | HYDRAULICS UNIT 1, | LEAKING POOL | LIMIT SWITCH |  | BB1LS600 | HYDRAULICS UNIT 1, LEAKING POOL LIMIT SWITCH
BB1GS609 |  | Unloading station 2, block 2, feeder 1, out |  | BB1GS609 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, OUT |  |  | BB1GS609 | UNLOADING STATION 2, BLOCK 2, FEEDER 1, OUT
BB1LS650 |  | Scraper conveyor 1 bed height level switch |  | BB1LS650 | SCRAPER CONVEYOR 1 | BED HEIGHT LEVEL SWITCH |  |  | BB1LS650 | SCRAPER CONVEYOR 1 BED HEIGHT LEVEL SWITCH
BB1GS617 |  | Unloading station 3, block 3, feeder 1, out |  | BB1GS617 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, OUT |  |  | BB1GS617 | UNLOADING STATION 3, BLOCK 3, FEEDER 1, OUT
BB1LS651 |  | Unloading station 3, block 3, blockage guard |  | BB1LS651 | UNLOADING STATION 3, | BLOCK 3, BLOCKAGE GUARD |  |  | BB1LS651 | UNLOADING STATION 3, BLOCK 3, BLOCKAGE GUARD
BB1GS612 |  | Unloading station 2, block 2, feeder 3, in |  | BB1GS612 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, IN |  |  | BB1GS612 | UNLOADING STATION 2, BLOCK 2, FEEDER 3, IN
BB1LS654 |  | Scraper conveyor 1, blockage guard |  | BB1LS654 | SCRAPER CONVEYOR 1, | BLOCKAGE GUARD |  |  | BB1LS654 | SCRAPER CONVEYOR 1, BLOCKAGE GUARD
BB1GS613 |  | Unloading station 2, block 2, feeder 3, out |  | BB1GS613 | UNLOADING STATION 2, | BLOCK 2, FEEDER 3, OUT |  |  | BB1GS613 | UNLOADING STATION 2, BLOCK 2, FEEDER 3, OUT
BB1GS620 |  | Unloading station 3, block 3, feeder 3, in |  | BB1GS620 | UNLOADING STATION 3, | BLOCK 3, FEEDER 3, IN |  |  | BB1GS620 | UNLOADING STATION 3, BLOCK 3, FEEDER 3, IN
BB1GS618 |  | Unloading station 3, block 3, feeder 2, in |  | BB1GS618 | UNLOADING STATION 3, | BLOCK 3, FEEDER 2, IN |  |  | BB1GS618 | UNLOADING STATION 3, BLOCK 3, FEEDER 2, IN
BB1PS600 |  | Hydraulics unit 1, block 1, pressure switch |  | BB1PS600 | HYDRAULICS UNIT 1, | BLOCK 1, PRESSURE SWITCH |  |  | BB1PS600 | HYDRAULICS UNIT 1, BLOCK 1, PRESSURE SWITCH
BB1GS608 |  | Unloading station 2, block 2, feeder 1, in |  | BB1GS608 | UNLOADING STATION 2, | BLOCK 2, FEEDER 1, IN |  |  | BB1GS608 | UNLOADING STATION 2, BLOCK 2, FEEDER 1, IN
BB1GS604 |  | Unloading station 1, block 1, feeder 3, in |  | BB1GS604 | UNLOADING STATION 1, | BLOCK 1, FEEDER 3, IN |  |  | BB1GS604 | UNLOADING STATION 1, BLOCK 1, FEEDER 3, IN
BB1LS653 |  | Unloading station 1, block 1, blockage guard |  | BB1LS653 | UNLOADING STATION 1, | BLOCK 1, BLOCKAGE GUARD |  |  | BB1LS653 | UNLOADING STATION 1, BLOCK 1, BLOCKAGE GUARD
BB1GS616 |  | Unloading station 3, block 3, feeder 1, in |  | BB1GS616 | UNLOADING STATION 3, | BLOCK 3, FEEDER 1, IN |  |  | BB1GS616 | UNLOADING STATION 3, BLOCK 3, FEEDER 1, IN
BB1GS600 |  | Unloading station 1, block 1, feeder 1, in |  | BB1GS600 | UNLOADING STATION 1, | BLOCK 1, FEEDER 1, IN |  |  | BB1GS600 | UNLOADING STATION 1, BLOCK 1, FEEDER 1, IN
BB1ST650 |  | Scraper conveyor 1, rotation guard |  | BB1ST650 | SCRAPER CONVEYOR 1, | ROTATION GUARD |  |  | BB1ST650 | SCRAPER CONVEYOR 1, ROTATION GUARD
BB1GS610 |  | Unloading station 2, block 2, feeder 2, in |  | BB1GS610 | UNLOADING STATION 2, | BLOCK 2, FEEDER 2, IN |  |  | BB1GS610 | UNLOADING STATION 2, BLOCK 2, FEEDER 2, IN
BB1ST675 |  | Leveling roller 3 speed switch |  | BB1ST675 | LEVELING ROLLER 3 | SPEED SWITCH |  |  | BB1ST675 | LEVELING ROLLER 3 SPEED SWITCH
BB1TS608 |  | High temperature switch hydraulic oil |  | BB1TS608 | HIGH TEMPERATURE SWITCH | HYDRAULIC OIL |  |  | BB1TS608 | HIGH TEMPERATURE SWITCH HYDRAULIC OIL
BB1ST673 |  | Leveling roller 1 speed switch |  | BB1ST673 | LEVELING ROLLER 1 | SPEED SWITCH |  |  | BB1ST673 | LEVELING ROLLER 1 SPEED SWITCH
BB1TS600 |  | Hydraulics unit, thermostat for heater |  | BB1TS600 | HYDRAULICS UNIT, | THERMOSTAT FOR HEATER |  |  | BB1TS600 | HYDRAULICS UNIT, THERMOSTAT FOR HEATER
BB1ST674 |  | Leveling roller 2 speed switch |  | BB1ST674 | LEVELING ROLLER 2 | SPEED SWITCH |  |  | BB1ST674 | LEVELING ROLLER 2 SPEED SWITCH
BB1PS605 |  | Hydraulic oil return block 3 filter pressure switch |  | BB1PS605 | HYDRAULIC OIL RETURN | BLOCK 3 FILTER | PRESSURE SWITCH |  | BB1PS605 | HYDRAULIC OIL RETURN BLOCK 3 FILTER PRESSURE SWITCH
BB1PS603 |  | Hydraulic oil return block 1 filter pressure switch |  | BB1PS603 | HYDRAULIC OIL RETURN | BLOCK 1 FILTER | PRESSURE SWITCH |  | BB1PS603 | HYDRAULIC OIL RETURN BLOCK 1 FILTER PRESSURE SWITCH
BB1PS604 |  | Hydraulic oil return block 2 filter pressure switch |  | BB1PS604 | HYDRAULIC OIL RETURN | BLOCK 2 FILTER | PRESSURE SWITCH |  | BB1PS604 | HYDRAULIC OIL RETURN BLOCK 2 FILTER PRESSURE SWITCH
BB1ST654 |  | Belt magnet rotation guard |  | BB1ST654 | BELT MAGNET | ROTATION GUARD |  |  | BB1ST654 | BELT MAGNET ROTATION GUARD
BB1GS661 |  | Belt magnet deviation detector 1 |  | BB1GS661 | BELT MAGNET | DEVIATION DETECTOR 1 |  |  | BB1GS661 | BELT MAGNET DEVIATION DETECTOR 1
BB1GS662 |  | Belt magnet deviation detector 2 |  | BB1GS662 | BELT MAGNET | DEVIATION DETECTOR 2 |  |  | BB1GS662 | BELT MAGNET DEVIATION DETECTOR 2
BB1ST652 |  | Belt conveyor rotation guard |  | BB1ST652 | BELT CONVEYOR | ROTATION GUARD |  |  | BB1ST652 | BELT CONVEYOR ROTATION GUARD
BB1GS659 |  | Belt conveyor deviation detector 1 |  | BB1GS659 | BELT CONVEYOR | DEVIATION DETECTOR 1 |  |  | BB1GS659 | BELT CONVEYOR DEVIATION DETECTOR 1
BB1GS660 |  | Belt conveyor deviation detector 2 |  | BB1GS660 | BELT CONVEYOR | DEVIATION DETECTOR 2 |  |  | BB1GS660 | BELT CONVEYOR DEVIATION DETECTOR 2
BB1GS663 |  | Belt conveyor oversize detector |  | BB1GS663 | BELT CONVEYOR | OVERSIZE DETECTOR |  |  | BB1GS663 | BELT CONVEYOR OVERSIZE DETECTOR
BB1ST656 |  | Disc screen drive 1 rotation guard |  | BB1ST656 | DISC SCREEN DRIVE 1 | ROTATION GUARD |  |  | BB1ST656 | DISC SCREEN DRIVE 1 ROTATION GUARD
BB1ST657 |  | Disc screen drive 2 rotation guard |  | BB1ST657 | DISC SCREEN DRIVE 2 | ROTATION GUARD |  |  | BB1ST657 | DISC SCREEN DRIVE 2 ROTATION GUARD
BB1GS652 |  | Explosion hatch limit switch 1 |  | BB1GS652 | EXPLOSION HATCH | LIMIT SWITCH 1 |  |  | BB1GS652 | EXPLOSION HATCH LIMIT SWITCH 1
BB1GS653 |  | Explosion hatch limit switch 2 |  | BB1GS653 | EXPLOSION HATCH | LIMIT SWITCH 2 |  |  | BB1GS653 | EXPLOSION HATCH LIMIT SWITCH 2
BB1GS654 |  | Explosion hatch limit switch 3 |  | BB1GS654 | EXPLOSION HATCH | LIMIT SWITCH 3 |  |  | BB1GS654 | EXPLOSION HATCH LIMIT SWITCH 3
BB1GS655 |  | Explosion hatch limit switch 4 |  | BB1GS655 | EXPLOSION HATCH | LIMIT SWITCH 4 |  |  | BB1GS655 | EXPLOSION HATCH LIMIT SWITCH 4
BB1LS657 |  | Fuel silo discharge screw blockage switch |  | BB1LS657 | FUEL SILO DISCHARGE | SCREW BLOCKAGE SWITCH |  |  | BB1LS657 | FUEL SILO DISCHARGE SCREW BLOCKAGE SWITCH
BB1LS658 |  | Fuel silo cross conveyor blockage switch |  | BB1LS658 | FUEL SILO CROSS CONVEYOR | BLOCKAGE SWITCH |  |  | BB1LS658 | FUEL SILO CROSS CONVEYOR BLOCKAGE SWITCH
<004> |  | Fuel silo cross conveyor explosion hatch limit switch |  | <004> | FUEL SILO CROSS CONVEYOR | EXPLOSION HATCH | LIMIT SWITCH |  | <004> | FUEL SILO CROSS CONVEYOR EXPLOSION HATCH LIMIT SWITCH
BB1LS659 |  | Fuel feeding screw 1 blockage switch |  | BB1LS659 | FUEL FEEDING SCREW 1 | BLOCKAGE SWITCH |  |  | BB1LS659 | FUEL FEEDING SCREW 1 BLOCKAGE SWITCH
BB1LS660 |  | Fuel feeding screw 2 blockage switch |  | BB1LS660 | FUEL FEEDING SCREW 2 | BLOCKAGE SWITCH |  |  | BB1LS660 | FUEL FEEDING SCREW 2 BLOCKAGE SWITCH
BB1ST649 |  | Fuel silo cross conveyor rotation guard |  | BB1ST649 | FUEL SILO CROSS CONVEYOR | ROTATION GUARD |  |  | BB1ST649 | FUEL SILO CROSS CONVEYOR ROTATION GUARD
BB1ST652 |  | Rotating fuel spreader rotation guard |  | BB1ST652 | ROTATING FUEL SPREADER | ROTATION GUARD |  |  | BB1ST652 | ROTATING FUEL SPREADER ROTATION GUARD
BB1ST653 |  | Fuel feeding screw 2 rotation guard |  | BB1ST653 | FUEL FEEDING SCREW 2 | ROTATION GUARD |  |  | BB1ST653 | FUEL FEEDING SCREW 2 ROTATION GUARD
BB1ST654 |  | Fuel feeding rotary feeder 1 rotation guard |  | BB1ST654 | FUEL FEEDING ROTARY | FEEDER 1 ROTATION GUARD |  |  | BB1ST654 | FUEL FEEDING ROTARY FEEDER 1 ROTATION GUARD
BB1ST655 |  | Fuel feeding rotary feeder 2 rotation guard |  | BB1ST655 | FUEL FEEDING ROTARY | FEEDER 2 ROTATION GUARD |  |  | BB1ST655 | FUEL FEEDING ROTARY FEEDER 2 ROTATION GUARD
BB1ST659 |  | Fuel feeding screw 1 rotation guard |  | BB1ST659 | FUEL FEEDING SCREW 1 | ROTATION GUARD |  |  | BB1ST659 | FUEL FEEDING SCREW 1 ROTATION GUARD
BB1GS655 |  | Slide gate valve open limit switch |  | BB1GS655 | SLIDE GATE VALVE OPEN | LIMIT SWITCH |  |  | BB1GS655 | SLIDE GATE VALVE OPEN LIMIT SWITCH
BB1GS656 |  | Slide gate valve close limit switch |  | BB1GS656 | SLIDE GATE VALVE CLOSE | LIMIT SWITCH |  |  | BB1GS656 | SLIDE GATE VALVE CLOSE LIMIT SWITCH
BB1LS661 |  | Lubrication alarm screw discharger |  | BB1LS661 | LUBRICATION ALARM | SCREW DISCHARGER |  |  | BB1LS661 | LUBRICATION ALARM SCREW DISCHARGER
BB1GS802 |  | Bottom ash valve limit switch |  | BB1GS802 | BOTTOM ASH VALVE | LIMIT SWITCH |  |  | BB1GS802 | BOTTOM ASH VALVE LIMIT SWITCH
BB1GS803 |  | Bottom ash dropping chuteclosing device limit switch |  | BB1GS803 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH |  | BB1GS803 | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH
BB1LS852 |  | Fly ash container level switch |  | BB1LS852 | FLY ASH CONTAINER | LEVEL SWITCH |  |  | BB1LS852 | FLY ASH CONTAINER LEVEL SWITCH
BB1ST805 |  | Heated ESP collection screw rotation guard |  | BB1ST805 | HEATED ESP COLLECTION | SCREW ROTATION GUARD |  |  | BB1ST805 | HEATED ESP COLLECTION SCREW ROTATION GUARD
BB1ST808 |  | ESP hopper 2 screw rotation guard |  | BB1ST808 | ESP HOPPER 2 SCREW | ROTATION GUARD |  |  | BB1ST808 | ESP HOPPER 2 SCREW ROTATION GUARD
BB1ST809 |  | ESP hopper 1 screw rotation guard |  | BB1ST809 | ESP HOPPER 1 SCREW | ROTATION GUARD |  |  | BB1ST809 | ESP HOPPER 1 SCREW ROTATION GUARD
BB1ST804 |  | ESP Rotary valve rotation guard |  | BB1ST804 | ESP ROTARY VALVE | ROTATION GUARD |  |  | BB1ST804 | ESP ROTARY VALVE ROTATION GUARD
BB1TS808 |  | ESP Ash hopper 2 overheat thermostat |  | BB1TS808 | ESP ASH HOPPER 2 | OVERHEAT THERMOSTAT |  |  | BB1TS808 | ESP ASH HOPPER 2 OVERHEAT THERMOSTAT
BB1TS809 |  | ESP Ash hopper 1 overheat thermostat |  | BB1TS809 | ESP ASH HOPPER 1 | OVERHEAT THERMOSTAT |  |  | BB1TS809 | ESP ASH HOPPER 1 OVERHEAT THERMOSTAT
BB1TS805 |  | ESP collection screw heating thermostat |  | BB1TS805 | ESP COLLECTION SCREW | HEATING THERMOSTAT |  |  | BB1TS805 | ESP COLLECTION SCREW HEATING THERMOSTAT
BB1TS804 |  | ESP Rotary valve heating thermostat |  | BB1TS804 | ESP ROTARY VALVE | HEATING THERMOSTAT |  |  | BB1TS804 | ESP ROTARY VALVE HEATING THERMOSTAT
BB1GS855 |  | Bottom ash valve solenoid valve open limit switch |  | BB1GS855 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  |  | BB1GS855 | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH
BB1GS856 |  | Bottom ash valve solenoid valve close limit switch |  | BB1GS856 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  |  | BB1GS856 | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH
BB1GS857 |  | Bottom ash valve solenoid valve open limit switch |  | BB1GS857 | BOTTOM ASH VALVE SOLENOID | VALVE OPEN LIMIT SWITCH |  |  | BB1GS857 | BOTTOM ASH VALVE SOLENOID VALVE OPEN LIMIT SWITCH
BB1GS858 |  | Bottom ash valve solenoid valve close limit switch |  | BB1GS858 | BOTTOM ASH VALVE SOLENOID | VALVE CLOSE LIMIT SWITCH |  |  | BB1GS858 | BOTTOM ASH VALVE SOLENOID VALVE CLOSE LIMIT SWITCH
BB1GS850 |  | Bottom ash sieve bypass valve close limit switch |  | BB1GS850 | BOTTOM ASH SIEVE BYPASS | VALVE CLOSE LIMIT SWITCH |  |  | BB1GS850 | BOTTOM ASH SIEVE BYPASS VALVE CLOSE LIMIT SWITCH
BB1GS851 |  | Bottom ash sieve bypass valve open limit switch |  | BB1GS851 | BOTTOM ASH SIEVE BYPASS | VALVE OPEN LIMIT SWITCH |  |  | BB1GS851 | BOTTOM ASH SIEVE BYPASS VALVE OPEN LIMIT SWITCH
BB1FS003 |  | Bottom ash cooling flow switch |  | BB1FS003 | BOTTOM ASH COOLING | FLOW SWITCH |  |  | BB1FS003 | BOTTOM ASH COOLING FLOW SWITCH
BB1GS801 |  | Sand filling valve position open limit switch |  | BB1GS801 | SAND FILLING VALVE | POSITION OPEN | LIMIT SWITCH |  | BB1GS801 | SAND FILLING VALVE POSITION OPEN LIMIT SWITCH
BB1GS800 |  | Sand filling valve position close limit switch |  | BB1GS800 | SAND FILLING VALVE | POSITION CLOSE | LIMIT SWITCH |  | BB1GS800 | SAND FILLING VALVE POSITION CLOSE LIMIT SWITCH
BB1GS854 |  | Bottom ash dropping chute limit switch |  | BB1GS854 | BOTTOM ASH DROPPING CHUTE | LIMIT SWITCH |  |  | BB1GS854 | BOTTOM ASH DROPPING CHUTE LIMIT SWITCH
BB1GS853 |  | Bottom ash dropping chute closing device limit switch |  | BB1GS853 | BOTTOM ASH DROPPING CHUTE | CLOSING DEVICE | LIMIT SWITCH |  | BB1GS853 | BOTTOM ASH DROPPING CHUTE CLOSING DEVICE LIMIT SWITCH
BB1GS859 |  | Bottom ash to container in place |  | BB1GS859 | BOTTOM ASH TO CONTAINER | IN PLACE |  |  | BB1GS859 | BOTTOM ASH TO CONTAINER IN PLACE
BB1LS850 |  | Bottom ash container level switch |  | BB1LS850 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  |  | BB1LS850 | BOTTOM ASH CONTAINER LEVEL SWITCH
BB1LS851 |  | Bottom ash container level switch |  | BB1LS851 | BOTTOM ASH CONTAINER | LEVEL SWITCH |  |  | BB1LS851 | BOTTOM ASH CONTAINER LEVEL SWITCH
BB1PT800 |  | Recycled bed material damper pressure switch |  | BB1PT800 | RECYCLED BED MATERIAL | DAMPER PRESSURE SWITCH |  |  | BB1PT800 | RECYCLED BED MATERIAL DAMPER PRESSURE SWITCH
BB1ST856 |  | Purified sand screw conveyor rotation guard |  | BB1ST856 | PURIFIED SAND SCREW | CONVEYOR ROTATION GUARD |  |  | BB1ST856 | PURIFIED SAND SCREW CONVEYOR ROTATION GUARD
BB1ST850 |  | Bottom ash conveyor rotation guard |  | BB1ST850 | BOTTOM ASH CONVEYOR | ROTATION GUARD |  |  | BB1ST850 | BOTTOM ASH CONVEYOR ROTATION GUARD
BB1GS852 |  | Bottom ash conveyor blockage detector |  | BB1GS852 | BOTTOM ASH CONVEYOR | BLOCKAGE DETECTOR |  |  | BB1GS852 | BOTTOM ASH CONVEYOR BLOCKAGE DETECTOR
BB1ST852 |  | 2nd pass fly ash rotary valve rotation guard |  | BB1ST852 | 2ND PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  |  | BB1ST852 | 2ND PASS FLY ASH ROTARY VALVE ROTATION GUARD
BB1ST853 |  | 3rd pass fly ash rotary valve rotation guard |  | BB1ST853 | 3RD PASS FLY ASH ROTARY | VALVE ROTATION GUARD |  |  | BB1ST853 | 3RD PASS FLY ASH ROTARY VALVE ROTATION GUARD
BB1GS020 |  | Emergency shower use switch |  | BB1GS020 | EMERGENCY SHOWER | USE SWITCH |  |  | BB1GS020 | EMERGENCY SHOWER USE SWITCH
BB1LS103 |  | Steam drum level switch 1 |  | BB1LS103 | STEAM DRUM LEVEL SWITCH 1 |  |  |  | BB1LS103 | STEAM DRUM LEVEL SWITCH 1
BB1LS104 |  | Steam drum level switch 2 |  | BB1LS104 | STEAM DRUM LEVEL SWITCH 2 |  |  |  | BB1LS104 | STEAM DRUM LEVEL SWITCH 2
BB1HS101 |  | Boiler emergency shutdown switch 1 |  | BB1HS101 | BOILER EMERGENCY | SHUTDOWN SWITCH 1 |  |  | BB1HS101 | BOILER EMERGENCY SHUTDOWN SWITCH 1
BB1HS103 |  | Boiler emergency shutdown switch 3 |  | BB1HS103 | BOILER EMERGENCY | SHUTDOWN SWITCH 3 |  |  | BB1HS103 | BOILER EMERGENCY SHUTDOWN SWITCH 3
BB1HS104 |  | Boiler emergency shutdown switch 4 |  | BB1HS104 | BOILER EMERGENCY | SHUTDOWN SWITCH 4 |  |  | BB1HS104 | BOILER EMERGENCY SHUTDOWN SWITCH 4
BB1HS102 |  | Boiler emergency shutdown switch 2 |  | BB1HS102 | BOILER EMERGENCY | SHUTDOWN SWITCH 2 |  |  | BB1HS102 | BOILER EMERGENCY SHUTDOWN SWITCH 2
BB1HS105 |  | Boiler emergency shutdown switch 5 |  | BB1HS105 | BOILER EMERGENCY | SHUTDOWN SWITCH 5 |  |  | BB1HS105 | BOILER EMERGENCY SHUTDOWN SWITCH 5
BB1HS106 |  | Boiler emergency shutdown switch 6 |  | BB1HS106 | BOILER EMERGENCY | SHUTDOWN SWITCH 6 |  |  | BB1HS106 | BOILER EMERGENCY SHUTDOWN SWITCH 6
BB1HS107 |  | Boiler emergency shutdown switch 7 |  | BB1HS107 | BOILER EMERGENCY | SHUTDOWN SWITCH 7 |  |  | BB1HS107 | BOILER EMERGENCY SHUTDOWN SWITCH 7
BB1HS108 |  | Boiler emergency shutdown switch 8 |  | BB1HS108 | BOILER EMERGENCY | SHUTDOWN SWITCH 8 |  |  | BB1HS108 | BOILER EMERGENCY SHUTDOWN SWITCH 8
BB1HS109 |  | Boiler emergency shutdown switch 9 |  | BB1HS109 | BOILER EMERGENCY | SHUTDOWN SWITCH 9 |  |  | BB1HS109 | BOILER EMERGENCY SHUTDOWN SWITCH 9
BB1HS110 |  | Boiler emergency shutdown switch 10 |  | BB1HS110 | BOILER EMERGENCY | SHUTDOWN SWITCH 10 |  |  | BB1HS110 | BOILER EMERGENCY SHUTDOWN SWITCH 10
BB1HS111 |  | Boiler emergency shutdown switch 11 |  | BB1HS111 | BOILER EMERGENCY | SHUTDOWN SWITCH 11 |  |  | BB1HS111 | BOILER EMERGENCY SHUTDOWN SWITCH 11
BB1HS112 |  | Boiler emergency shutdown switch 12 |  | BB1HS112 | BOILER EMERGENCY | SHUTDOWN SWITCH 12 |  |  | BB1HS112 | BOILER EMERGENCY SHUTDOWN SWITCH 12
BB1HS601 |  | Fuel system emergency shutdown switch 1 |  | BB1HS601 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 1 |  |  | BB1HS601 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 1
BB1HS602 |  | Fuel system emergency shutdown switch 2 |  | BB1HS602 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 2 |  |  | BB1HS602 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 2
BB1HS603 |  | Fuel system emergency shutdown switch 3 |  | BB1HS603 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 3 |  |  | BB1HS603 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 3
BB1HS604 |  | Fuel system emergency shutdown switch 4 |  | BB1HS604 | FUEL SYSTEM EMERGENCY | SHUTDOWN SWITCH 4 |  |  | BB1HS604 | FUEL SYSTEM EMERGENCY SHUTDOWN SWITCH 4
BB1IV002 |  | Feedwater pump 1 on-off valve |  | BB1IV002 | FEEDWATER PUMP 1 ON-OFF | VALVE |  |  | BB1IV002 | FEEDWATER PUMP 1 ON-OFF VALVE
BB1IV002 | _OPEN | Feedwater pump 1 on-off valve OPEN |  | BB1IV002_OPEN | FEEDWATER PUMP 1 ON-OFF | VALVE OPEN |  |  | BB1IV002_OPEN | FEEDWATER PUMP 1 ON-OFF VALVE OPEN
BB1IV002 | _CLOSE | Feedwater pump 1 on-off valve CLOSE |  | BB1IV002_CLOSE | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSE |  |  | BB1IV002_CLOSE | FEEDWATER PUMP 1 ON-OFF VALVE CLOSE
BB1IV002 | _OPENED | Feedwater pump 1 on-off valve OPENED |  | BB1IV002_OPENED | FEEDWATER PUMP 1 ON-OFF | VALVE OPENED |  |  | BB1IV002_OPENED | FEEDWATER PUMP 1 ON-OFF VALVE OPENED
BB1IV002 | _CLOSED | Feedwater pump 1 on-off valve CLOSED |  | BB1IV002_CLOSED | FEEDWATER PUMP 1 ON-OFF | VALVE CLOSED |  |  | BB1IV002_CLOSED | FEEDWATER PUMP 1 ON-OFF VALVE CLOSED
BB1IV002 | _FAULT | Feedwater pump 1 on-off valve FAULT |  | BB1IV002_FAULT | FEEDWATER PUMP 1 ON-OFF | VALVE FAULT |  |  | BB1IV002_FAULT | FEEDWATER PUMP 1 ON-OFF VALVE FAULT
BB1IV002 | _POSITION | Feedwater pump 1 on-off valve POSITION |  | BB1IV002_POSITION | FEEDWATER PUMP 1 ON-OFF | VALVE POSITION |  |  | BB1IV002_POSITION | FEEDWATER PUMP 1 ON-OFF VALVE POSITION
BB1IV003 |  | Feed water pump 2 on-off valve |  | BB1IV003 | FEED WATER PUMP 2 ON-OFF | VALVE |  |  | BB1IV003 | FEED WATER PUMP 2 ON-OFF VALVE
BB1IV003 | _OPEN | Feed water pump 2 on-off valve OPEN |  | BB1IV003_OPEN | FEED WATER PUMP 2 ON-OFF | VALVE OPEN |  |  | BB1IV003_OPEN | FEED WATER PUMP 2 ON-OFF VALVE OPEN
BB1IV003 | _CLOSE | Feed water pump 2 on-off valve CLOSE |  | BB1IV003_CLOSE | FEED WATER PUMP 2 ON-OFF | VALVE CLOSE |  |  | BB1IV003_CLOSE | FEED WATER PUMP 2 ON-OFF VALVE CLOSE
BB1IV003 | _OPENED | Feed water pump 2 on-off valve OPENED |  | BB1IV003_OPENED | FEED WATER PUMP 2 ON-OFF | VALVE OPENED |  |  | BB1IV003_OPENED | FEED WATER PUMP 2 ON-OFF VALVE OPENED
BB1IV003 | _CLOSED | Feed water pump 2 on-off valve CLOSED |  | BB1IV003_CLOSED | FEED WATER PUMP 2 ON-OFF | VALVE CLOSED |  |  | BB1IV003_CLOSED | FEED WATER PUMP 2 ON-OFF VALVE CLOSED
BB1IV003 | _FAULT | Feed water pump 2 on-off valve FAULT |  | BB1IV003_FAULT | FEED WATER PUMP 2 ON-OFF | VALVE FAULT |  |  | BB1IV003_FAULT | FEED WATER PUMP 2 ON-OFF VALVE FAULT
BB1IV003 | _POSITION | Feed water pump 2 on-off valve POSITION |  | BB1IV003_POSITION | FEED WATER PUMP 2 ON-OFF | VALVE POSITION |  |  | BB1IV003_POSITION | FEED WATER PUMP 2 ON-OFF VALVE POSITION
BB1IV202 |  | Main steam valve by-pass valve |  | BB1IV202 | MAIN STEAM VALVE BY-PASS | VALVE |  |  | BB1IV202 | MAIN STEAM VALVE BY-PASS VALVE
BB1IV202 | _OPEN | Main steam valve by-pass valve OPEN |  | BB1IV202_OPEN | MAIN STEAM VALVE BY-PASS | VALVE OPEN |  |  | BB1IV202_OPEN | MAIN STEAM VALVE BY-PASS VALVE OPEN
BB1IV202 | _CLOSE | Main steam valve by-pass valve CLOSE |  | BB1IV202_CLOSE | MAIN STEAM VALVE BY-PASS | VALVE CLOSE |  |  | BB1IV202_CLOSE | MAIN STEAM VALVE BY-PASS VALVE CLOSE
BB1IV202 | _OPENED | Main steam valve by-pass valve OPENED |  | BB1IV202_OPENED | MAIN STEAM VALVE BY-PASS | VALVE OPENED |  |  | BB1IV202_OPENED | MAIN STEAM VALVE BY-PASS VALVE OPENED
BB1IV202 | _CLOSED | Main steam valve by-pass valve CLOSED |  | BB1IV202_CLOSED | MAIN STEAM VALVE BY-PASS | VALVE CLOSED |  |  | BB1IV202_CLOSED | MAIN STEAM VALVE BY-PASS VALVE CLOSED
BB1IV202 | _FAULT | Main steam valve by-pass valve FAULT |  | BB1IV202_FAULT | MAIN STEAM VALVE BY-PASS | VALVE FAULT |  |  | BB1IV202_FAULT | MAIN STEAM VALVE BY-PASS VALVE FAULT
BB1IV202 | _POSITION | Main steam valve by-pass valve POSITION |  | BB1IV202_POSITION | MAIN STEAM VALVE BY-PASS | VALVE POSITION |  |  | BB1IV202_POSITION | MAIN STEAM VALVE BY-PASS VALVE POSITION
BB1CV201 |  | Start-up valve |  | BB1CV201 | START-UP VALVE |  |  |  | BB1CV201 | START-UP VALVE
BB1CV201 | _OPEN | Start-up valve OPEN |  | BB1CV201_OPEN | START-UP VALVE OPEN |  |  |  | BB1CV201_OPEN | START-UP VALVE OPEN
BB1CV201 | _CLOSE | Start-up valve CLOSE |  | BB1CV201_CLOSE | START-UP VALVE CLOSE |  |  |  | BB1CV201_CLOSE | START-UP VALVE CLOSE
BB1CV201 | _OPENED | Start-up valve OPENED |  | BB1CV201_OPENED | START-UP VALVE OPENED |  |  |  | BB1CV201_OPENED | START-UP VALVE OPENED
BB1CV201 | _CLOSED | Start-up valve CLOSED |  | BB1CV201_CLOSED | START-UP VALVE CLOSED |  |  |  | BB1CV201_CLOSED | START-UP VALVE CLOSED
BB1CV201 | _FAULT | Start-up valve FAULT |  | BB1CV201_FAULT | START-UP VALVE FAULT |  |  |  | BB1CV201_FAULT | START-UP VALVE FAULT
BB1CV201 | _POSITION | Start-up valve POSITION |  | BB1CV201_POSITION | START-UP VALVE POSITION |  |  |  | BB1CV201_POSITION | START-UP VALVE POSITION
BB1IV201 |  | Main steam valve |  | BB1IV201 | MAIN STEAM VALVE |  |  |  | BB1IV201 | MAIN STEAM VALVE
BB1IV201 | _OPEN | Main steam valve OPEN |  | BB1IV201_OPEN | MAIN STEAM VALVE OPEN |  |  |  | BB1IV201_OPEN | MAIN STEAM VALVE OPEN
BB1IV201 | _CLOSE | Main steam valve CLOSE |  | BB1IV201_CLOSE | MAIN STEAM VALVE CLOSE |  |  |  | BB1IV201_CLOSE | MAIN STEAM VALVE CLOSE
BB1IV201 | _OPENED | Main steam valve OPENED |  | BB1IV201_OPENED | MAIN STEAM VALVE OPENED |  |  |  | BB1IV201_OPENED | MAIN STEAM VALVE OPENED
BB1IV201 | _CLOSED | Main steam valve CLOSED |  | BB1IV201_CLOSED | MAIN STEAM VALVE CLOSED |  |  |  | BB1IV201_CLOSED | MAIN STEAM VALVE CLOSED
BB1IV201 | _FAULT | Main steam valve FAULT |  | BB1IV201_FAULT | MAIN STEAM VALVE FAULT |  |  |  | BB1IV201_FAULT | MAIN STEAM VALVE FAULT
BB1IV201 | _POSITION | Main steam valve POSITION |  | BB1IV201_POSITION | MAIN STEAM VALVE POSITION |  |  |  | BB1IV201_POSITION | MAIN STEAM VALVE POSITION
BB1IV200 |  | Start-up check valve |  | BB1IV200 | START-UP CHECK VALVE |  |  |  | BB1IV200 | START-UP CHECK VALVE
BB1IV200 | _OPEN | Start-up check valve OPEN |  | BB1IV200_OPEN | START-UP CHECK VALVE | OPEN |  |  | BB1IV200_OPEN | START-UP CHECK VALVE OPEN
BB1IV200 | _CLOSE | Start-up check valve CLOSE |  | BB1IV200_CLOSE | START-UP CHECK VALVE | CLOSE |  |  | BB1IV200_CLOSE | START-UP CHECK VALVE CLOSE
BB1IV200 | _OPENED | Start-up check valve OPENED |  | BB1IV200_OPENED | START-UP CHECK VALVE | OPENED |  |  | BB1IV200_OPENED | START-UP CHECK VALVE OPENED
BB1IV200 | _CLOSED | Start-up check valve CLOSED |  | BB1IV200_CLOSED | START-UP CHECK VALVE | CLOSED |  |  | BB1IV200_CLOSED | START-UP CHECK VALVE CLOSED
BB1IV200 | _FAULT | Start-up check valve FAULT |  | BB1IV200_FAULT | START-UP CHECK VALVE | FAULT |  |  | BB1IV200_FAULT | START-UP CHECK VALVE FAULT
BB1IV200 | _POSITION | Start-up check valve POSITION |  | BB1IV200_POSITION | START-UP CHECK VALVE | POSITION |  |  | BB1IV200_POSITION | START-UP CHECK VALVE POSITION
BB1IV203 |  | Sootblowing line on-off valve |  | BB1IV203 | SOOTBLOWING LINE ON-OFF | VALVE |  |  | BB1IV203 | SOOTBLOWING LINE ON-OFF VALVE
BB1IV203 | _OPEN | Sootblowing line on-off valve OPEN |  | BB1IV203_OPEN | SOOTBLOWING LINE ON-OFF | VALVE OPEN |  |  | BB1IV203_OPEN | SOOTBLOWING LINE ON-OFF VALVE OPEN
BB1IV203 | _CLOSE | Sootblowing line on-off valve CLOSE |  | BB1IV203_CLOSE | SOOTBLOWING LINE ON-OFF | VALVE CLOSE |  |  | BB1IV203_CLOSE | SOOTBLOWING LINE ON-OFF VALVE CLOSE
BB1IV203 | _OPENED | Sootblowing line on-off valve OPENED |  | BB1IV203_OPENED | SOOTBLOWING LINE ON-OFF | VALVE OPENED |  |  | BB1IV203_OPENED | SOOTBLOWING LINE ON-OFF VALVE OPENED
BB1IV203 | _CLOSED | Sootblowing line on-off valve CLOSED |  | BB1IV203_CLOSED | SOOTBLOWING LINE ON-OFF | VALVE CLOSED |  |  | BB1IV203_CLOSED | SOOTBLOWING LINE ON-OFF VALVE CLOSED
BB1IV203 | _FAULT | Sootblowing line on-off valve FAULT |  | BB1IV203_FAULT | SOOTBLOWING LINE ON-OFF | VALVE FAULT |  |  | BB1IV203_FAULT | SOOTBLOWING LINE ON-OFF VALVE FAULT
BB1IV203 | _POSITION | Sootblowing line on-off valve POSITION |  | BB1IV203_POSITION | SOOTBLOWING LINE ON-OFF | VALVE POSITION |  |  | BB1IV203_POSITION | SOOTBLOWING LINE ON-OFF VALVE POSITION
BB1CV003 |  | Continuous blow down valve |  | BB1CV003 | CONTINUOUS BLOW DOWN | VALVE |  |  | BB1CV003 | CONTINUOUS BLOW DOWN VALVE
BB1CV003 | _OPEN | Continuous blow down valve OPEN |  | BB1CV003_OPEN | CONTINUOUS BLOW DOWN | VALVE OPEN |  |  | BB1CV003_OPEN | CONTINUOUS BLOW DOWN VALVE OPEN
BB1CV003 | _CLOSE | Continuous blow down valve CLOSE |  | BB1CV003_CLOSE | CONTINUOUS BLOW DOWN | VALVE CLOSE |  |  | BB1CV003_CLOSE | CONTINUOUS BLOW DOWN VALVE CLOSE
BB1CV003 | _OPENED | Continuous blow down valve OPENED |  | BB1CV003_OPENED | CONTINUOUS BLOW DOWN | VALVE OPENED |  |  | BB1CV003_OPENED | CONTINUOUS BLOW DOWN VALVE OPENED
BB1CV003 | _CLOSED | Continuous blow down valve CLOSED |  | BB1CV003_CLOSED | CONTINUOUS BLOW DOWN | VALVE CLOSED |  |  | BB1CV003_CLOSED | CONTINUOUS BLOW DOWN VALVE CLOSED
BB1CV003 | _FAULT | Continuous blow down valve FAULT |  | BB1CV003_FAULT | CONTINUOUS BLOW DOWN | VALVE FAULT |  |  | BB1CV003_FAULT | CONTINUOUS BLOW DOWN VALVE FAULT
BB1CV003 | _POSITION | Continuous blow down valve POSITION |  | BB1CV003_POSITION | CONTINUOUS BLOW DOWN | VALVE POSITION |  |  | BB1CV003_POSITION | CONTINUOUS BLOW DOWN VALVE POSITION
BB1CV203 |  | Steam accumulator pressure control valve |  | BB1CV203 | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE |  |  | BB1CV203 | STEAM ACCUMULATOR PRESSURE CONTROL VALVE
BB1CV203 | _OPEN | Steam accumulator pressure control valve OPEN |  | BB1CV203_OPEN | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPEN |  | BB1CV203_OPEN | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPEN
BB1CV203 | _CLOSE | Steam accumulator pressure control valve CLOSE |  | BB1CV203_CLOSE | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSE |  | BB1CV203_CLOSE | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSE
BB1CV203 | _OPENED | Steam accumulator pressure control valve OPENED |  | BB1CV203_OPENED | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | OPENED |  | BB1CV203_OPENED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE OPENED
BB1CV203 | _CLOSED | Steam accumulator pressure control valve CLOSED |  | BB1CV203_CLOSED | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | CLOSED |  | BB1CV203_CLOSED | STEAM ACCUMULATOR PRESSURE CONTROL VALVE CLOSED
BB1CV203 | _FAULT | Steam accumulator pressure control valve FAULT |  | BB1CV203_FAULT | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | FAULT |  | BB1CV203_FAULT | STEAM ACCUMULATOR PRESSURE CONTROL VALVE FAULT
BB1CV203 | _POSITION | Steam accumulator pressure control valve POSITION |  | BB1CV203_POSITION | STEAM ACCUMULATOR | PRESSURE CONTROL VALVE | POSITION |  | BB1CV203_POSITION | STEAM ACCUMULATOR PRESSURE CONTROL VALVE POSITION
BB1CV202 |  | Steam pressure reduction valve |  | BB1CV202 | STEAM PRESSURE REDUCTION | VALVE |  |  | BB1CV202 | STEAM PRESSURE REDUCTION VALVE
BB1CV202 | _OPEN | Steam pressure reduction valve OPEN |  | BB1CV202_OPEN | STEAM PRESSURE REDUCTION | VALVE OPEN |  |  | BB1CV202_OPEN | STEAM PRESSURE REDUCTION VALVE OPEN
BB1CV202 | _CLOSE | Steam pressure reduction valve CLOSE |  | BB1CV202_CLOSE | STEAM PRESSURE REDUCTION | VALVE CLOSE |  |  | BB1CV202_CLOSE | STEAM PRESSURE REDUCTION VALVE CLOSE
BB1CV202 | _OPENED | Steam pressure reduction valve OPENED |  | BB1CV202_OPENED | STEAM PRESSURE REDUCTION | VALVE OPENED |  |  | BB1CV202_OPENED | STEAM PRESSURE REDUCTION VALVE OPENED
BB1CV202 | _CLOSED | Steam pressure reduction valve CLOSED |  | BB1CV202_CLOSED | STEAM PRESSURE REDUCTION | VALVE CLOSED |  |  | BB1CV202_CLOSED | STEAM PRESSURE REDUCTION VALVE CLOSED
BB1CV202 | _FAULT | Steam pressure reduction valve FAULT |  | BB1CV202_FAULT | STEAM PRESSURE REDUCTION | VALVE FAULT |  |  | BB1CV202_FAULT | STEAM PRESSURE REDUCTION VALVE FAULT
BB1CV202 | _POSITION | Steam pressure reduction valve POSITION |  | BB1CV202_POSITION | STEAM PRESSURE REDUCTION | VALVE POSITION |  |  | BB1CV202_POSITION | STEAM PRESSURE REDUCTION VALVE POSITION
BB1IV204 |  | Main steam line accumulator bypass on-off valve |  | BB1IV204 | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE |  | BB1IV204 | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE
BB1IV204 | _OPEN | Main steam line accumulator bypass on-off valve OPEN |  | BB1IV204_OPEN | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPEN |  | BB1IV204_OPEN | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPEN
BB1IV204 | _CLOSE | Main steam line accumulator bypass on-off valve CLOSE |  | BB1IV204_CLOSE | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSE |  | BB1IV204_CLOSE | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSE
BB1IV204 | _OPENED | Main steam line accumulator bypass on-off valve OPENED |  | BB1IV204_OPENED | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE OPENED |  | BB1IV204_OPENED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE OPENED
BB1IV204 | _CLOSED | Main steam line accumulator bypass on-off valve CLOSED |  | BB1IV204_CLOSED | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE CLOSED |  | BB1IV204_CLOSED | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE CLOSED
BB1IV204 | _FAULT | Main steam line accumulator bypass on-off valve FAULT |  | BB1IV204_FAULT | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE FAULT |  | BB1IV204_FAULT | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE FAULT
BB1IV204 | _POSITION | Main steam line accumulator bypass on-off valve POSITION |  | BB1IV204_POSITION | MAIN STEAM LINE | ACCUMULATOR BYPASS ON-OFF | VALVE POSITION |  | BB1IV204_POSITION | MAIN STEAM LINE ACCUMULATOR BYPASS ON-OFF VALVE POSITION
BB1IV205 |  | Steam accumulator ON-OFF isolating valve |  | BB1IV205 | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE |  |  | BB1IV205 | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE
BB1IV205 | _OPEN | Steam accumulator ON-OFF isolating valve OPEN |  | BB1IV205_OPEN | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPEN |  |  | BB1IV205_OPEN | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPEN
BB1IV205 | _CLOSE | Steam accumulator ON-OFF isolating valve CLOSE |  | BB1IV205_CLOSE | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSE |  |  | BB1IV205_CLOSE | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSE
BB1IV205 | _OPENED | Steam accumulator ON-OFF isolating valve OPENED |  | BB1IV205_OPENED | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE OPENED |  |  | BB1IV205_OPENED | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE OPENED
BB1IV205 | _CLOSED | Steam accumulator ON-OFF isolating valve CLOSED |  | BB1IV205_CLOSED | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE CLOSED |  |  | BB1IV205_CLOSED | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE CLOSED
BB1IV205 | _FAULT | Steam accumulator ON-OFF isolating valve FAULT |  | BB1IV205_FAULT | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE FAULT |  |  | BB1IV205_FAULT | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE FAULT
BB1IV205 | _POSITION | Steam accumulator ON-OFF isolating valve POSITION |  | BB1IV205_POSITION | STEAM ACCUMULATOR ON-OFF | ISOLATING VALVE POSITION |  |  | BB1IV205_POSITION | STEAM ACCUMULATOR ON-OFF ISOLATING VALVE POSITION
BB1IV206 |  | Primary air preheater on-off valve |  | BB1IV206 | PRIMARY AIR PREHEATER | ON-OFF VALVE |  |  | BB1IV206 | PRIMARY AIR PREHEATER ON-OFF VALVE
BB1IV206 | _OPEN | Primary air preheater on-off valve OPEN |  | BB1IV206_OPEN | PRIMARY AIR PREHEATER | ON-OFF VALVE OPEN |  |  | BB1IV206_OPEN | PRIMARY AIR PREHEATER ON-OFF VALVE OPEN
BB1IV206 | _CLOSE | Primary air preheater on-off valve CLOSE |  | BB1IV206_CLOSE | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSE |  |  | BB1IV206_CLOSE | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSE
BB1IV206 | _OPENED | Primary air preheater on-off valve OPENED |  | BB1IV206_OPENED | PRIMARY AIR PREHEATER | ON-OFF VALVE OPENED |  |  | BB1IV206_OPENED | PRIMARY AIR PREHEATER ON-OFF VALVE OPENED
BB1IV206 | _CLOSED | Primary air preheater on-off valve CLOSED |  | BB1IV206_CLOSED | PRIMARY AIR PREHEATER | ON-OFF VALVE CLOSED |  |  | BB1IV206_CLOSED | PRIMARY AIR PREHEATER ON-OFF VALVE CLOSED
BB1IV206 | _FAULT | Primary air preheater on-off valve FAULT |  | BB1IV206_FAULT | PRIMARY AIR PREHEATER | ON-OFF VALVE FAULT |  |  | BB1IV206_FAULT | PRIMARY AIR PREHEATER ON-OFF VALVE FAULT
BB1IV206 | _POSITION | Primary air preheater on-off valve POSITION |  | BB1IV206_POSITION | PRIMARY AIR PREHEATER | ON-OFF VALVE POSITION |  |  | BB1IV206_POSITION | PRIMARY AIR PREHEATER ON-OFF VALVE POSITION
BB1FM001 |  | Bottom ash sieve feed |  | BB1FM001 | BOTTOM ASH SIEVE FEED |  |  |  | BB1FM001 | BOTTOM ASH SIEVE FEED
BB1FM001 | _ESTOP | Bottom ash sieve feed ESTOP |  | BB1FM001_ESTOP | BOTTOM ASH SIEVE FEED | ESTOP |  |  | BB1FM001_ESTOP | BOTTOM ASH SIEVE FEED ESTOP
BB1FM001 | _RUNNING | Bottom ash sieve feed RUNNING |  | BB1FM001_RUNNING | BOTTOM ASH SIEVE FEED | RUNNING |  |  | BB1FM001_RUNNING | BOTTOM ASH SIEVE FEED RUNNING
BB1FM001 | _MAN_AUTO | Bottom ash sieve feed MAN/AUTO |  | BB1FM001_MAN_AUTO | BOTTOM ASH SIEVE FEED | MAN/AUTO |  |  | BB1FM001_MAN_AUTO | BOTTOM ASH SIEVE FEED MAN/AUTO
BB1FM001 | _FAULT | Bottom ash sieve feed THERMAL FAULT |  | BB1FM001_FAULT | BOTTOM ASH SIEVE FEED | THERMAL FAULT |  |  | BB1FM001_FAULT | BOTTOM ASH SIEVE FEED THERMAL FAULT
BB1FM001 | _VOLTAGE_OK | Bottom ash sieve feed VOLTAGE OK |  | BB1FM001_VOLTAGE_OK | BOTTOM ASH SIEVE FEED | VOLTAGE OK |  |  | BB1FM001_VOLTAGE_OK | BOTTOM ASH SIEVE FEED VOLTAGE OK
BB1FM001 | _START_STOP | Bottom ash sieve feed START/STOP |  | BB1FM001_START_STOP | BOTTOM ASH SIEVE FEED | START/STOP |  |  | BB1FM001_START_STOP | BOTTOM ASH SIEVE FEED START/STOP
BB1FL650 |  | Fuel silo dust filter control box feed |  | BB1FL650 | FUEL SILO DUST FILTER | CONTROL BOX FEED |  |  | BB1FL650 | FUEL SILO DUST FILTER CONTROL BOX FEED
BB1EH662 |  | Heater for slipring unit |  | BB1EH662 | HEATER FOR SLIPRING UNIT |  |  |  | BB1EH662 | HEATER FOR SLIPRING UNIT
<005> |  | Sand transmitter 230 Vac feed |  | <005> | SAND TRANSMITTER | 230 VAC FEED |  |  | <005> | SAND TRANSMITTER 230 VAC FEED
BB1DR400 |  | Compressor 1 dryer |  | BB1DR400 | COMPRESSOR 1 DRYER |  |  |  | BB1DR400 | COMPRESSOR 1 DRYER
BB1DR401 |  | Compressor 2 dryer |  | BB1DR401 | COMPRESSOR 2 DRYER |  |  |  | BB1DR401 | COMPRESSOR 2 DRYER
BB1CP002 |  | Smoke Exhaust cabinet |  | BB1CP002 | SMOKE EXHAUST CABINET |  |  |  | BB1CP002 | SMOKE EXHAUST CABINET
BB1FG300 |  | ESP hardwired signals to/from Boiler PLC |  | BB1FG300 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC |  |  | BB1FG300 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC
BB1FG300 | _ESP_COLLECTIVE_ALARM | ESP hardwired signals to/from Boiler PLC ESP_COLLECTIVE_ALARM |  | BB1FG300_ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_ALARM |  | BB1FG300_ESP_COLLECTIVE_ALARM | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_ALARM
BB1FG300 | _ESP_COLLECTIVE_WARNING | ESP hardwired signals to/from Boiler PLC ESP_COLLECTIVE_WARNING |  | BB1FG300_ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_COLLECTIVE_WARNING |  | BB1FG300_ESP_COLLECTIVE_WARNING | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_COLLECTIVE_WARNING
BB1FG300 | _ESP_IN_STANDBY | ESP hardwired signals to/from Boiler PLC ESP_IN_STANDBY |  | BB1FG300_ESP_IN_STANDBY | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_IN_STANDBY |  | BB1FG300_ESP_IN_STANDBY | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_STANDBY
BB1FG300 | _ESP_IN_OPERATION | ESP hardwired signals to/from Boiler PLC ESP_IN_OPERATION |  | BB1FG300_ESP_IN_OPERATION | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_IN_OPERATION |  | BB1FG300_ESP_IN_OPERATION | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_IN_OPERATION
BB1FG300 | _ESP_SPARE_DI1 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI1 |  | BB1FG300_ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI1 |  | BB1FG300_ESP_SPARE_DI1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI1
BB1FG300 | _ESP_SPARE_DI2 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI2 |  | BB1FG300_ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI2 |  | BB1FG300_ESP_SPARE_DI2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI2
BB1FG300 | _ESP_SPARE_DI3 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI3 |  | BB1FG300_ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI3 |  | BB1FG300_ESP_SPARE_DI3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI3
BB1FG300 | _ESP_SPARE_DI4 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DI4 |  | BB1FG300_ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DI4 |  | BB1FG300_ESP_SPARE_DI4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DI4
BB1FG300 | _ESP_EXT_RELEASE_FILTER | ESP hardwired signals to/from Boiler PLC ESP_EXT_RELEASE_FILTER |  | BB1FG300_ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_EXT_RELEASE_FILTER |  | BB1FG300_ESP_EXT_RELEASE_FILTER | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_EXT_RELEASE_FILTER
BB1FG300 | _ESP_SPARE_DO1 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO1 |  | BB1FG300_ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO1 |  | BB1FG300_ESP_SPARE_DO1 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO1
BB1FG300 | _ESP_SPARE_DO2 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO2 |  | BB1FG300_ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO2 |  | BB1FG300_ESP_SPARE_DO2 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO2
BB1FG300 | _ESP_SPARE_DO3 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO3 |  | BB1FG300_ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO3 |  | BB1FG300_ESP_SPARE_DO3 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO3
BB1FG300 | _ESP_SPARE_DO4 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO4 |  | BB1FG300_ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO4 |  | BB1FG300_ESP_SPARE_DO4 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO4
BB1FG300 | _ESP_SPARE_DO5 | ESP hardwired signals to/from Boiler PLC ESP_SPARE_DO5 |  | BB1FG300_ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS | TO/FROM BOILER PLC | ESP_SPARE_DO5 |  | BB1FG300_ESP_SPARE_DO5 | ESP HARDWIRED SIGNALS TO/FROM BOILER PLC ESP_SPARE_DO5
BB1SI400 |  | Primary air fan safety interlock |  | BB1SI400 | PRIMARY AIR FAN | SAFETY INTERLOCK |  |  | BB1SI400 | PRIMARY AIR FAN SAFETY INTERLOCK
BB1SI401 |  | Secondary air fan safety interlock |  | BB1SI401 | SECONDARY AIR FAN | SAFETY INTERLOCK |  |  | BB1SI401 | SECONDARY AIR FAN SAFETY INTERLOCK
BB1SI603 |  | Fuel reception hydraulic unit 1, pump 1 safety interlock |  | BB1SI603 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 1 | SAFETY INTERLOCK |  | BB1SI603 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 SAFETY INTERLOCK
BB1SI604 |  | Fuel reception hydraulic unit 1, pump 2 safety interlock |  | BB1SI604 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 2 | SAFETY INTERLOCK |  | BB1SI604 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 SAFETY INTERLOCK
BB1SI605 |  | Fuel reception hydraulic unit 1, pump 3 safety interlock |  | BB1SI605 | FUEL RECEPTION HYDRAULIC | UNIT 1, PUMP 3 | SAFETY INTERLOCK |  | BB1SI605 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 SAFETY INTERLOCK
BB1SI658 |  | Scraper Conveyor 1 safety interlock |  | BB1SI658 | SCRAPER CONVEYOR 1 | SAFETY INTERLOCK |  |  | BB1SI658 | SCRAPER CONVEYOR 1 SAFETY INTERLOCK
BB1SI659 |  | Belt Conveyor safety interlock |  | BB1SI659 | BELT CONVEYOR | SAFETY INTERLOCK |  |  | BB1SI659 | BELT CONVEYOR SAFETY INTERLOCK
BB1SI675 |  | Disc screen drive 1 safety interlock |  | BB1SI675 | DISC SCREEN DRIVE 1 | SAFETY INTERLOCK |  |  | BB1SI675 | DISC SCREEN DRIVE 1 SAFETY INTERLOCK
BB1SI676 |  | Disc screen drive 2 safety interlock |  | BB1SI676 | DISC SCREEN DRIVE 2 | SAFETY INTERLOCK |  |  | BB1SI676 | DISC SCREEN DRIVE 2 SAFETY INTERLOCK
BB1SI672 |  | Scraper Conveyor 2 safety interlock |  | BB1SI672 | SCRAPER CONVEYOR 2 | SAFETY INTERLOCK |  |  | BB1SI672 | SCRAPER CONVEYOR 2 SAFETY INTERLOCK
BB1SI550 |  | Flue gas fan safety interlock |  | BB1SI550 | FLUE GAS FAN | SAFETY INTERLOCK |  |  | BB1SI550 | FLUE GAS FAN SAFETY INTERLOCK
BB1SV601 |  | Control Valve push feeders unloading station 1 |  | BB1SV601 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 |  | BB1SV601 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1
BB1SV601 | _OUT | Control Valve push feeders unloading station 1 |  | BB1SV601_OUT | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 |  | BB1SV601_OUT | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1
BB1SV601 | _IN | Control Valve push feeders unloading station 1 |  | BB1SV601_IN | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 1 |  | BB1SV601_IN | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 1
BB1SV603 |  | Control Valve push feeders unloading station 3 |  | BB1SV603 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 |  | BB1SV603 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3
BB1SV603 | _OUT | Control Valve push feeders unloading station 3 |  | BB1SV603_OUT | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 |  | BB1SV603_OUT | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3
BB1SV603 | _IN | Control Valve push feeders unloading station 3 |  | BB1SV603_IN | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 3 |  | BB1SV603_IN | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 3
BB1SV602 |  | Control Valve push feeders unloading station 2 |  | BB1SV602 | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 |  | BB1SV602 | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2
BB1SV602 | _OUT | Control Valve push feeders unloading station 2 |  | BB1SV602_OUT | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 |  | BB1SV602_OUT | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2
BB1SV602 | _IN | Control Valve push feeders unloading station 2 |  | BB1SV602_IN | CONTROL VALVE PUSH | FEEDERS UNLOADING | STATION 2 |  | BB1SV602_IN | CONTROL VALVE PUSH FEEDERS UNLOADING STATION 2
BB1EM001 |  | Feed water pump 1 |  | BB1EM001 | FEED WATER PUMP 1 |  |  |  | BB1EM001 | FEED WATER PUMP 1
BB1EM002 |  | Feed water pump 2 |  | BB1EM002 | FEED WATER PUMP 2 |  |  |  | BB1EM002 | FEED WATER PUMP 2
BB1EM400 |  | Primary air fan |  | BB1EM400 | PRIMARY AIR FAN |  |  |  | BB1EM400 | PRIMARY AIR FAN
BB1EM401 |  | Secondary air fan |  | BB1EM401 | SECONDARY AIR FAN |  |  |  | BB1EM401 | SECONDARY AIR FAN
BB1EM550 |  | Flue gas fan |  | BB1EM550 | FLUE GAS FAN |  |  |  | BB1EM550 | FLUE GAS FAN
BB1EM603 |  | Fuel reception hydraulic unit 1, pump 1 |  | BB1EM603 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 |  |  | BB1EM603 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1
BB1EM603 | _LOCAL_MODE | Fuel reception hydraulic unit 1, pump 1 LOCAL_MODE |  | BB1EM603_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_MODE |  | BB1EM603_LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_MODE
BB1EM603 | _LOCAL_RUN | Fuel reception hydraulic unit 1, pump 1 LOCAL_RUN |  | BB1EM603_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | LOCAL_RUN |  | BB1EM603_LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 LOCAL_RUN
BB1EM603 | _ISOLATOR | Fuel reception hydraulic unit 1, pump 1 ISOLATOR |  | BB1EM603_ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 1 | ISOLATOR |  | BB1EM603_ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 1 ISOLATOR
BB1EM604 |  | Fuel reception hydraulic unit 1, pump 2 |  | BB1EM604 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 |  |  | BB1EM604 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2
BB1EM604 | _LOCAL_MODE | Fuel reception hydraulic unit 1, pump 2 LOCAL_MODE |  | BB1EM604_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_MODE |  | BB1EM604_LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_MODE
BB1EM604 | _LOCAL_RUN | Fuel reception hydraulic unit 1, pump 2 LOCAL_RUN |  | BB1EM604_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | LOCAL_RUN |  | BB1EM604_LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 LOCAL_RUN
BB1EM604 | _ISOLATOR | Fuel reception hydraulic unit 1, pump 2 ISOLATOR |  | BB1EM604_ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 2 | ISOLATOR |  | BB1EM604_ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 2 ISOLATOR
BB1EM605 |  | Fuel reception hydraulic unit 1, pump 3 |  | BB1EM605 | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 |  |  | BB1EM605 | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3
BB1EM605 | _LOCAL_MODE | Fuel reception hydraulic unit 1, pump 3 LOCAL_MODE |  | BB1EM605_LOCAL_MODE | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_MODE |  | BB1EM605_LOCAL_MODE | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_MODE
BB1EM605 | _LOCAL_RUN | Fuel reception hydraulic unit 1, pump 3 LOCAL_RUN |  | BB1EM605_LOCAL_RUN | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | LOCAL_RUN |  | BB1EM605_LOCAL_RUN | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 LOCAL_RUN
BB1EM605 | _ISOLATOR | Fuel reception hydraulic unit 1, pump 3 ISOLATOR |  | BB1EM605_ISOLATOR | FUEL RECEPTION | HYDRAULIC UNIT 1, PUMP 3 | ISOLATOR |  | BB1EM605_ISOLATOR | FUEL RECEPTION HYDRAULIC UNIT 1, PUMP 3 ISOLATOR
BB1EM658 |  | SCRAPER CONVEYOR 1 |  | BB1EM658 | SCRAPER CONVEYOR 1 |  |  |  | BB1EM658 | SCRAPER CONVEYOR 1
BB1EM658 | _LOCAL_MODE | SCRAPER CONVEYOR 1 LOCAL_MODE |  | BB1EM658_LOCAL_MODE | SCRAPER CONVEYOR 1 | LOCAL_MODE |  |  | BB1EM658_LOCAL_MODE | SCRAPER CONVEYOR 1 LOCAL_MODE
BB1EM658 | _LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD |  | BB1EM658_LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 | LOCAL_RUN_FWD |  |  | BB1EM658_LOCAL_RUN_FWD | SCRAPER CONVEYOR 1 LOCAL_RUN_FWD
BB1EM658 | _LOCAL_RUN_REV | SCRAPER CONVEYOR 1 LOCAL_RUN_REV |  | BB1EM658_LOCAL_RUN_REV | SCRAPER CONVEYOR 1 | LOCAL_RUN_REV |  |  | BB1EM658_LOCAL_RUN_REV | SCRAPER CONVEYOR 1 LOCAL_RUN_REV
BB1EM658 | _ISOLATOR | SCRAPER CONVEYOR 1 ISOLATOR |  | BB1EM658_ISOLATOR | SCRAPER CONVEYOR 1 | ISOLATOR |  |  | BB1EM658_ISOLATOR | SCRAPER CONVEYOR 1 ISOLATOR
BB1EM659 |  | BELT CONVEYOR |  | BB1EM659 | BELT CONVEYOR |  |  |  | BB1EM659 | BELT CONVEYOR
BB1EM659 | _LOCAL_MODE | BELT CONVEYOR LOCAL_MODE |  | BB1EM659_LOCAL_MODE | BELT CONVEYOR | LOCAL_MODE |  |  | BB1EM659_LOCAL_MODE | BELT CONVEYOR LOCAL_MODE
BB1EM659 | _LOCAL_RUN_FWD | BELT CONVEYOR LOCAL_RUN_FWD |  | BB1EM659_LOCAL_RUN_FWD | BELT CONVEYOR | LOCAL_RUN_FWD |  |  | BB1EM659_LOCAL_RUN_FWD | BELT CONVEYOR LOCAL_RUN_FWD
BB1EM659 | _LOCAL_RUN_REV | BELT CONVEYOR LOCAL_RUN_REV |  | BB1EM659_LOCAL_RUN_REV | BELT CONVEYOR | LOCAL_RUN_REV |  |  | BB1EM659_LOCAL_RUN_REV | BELT CONVEYOR LOCAL_RUN_REV
BB1EM659 | _ISOLATOR | BELT CONVEYOR ISOLATOR |  | BB1EM659_ISOLATOR | BELT CONVEYOR | ISOLATOR |  |  | BB1EM659_ISOLATOR | BELT CONVEYOR ISOLATOR
BB1EM675 |  | DISC SCREEN DRIVE 1 |  | BB1EM675 | DISC SCREEN DRIVE 1 |  |  |  | BB1EM675 | DISC SCREEN DRIVE 1
BB1EM675 | _LOCAL_MODE | DISC SCREEN DRIVE 1 LOCAL_MODE |  | BB1EM675_LOCAL_MODE | DISC SCREEN DRIVE 1 | LOCAL_MODE |  |  | BB1EM675_LOCAL_MODE | DISC SCREEN DRIVE 1 LOCAL_MODE
BB1EM675 | _LOCAL_RUN_FWD | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD |  | BB1EM675_LOCAL_RUN_FWD | DISC SCREEN DRIVE 1 | LOCAL_RUN_FWD |  |  | BB1EM675_LOCAL_RUN_FWD | DISC SCREEN DRIVE 1 LOCAL_RUN_FWD
BB1EM675 | _LOCAL_RUN_REV | DISC SCREEN DRIVE 1 LOCAL_RUN_REV |  | BB1EM675_LOCAL_RUN_REV | DISC SCREEN DRIVE 1 | LOCAL_RUN_REV |  |  | BB1EM675_LOCAL_RUN_REV | DISC SCREEN DRIVE 1 LOCAL_RUN_REV
BB1EM675 | _ISOLATOR | DISC SCREEN DRIVE 1 ISOLATOR |  | BB1EM675_ISOLATOR | DISC SCREEN DRIVE 1 | ISOLATOR |  |  | BB1EM675_ISOLATOR | DISC SCREEN DRIVE 1 ISOLATOR
BB1EM676 |  | DISC SCREEN DRIVE 2 |  | BB1EM676 | DISC SCREEN DRIVE 2 |  |  |  | BB1EM676 | DISC SCREEN DRIVE 2
BB1EM676 | _LOCAL_MODE | DISC SCREEN DRIVE 2 LOCAL_MODE |  | BB1EM676_LOCAL_MODE | DISC SCREEN DRIVE 2 | LOCAL_MODE |  |  | BB1EM676_LOCAL_MODE | DISC SCREEN DRIVE 2 LOCAL_MODE
BB1EM676 | _LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD |  | BB1EM676_LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 | LOCAL_RUN_FWD |  |  | BB1EM676_LOCAL_RUN_FWD | DISC SCREEN DRIVE 2 LOCAL_RUN_FWD
BB1EM676 | _LOCAL_RUN_REV | DISC SCREEN DRIVE 2 LOCAL_RUN_REV |  | BB1EM676_LOCAL_RUN_REV | DISC SCREEN DRIVE 2 | LOCAL_RUN_REV |  |  | BB1EM676_LOCAL_RUN_REV | DISC SCREEN DRIVE 2 LOCAL_RUN_REV
BB1EM676 | _ISOLATOR | DISC SCREEN DRIVE 2 ISOLATOR |  | BB1EM676_ISOLATOR | DISC SCREEN DRIVE 2 | ISOLATOR |  |  | BB1EM676_ISOLATOR | DISC SCREEN DRIVE 2 ISOLATOR
BB1EM672 |  | SCRAPER CONVEYOR 2 |  | BB1EM672 | SCRAPER CONVEYOR 2 |  |  |  | BB1EM672 | SCRAPER CONVEYOR 2
BB1EM672 | _LOCAL_MODE | SCRAPER CONVEYOR 2 LOCAL_MODE |  | BB1EM672_LOCAL_MODE | SCRAPER CONVEYOR 2 | LOCAL_MODE |  |  | BB1EM672_LOCAL_MODE | SCRAPER CONVEYOR 2 LOCAL_MODE
BB1EM672 | _LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD |  | BB1EM672_LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 | LOCAL_RUN_FWD |  |  | BB1EM672_LOCAL_RUN_FWD | SCRAPER CONVEYOR 2 LOCAL_RUN_FWD
BB1EM672 | _LOCAL_RUN_REV | SCRAPER CONVEYOR 2 LOCAL_RUN_REV |  | BB1EM672_LOCAL_RUN_REV | SCRAPER CONVEYOR 2 | LOCAL_RUN_REV |  |  | BB1EM672_LOCAL_RUN_REV | SCRAPER CONVEYOR 2 LOCAL_RUN_REV
BB1EM672 | _ISOLATOR | SCRAPER CONVEYOR 2 ISOLATOR |  | BB1EM672_ISOLATOR | SCRAPER CONVEYOR 2 | ISOLATOR |  |  | BB1EM672_ISOLATOR | SCRAPER CONVEYOR 2 ISOLATOR
BB1EM662 |  | FUEL SILO SCREW DISCHARGE |  | BB1EM662 | FUEL SILO SCREW DISCHARGE |  |  |  | BB1EM662 | FUEL SILO SCREW DISCHARGE
BB1EM662 | _LOCAL_MODE | FUEL SILO SCREW DISCHARGELOCAL_MODE |  | BB1EM662_LOCAL_MODE | FUEL SILO SCREW DISCHARGE | LOCAL_MODE |  |  | BB1EM662_LOCAL_MODE | FUEL SILO SCREW DISCHARGE LOCAL_MODE
BB1EM662 | _LOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGELOCAL_RUN_FWD |  | BB1EM662_LOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_FWD |  |  | BB1EM662_LOCAL_RUN_FWD | FUEL SILO SCREW DISCHARGE LOCAL_RUN_FWD
BB1EM662 | _LOCAL_RUN_REV | FUEL SILO SCREW DISCHARGELOCAL_RUN_REV |  | BB1EM662_LOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE | LOCAL_RUN_REV |  |  | BB1EM662_LOCAL_RUN_REV | FUEL SILO SCREW DISCHARGE LOCAL_RUN_REV
BB1EM662 | _ISOLATOR | FUEL SILO SCREW DISCHARGEISOLATOR |  | BB1EM662_ISOLATOR | FUEL SILO SCREW DISCHARGE | ISOLATOR |  |  | BB1EM662_ISOLATOR | FUEL SILO SCREW DISCHARGE ISOLATOR
BB1EM650 |  | SLEWING MOTOR FOR SCREW |  | BB1EM650 | SLEWING MOTOR FOR SCREW |  |  |  | BB1EM650 | SLEWING MOTOR FOR SCREW
BB1EM650 | _LOCAL_MODE | SLEWING MOTOR FOR SCREW LOCAL_MODE |  | BB1EM650_LOCAL_MODE | SLEWING MOTOR FOR SCREW | LOCAL_MODE |  |  | BB1EM650_LOCAL_MODE | SLEWING MOTOR FOR SCREW LOCAL_MODE
BB1EM650 | _LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD |  | BB1EM650_LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW | LOCAL_RUN_FWD |  |  | BB1EM650_LOCAL_RUN_FWD | SLEWING MOTOR FOR SCREW LOCAL_RUN_FWD
BB1EM650 | _LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV |  | BB1EM650_LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW | LOCAL_RUN_REV |  |  | BB1EM650_LOCAL_RUN_REV | SLEWING MOTOR FOR SCREW LOCAL_RUN_REV
BB1EM650 | _ISOLATOR | SLEWING MOTOR FOR SCREW ISOLATOR |  | BB1EM650_ISOLATOR | SLEWING MOTOR FOR SCREW | ISOLATOR |  |  | BB1EM650_ISOLATOR | SLEWING MOTOR FOR SCREW ISOLATOR
BB1EM663 |  | FUEL SILO CROSS CONVEYOR |  | BB1EM663 | FUEL SILO CROSS CONVEYOR |  |  |  | BB1EM663 | FUEL SILO CROSS CONVEYOR
BB1EM663 | _LOCAL_MODE | FUEL SILO CROSS CONVEYOR LOCAL_MODE |  | BB1EM663_LOCAL_MODE | FUEL SILO CROSS CONVEYOR | LOCAL_MODE |  |  | BB1EM663_LOCAL_MODE | FUEL SILO CROSS CONVEYOR LOCAL_MODE
BB1EM663 | _LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD |  | BB1EM663_LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_FWD |  |  | BB1EM663_LOCAL_RUN_FWD | FUEL SILO CROSS CONVEYOR LOCAL_RUN_FWD
BB1EM663 | _LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV |  | BB1EM663_LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR | LOCAL_RUN_REV |  |  | BB1EM663_LOCAL_RUN_REV | FUEL SILO CROSS CONVEYOR LOCAL_RUN_REV
BB1EM663 | _ISOLATOR | FUEL SILO CROSS CONVEYOR ISOLATOR |  | BB1EM663_ISOLATOR | FUEL SILO CROSS CONVEYOR | ISOLATOR |  |  | BB1EM663_ISOLATOR | FUEL SILO CROSS CONVEYOR ISOLATOR
BB1EM664 |  | FUEL FEEDING SCREW 1 |  | BB1EM664 | FUEL FEEDING SCREW 1 |  |  |  | BB1EM664 | FUEL FEEDING SCREW 1
BB1EM664 | _LOCAL_MODE | FUEL FEEDING SCREW 1 LOCAL_MODE |  | BB1EM664_LOCAL_MODE | FUEL FEEDING SCREW 1 | LOCAL_MODE |  |  | BB1EM664_LOCAL_MODE | FUEL FEEDING SCREW 1 LOCAL_MODE
BB1EM664 | _LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD |  | BB1EM664_LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 | LOCAL_RUN_FWD |  |  | BB1EM664_LOCAL_RUN_FWD | FUEL FEEDING SCREW 1 LOCAL_RUN_FWD
BB1EM664 | _LOCAL_RUN_REV | FUEL FEEDING SCREW 1 LOCAL_RUN_REV |  | BB1EM664_LOCAL_RUN_REV | FUEL FEEDING SCREW 1 | LOCAL_RUN_REV |  |  | BB1EM664_LOCAL_RUN_REV | FUEL FEEDING SCREW 1 LOCAL_RUN_REV
BB1EM664 | _ISOLATOR | FUEL FEEDING SCREW 1 ISOLATOR |  | BB1EM664_ISOLATOR | FUEL FEEDING SCREW 1 | ISOLATOR |  |  | BB1EM664_ISOLATOR | FUEL FEEDING SCREW 1 ISOLATOR
BB1EM665 |  | FUEL FEEDING SCREW 2 |  | BB1EM665 | FUEL FEEDING SCREW 2 |  |  |  | BB1EM665 | FUEL FEEDING SCREW 2
BB1EM665 | _LOCAL_MODE | FUEL FEEDING SCREW 2 LOCAL_MODE |  | BB1EM665_LOCAL_MODE | FUEL FEEDING SCREW 2 | LOCAL_MODE |  |  | BB1EM665_LOCAL_MODE | FUEL FEEDING SCREW 2 LOCAL_MODE
BB1EM665 | _LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD |  | BB1EM665_LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 | LOCAL_RUN_FWD |  |  | BB1EM665_LOCAL_RUN_FWD | FUEL FEEDING SCREW 2 LOCAL_RUN_FWD
BB1EM665 | _LOCAL_RUN_REV | FUEL FEEDING SCREW 2 LOCAL_RUN_REV |  | BB1EM665_LOCAL_RUN_REV | FUEL FEEDING SCREW 2 | LOCAL_RUN_REV |  |  | BB1EM665_LOCAL_RUN_REV | FUEL FEEDING SCREW 2 LOCAL_RUN_REV
BB1EM665 | _ISOLATOR | FUEL FEEDING SCREW 2 ISOLATOR |  | BB1EM665_ISOLATOR | FUEL FEEDING SCREW 2 | ISOLATOR |  |  | BB1EM665_ISOLATOR | FUEL FEEDING SCREW 2 ISOLATOR
BB1EM852 |  | BOTTOM ASH CONVEYOR |  | BB1EM852 | BOTTOM ASH CONVEYOR |  |  |  | BB1EM852 | BOTTOM ASH CONVEYOR
BB1EM852 | _LOCAL_MODE | BOTTOM ASH CONVEYOR LOCAL_MODE |  | BB1EM852_LOCAL_MODE | BOTTOM ASH CONVEYOR | LOCAL_MODE |  |  | BB1EM852_LOCAL_MODE | BOTTOM ASH CONVEYOR LOCAL_MODE
BB1EM852 | _LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD |  | BB1EM852_LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR | LOCAL_RUN_FWD |  |  | BB1EM852_LOCAL_RUN_FWD | BOTTOM ASH CONVEYOR LOCAL_RUN_FWD
BB1EM852 | _LOCAL_RUN_REV | BOTTOM ASH CONVEYOR LOCAL_RUN_REV |  | BB1EM852_LOCAL_RUN_REV | BOTTOM ASH CONVEYOR | LOCAL_RUN_REV |  |  | BB1EM852_LOCAL_RUN_REV | BOTTOM ASH CONVEYOR LOCAL_RUN_REV
BB1EM852 | _ISOLATOR | BOTTOM ASH CONVEYOR ISOLATOR |  | BB1EM852_ISOLATOR | BOTTOM ASH CONVEYOR | ISOLATOR |  |  | BB1EM852_ISOLATOR | BOTTOM ASH CONVEYOR ISOLATOR
BB1EM660 |  | Cooling fan for slewing motor |  | BB1EM660 | COOLING FAN FOR | SLEWING MOTOR |  |  | BB1EM660 | COOLING FAN FOR SLEWING MOTOR
BB1EM660 | _RUNNING | Cooling fan for slewing motor RUNNING |  | BB1EM660_RUNNING | COOLING FAN FOR | SLEWING MOTOR RUNNING |  |  | BB1EM660_RUNNING | COOLING FAN FOR SLEWING MOTOR RUNNING
BB1EM660 | _FAULT | Cooling fan for slewing motor FAULT |  | BB1EM660_FAULT | COOLING FAN FOR | SLEWING MOTOR FAULT |  |  | BB1EM660_FAULT | COOLING FAN FOR SLEWING MOTOR FAULT
BB1EM660 | _RUN | Cooling fan for slewing motor RUN |  | BB1EM660_RUN | COOLING FAN FOR | SLEWING MOTOR RUN |  |  | BB1EM660_RUN | COOLING FAN FOR SLEWING MOTOR RUN
BB1EM660 | _ISOLATOR | Cooling fan for slewing motor ISOLATOR |  | BB1EM660_ISOLATOR | COOLING FAN FOR | SLEWING MOTOR ISOLATOR |  |  | BB1EM660_ISOLATOR | COOLING FAN FOR SLEWING MOTOR ISOLATOR
BB1EM654 |  | Lubrication unit |  | BB1EM654 | LUBRICATION UNIT |  |  |  | BB1EM654 | LUBRICATION UNIT
BB1EM654 | _RUNNING | Lubrication unit RUNNING |  | BB1EM654_RUNNING | LUBRICATION UNIT RUNNING |  |  |  | BB1EM654_RUNNING | LUBRICATION UNIT RUNNING
BB1EM654 | _FAULT | Lubrication unit FAULT |  | BB1EM654_FAULT | LUBRICATION UNIT FAULT |  |  |  | BB1EM654_FAULT | LUBRICATION UNIT FAULT
BB1EM654 | _RUN | Lubrication unit RUN |  | BB1EM654_RUN | LUBRICATION UNIT RUN |  |  |  | BB1EM654_RUN | LUBRICATION UNIT RUN
BB1EM654 | _ISOLATOR | Lubrication unit ISOLATOR |  | BB1EM654_ISOLATOR | LUBRICATION UNIT ISOLATOR |  |  |  | BB1EM654_ISOLATOR | LUBRICATION UNIT ISOLATOR
BB1EM653 |  | Cooling fan fuel feeding screw 1 |  | BB1EM653 | COOLING FAN FUEL | FEEDING SCREW 1 |  |  | BB1EM653 | COOLING FAN FUEL FEEDING SCREW 1
BB1EM653 | _RUNNING | Cooling fan fuel feeding screw 1 RUNNING |  | BB1EM653_RUNNING | COOLING FAN FUEL | FEEDING SCREW 1 RUNNING |  |  | BB1EM653_RUNNING | COOLING FAN FUEL FEEDING SCREW 1 RUNNING
BB1EM653 | _FAULT | Cooling fan fuel feeding screw 1 FAULT |  | BB1EM653_FAULT | COOLING FAN FUEL | FEEDING SCREW 1 FAULT |  |  | BB1EM653_FAULT | COOLING FAN FUEL FEEDING SCREW 1 FAULT
BB1EM653 | _RUN | Cooling fan fuel feeding screw 1 RUN |  | BB1EM653_RUN | COOLING FAN FUEL | FEEDING SCREW 1 RUN |  |  | BB1EM653_RUN | COOLING FAN FUEL FEEDING SCREW 1 RUN
BB1EM653 | _ISOLATOR | Cooling fan fuel feeding screw 1 ISOLATOR |  | BB1EM653_ISOLATOR | COOLING FAN FUEL | FEEDING SCREW 1 ISOLATOR |  |  | BB1EM653_ISOLATOR | COOLING FAN FUEL FEEDING SCREW 1 ISOLATOR
BB1EM655 |  | Cooling fan fuel feeding screw 2 |  | BB1EM655 | COOLING FAN FUEL | FEEDING SCREW 2 |  |  | BB1EM655 | COOLING FAN FUEL FEEDING SCREW 2
BB1EM655 | _RUNNING | Cooling fan fuel feeding screw 2 RUNNING |  | BB1EM655_RUNNING | COOLING FAN FUEL | FEEDING SCREW 2 RUNNING |  |  | BB1EM655_RUNNING | COOLING FAN FUEL FEEDING SCREW 2 RUNNING
BB1EM655 | _FAULT | Cooling fan fuel feeding screw 2 FAULT |  | BB1EM655_FAULT | COOLING FAN FUEL | FEEDING SCREW 2 FAULT |  |  | BB1EM655_FAULT | COOLING FAN FUEL FEEDING SCREW 2 FAULT
BB1EM655 | _RUN | Cooling fan fuel feeding screw 2 RUN |  | BB1EM655_RUN | COOLING FAN FUEL | FEEDING SCREW 2 RUN |  |  | BB1EM655_RUN | COOLING FAN FUEL FEEDING SCREW 2 RUN
BB1EM655 | _ISOLATOR | Cooling fan fuel feeding screw 2 ISOLATOR |  | BB1EM655_ISOLATOR | COOLING FAN FUEL | FEEDING SCREW 2 ISOLATOR |  |  | BB1EM655_ISOLATOR | COOLING FAN FUEL FEEDING SCREW 2 ISOLATOR
BB1EM606 |  | Dust extraction fan |  | BB1EM606 | DUST EXTRACTION FAN |  |  |  | BB1EM606 | DUST EXTRACTION FAN
BB1EM606 | _ISOLATOR | Dust extraction fan ISOLATOR |  | BB1EM606_ISOLATOR | DUST EXTRACTION FAN | ISOLATOR |  |  | BB1EM606_ISOLATOR | DUST EXTRACTION FAN ISOLATOR
BB1EH600 |  | Electric heater hydraulic unit |  | BB1EH600 | ELECTRIC HEATER | HYDRAULIC UNIT |  |  | BB1EH600 | ELECTRIC HEATER HYDRAULIC UNIT
BB1EH600 | _ISOLATOR | Electric heater hydraulic unit ISOLATOR |  | BB1EH600_ISOLATOR | ELECTRIC HEATER | HYDRAULIC UNIT ISOLATOR |  |  | BB1EH600_ISOLATOR | ELECTRIC HEATER HYDRAULIC UNIT ISOLATOR
BB1EM651 |  | Fuel silo dust filter fan |  | BB1EM651 | FUEL SILO DUST FILTER FAN |  |  |  | BB1EM651 | FUEL SILO DUST FILTER FAN
BB1EM651 | _ISOLATOR | Fuel silo dust filter fanISOLATOR |  | BB1EM651_ISOLATOR | FUEL SILO DUST FILTER FAN | ISOLATOR |  |  | BB1EM651_ISOLATOR | FUEL SILO DUST FILTER FAN ISOLATOR
BB1EM008 |  | Conveyor cooling pump |  | BB1EM008 | CONVEYOR COOLING PUMP |  |  |  | BB1EM008 | CONVEYOR COOLING PUMP
BB1EM008 | _ISOLATOR | Conveyor cooling pump ISOLATOR |  | BB1EM008_ISOLATOR | CONVEYOR COOLING PUMP | ISOLATOR |  |  | BB1EM008_ISOLATOR | CONVEYOR COOLING PUMP ISOLATOR
BB1EM009 |  | Bottom ash conveyor heat exchanger fan |  | BB1EM009 | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN |  |  | BB1EM009 | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN
BB1EM009 | _ISOLATOR | Bottom ash conveyor heat exchanger fan ISOLATOR |  | BB1EM009_ISOLATOR | BOTTOM ASH CONVEYOR | HEAT EXCHANGER FAN ISOLAT | OR |  | BB1EM009_ISOLATOR | BOTTOM ASH CONVEYOR HEAT EXCHANGER FAN ISOLAT OR
BB1EM408 |  | Boiler house heater 1 |  | BB1EM408 | BOILER HOUSE HEATER 1 |  |  |  | BB1EM408 | BOILER HOUSE HEATER 1
BB1EM408 | _ISOLATOR | Boiler house heater 1 ISOLATOR |  | BB1EM408_ISOLATOR | BOILER HOUSE HEATER 1 | ISOLATOR |  |  | BB1EM408_ISOLATOR | BOILER HOUSE HEATER 1 ISOLATOR
BB1EM409 |  | Boiler house heater 2 |  | BB1EM409 | BOILER HOUSE HEATER 2 |  |  |  | BB1EM409 | BOILER HOUSE HEATER 2
BB1EM409 | _ISOLATOR | Boiler house heater 2 ISOLATOR |  | BB1EM409_ISOLATOR | BOILER HOUSE HEATER 2 | ISOLATOR |  |  | BB1EM409_ISOLATOR | BOILER HOUSE HEATER 2 ISOLATOR
BB1EM703 |  | Chemical filling pump 1 |  | BB1EM703 | CHEMICAL FILLING PUMP 1 |  |  |  | BB1EM703 | CHEMICAL FILLING PUMP 1
BB1EM703 | _RUNNING | Chemical filling pump 1 RUNNING |  | BB1EM703_RUNNING | CHEMICAL FILLING PUMP 1 | RUNNING |  |  | BB1EM703_RUNNING | CHEMICAL FILLING PUMP 1 RUNNING
BB1EM703 | _FAULT | Chemical filling pump 1 FAULT |  | BB1EM703_FAULT | CHEMICAL FILLING PUMP 1 | FAULT |  |  | BB1EM703_FAULT | CHEMICAL FILLING PUMP 1 FAULT
BB1EM703 | _RUN | Chemical filling pump 1 RUN |  | BB1EM703_RUN | CHEMICAL FILLING PUMP 1 | RUN |  |  | BB1EM703_RUN | CHEMICAL FILLING PUMP 1 RUN
BB1EM703 | _LOCAL_MODE | Chemical filling pump 1 LOCAL_MODE |  | BB1EM703_LOCAL_MODE | CHEMICAL FILLING PUMP 1 | LOCAL_MODE |  |  | BB1EM703_LOCAL_MODE | CHEMICAL FILLING PUMP 1 LOCAL_MODE
BB1EM703 | _LOCAL_RUN | Chemical filling pump 1 LOCAL_RUN |  | BB1EM703_LOCAL_RUN | CHEMICAL FILLING PUMP 1 | LOCAL_RUN |  |  | BB1EM703_LOCAL_RUN | CHEMICAL FILLING PUMP 1 LOCAL_RUN
BB1EM703 | _ISOLATOR | Chemical filling pump 1 ISOLATOR |  | BB1EM703_ISOLATOR | CHEMICAL FILLING PUMP 1 | ISOLATOR |  |  | BB1EM703_ISOLATOR | CHEMICAL FILLING PUMP 1 ISOLATOR
BB1EM704 |  | Chemical filling pump 2 |  | BB1EM704 | CHEMICAL FILLING PUMP 2 |  |  |  | BB1EM704 | CHEMICAL FILLING PUMP 2
BB1EM704 | _RUNNING | Chemical filling pump 2 RUNNING |  | BB1EM704_RUNNING | CHEMICAL FILLING PUMP 2 | RUNNING |  |  | BB1EM704_RUNNING | CHEMICAL FILLING PUMP 2 RUNNING
BB1EM704 | _FAULT | Chemical filling pump 2 FAULT |  | BB1EM704_FAULT | CHEMICAL FILLING PUMP 2 | FAULT |  |  | BB1EM704_FAULT | CHEMICAL FILLING PUMP 2 FAULT
BB1EM704 | _RUN | Chemical filling pump 2 RUN |  | BB1EM704_RUN | CHEMICAL FILLING PUMP 2 | RUN |  |  | BB1EM704_RUN | CHEMICAL FILLING PUMP 2 RUN
BB1EM704 | _LOCAL_MODE | Chemical filling pump 2 LOCAL_MODE |  | BB1EM704_LOCAL_MODE | CHEMICAL FILLING PUMP 2 | LOCAL_MODE |  |  | BB1EM704_LOCAL_MODE | CHEMICAL FILLING PUMP 2 LOCAL_MODE
BB1EM704 | _LOCAL_RUN | Chemical filling pump 2 LOCAL_RUN |  | BB1EM704_LOCAL_RUN | CHEMICAL FILLING PUMP 2 | LOCAL_RUN |  |  | BB1EM704_LOCAL_RUN | CHEMICAL FILLING PUMP 2 LOCAL_RUN
BB1EM704 | _ISOLATOR | Chemical filling pump 2 ISOLATOR |  | BB1EM704_ISOLATOR | CHEMICAL FILLING PUMP 2 | ISOLATOR |  |  | BB1EM704_ISOLATOR | CHEMICAL FILLING PUMP 2 ISOLATOR
BB1EM670 |  | Belt magnet |  | BB1EM670 | BELT MAGNET |  |  |  | BB1EM670 | BELT MAGNET
BB1EM670 | _LOCAL_MODE | Belt magnet LOCAL_MODE |  | BB1EM670_LOCAL_MODE | BELT MAGNET LOCAL_MODE |  |  |  | BB1EM670_LOCAL_MODE | BELT MAGNET LOCAL_MODE
BB1EM670 | _LOCAL_RUN | Belt magnet LOCAL_RUN |  | BB1EM670_LOCAL_RUN | BELT MAGNET LOCAL_RUN |  |  |  | BB1EM670_LOCAL_RUN | BELT MAGNET LOCAL_RUN
BB1EM670 | _ISOLATOR | Belt magnet ISOLATOR |  | BB1EM670_ISOLATOR | BELT MAGNET ISOLATOR |  |  |  | BB1EM670_ISOLATOR | BELT MAGNET ISOLATOR
BB1EM652 |  | Rotating fuel spreader |  | BB1EM652 | ROTATING FUEL SPREADER |  |  |  | BB1EM652 | ROTATING FUEL SPREADER
BB1EM652 | _LOCAL_MODE | Rotating fuel spreader LOCAL_MODE |  | BB1EM652_LOCAL_MODE | ROTATING FUEL SPREADER | LOCAL_MODE |  |  | BB1EM652_LOCAL_MODE | ROTATING FUEL SPREADER LOCAL_MODE
BB1EM652 | _LOCAL_RUN | Rotating fuel spreader LOCAL_RUN |  | BB1EM652_LOCAL_RUN | ROTATING FUEL SPREADER | LOCAL_RUN |  |  | BB1EM652_LOCAL_RUN | ROTATING FUEL SPREADER LOCAL_RUN
BB1EM652 | _ISOLATOR | Rotating fuel spreader ISOLATOR |  | BB1EM652_ISOLATOR | ROTATING FUEL SPREADER | ISOLATOR |  |  | BB1EM652_ISOLATOR | ROTATING FUEL SPREADER ISOLATOR
BB1BL200 |  | Sootblower 1 |  | BB1BL200 | SOOTBLOWER 1 |  |  |  | BB1BL200 | SOOTBLOWER 1
BB1BL200 | _ISOLATOR | Sootblower 1 ISOLATOR |  | BB1BL200_ISOLATOR | SOOTBLOWER 1 ISOLATOR |  |  |  | BB1BL200_ISOLATOR | SOOTBLOWER 1 ISOLATOR
BB1BL201 |  | Sootblower 2 |  | BB1BL201 | SOOTBLOWER 2 |  |  |  | BB1BL201 | SOOTBLOWER 2
BB1BL201 | _ISOLATOR | Sootblower 2 ISOLATOR |  | BB1BL201_ISOLATOR | SOOTBLOWER 2 ISOLATOR |  |  |  | BB1BL201_ISOLATOR | SOOTBLOWER 2 ISOLATOR
BB1BL202 |  | Sootblower 3 |  | BB1BL202 | SOOTBLOWER 3 |  |  |  | BB1BL202 | SOOTBLOWER 3
BB1BL202 | _ISOLATOR | Sootblower 3 ISOLATOR |  | BB1BL202_ISOLATOR | SOOTBLOWER 3 ISOLATOR |  |  |  | BB1BL202_ISOLATOR | SOOTBLOWER 3 ISOLATOR
BB1BL203 |  | Sootblower 4 |  | BB1BL203 | SOOTBLOWER 4 |  |  |  | BB1BL203 | SOOTBLOWER 4
BB1BL203 | _ISOLATOR | Sootblower 4 ISOLATOR |  | BB1BL203_ISOLATOR | SOOTBLOWER 4 ISOLATOR |  |  |  | BB1BL203_ISOLATOR | SOOTBLOWER 4 ISOLATOR
BB1BL204 |  | Sootblower 5 |  | BB1BL204 | SOOTBLOWER 5 |  |  |  | BB1BL204 | SOOTBLOWER 5
BB1BL204 | _ISOLATOR | Sootblower 5 ISOLATOR |  | BB1BL204_ISOLATOR | SOOTBLOWER 5 ISOLATOR |  |  |  | BB1BL204_ISOLATOR | SOOTBLOWER 5 ISOLATOR
BB1BL205 |  | Sootblower 6 |  | BB1BL205 | SOOTBLOWER 6 |  |  |  | BB1BL205 | SOOTBLOWER 6
BB1BL205 | _ISOLATOR | Sootblower 6 ISOLATOR |  | BB1BL205_ISOLATOR | SOOTBLOWER 6 ISOLATOR |  |  |  | BB1BL205_ISOLATOR | SOOTBLOWER 6 ISOLATOR
BB1BL206 |  | Sootblower 7 |  | BB1BL206 | SOOTBLOWER 7 |  |  |  | BB1BL206 | SOOTBLOWER 7
BB1BL206 | _ISOLATOR | Sootblower 7 ISOLATOR |  | BB1BL206_ISOLATOR | SOOTBLOWER 7 ISOLATOR |  |  |  | BB1BL206_ISOLATOR | SOOTBLOWER 7 ISOLATOR
BB1EM815 |  | Fly ash container screw |  | BB1EM815 | FLY ASH CONTAINER SCREW |  |  |  | BB1EM815 | FLY ASH CONTAINER SCREW
BB1EM815 | _ISOLATOR | Fly ash container screw ISOLATOR |  | BB1EM815_ISOLATOR | FLY ASH CONTAINER SCREW I | SOLATOR |  |  | BB1EM815_ISOLATOR | FLY ASH CONTAINER SCREW I SOLATOR
BB1EM855 |  | Ash container screw |  | BB1EM855 | ASH CONTAINER SCREW |  |  |  | BB1EM855 | ASH CONTAINER SCREW
BB1EM855 | _ISOLATOR | Ash container screw ISOLATOR |  | BB1EM855_ISOLATOR | ASH CONTAINER SCREW ISOLA | TOR |  |  | BB1EM855_ISOLATOR | ASH CONTAINER SCREW ISOLA TOR
BB1EM401 |  | Exhaust fan 1 |  | BB1EM401 | EXHAUST FAN 1 |  |  |  | BB1EM401 | EXHAUST FAN 1
BB1EM401 | _ISOLATOR | Exhaust fan 1 ISOLATOR |  | BB1EM401_ISOLATOR | EXHAUST FAN 1 ISOLATOR |  |  |  | BB1EM401_ISOLATOR | EXHAUST FAN 1 ISOLATOR
BB1EM402 |  | Exhaust fan 2 |  | BB1EM402 | EXHAUST FAN 2 |  |  |  | BB1EM402 | EXHAUST FAN 2
BB1EM402 | _ISOLATOR | Exhaust fan 2 ISOLATOR |  | BB1EM402_ISOLATOR | EXHAUST FAN 2 ISOLATOR |  |  |  | BB1EM402_ISOLATOR | EXHAUST FAN 2 ISOLATOR
BB1EM403 |  | Exhaust fan 3 |  | BB1EM403 | EXHAUST FAN 3 |  |  |  | BB1EM403 | EXHAUST FAN 3
BB1EM403 | _ISOLATOR | Exhaust fan 3 ISOLATOR |  | BB1EM403_ISOLATOR | EXHAUST FAN 3 ISOLATOR |  |  |  | BB1EM403_ISOLATOR | EXHAUST FAN 3 ISOLATOR
BB1EM673 |  | Levelling roller 1 |  | BB1EM673 | LEVELLING ROLLER 1 |  |  |  | BB1EM673 | LEVELLING ROLLER 1
BB1EM673 | _LOCAL_MODE | Levelling roller 1 LOCAL_MODE |  | BB1EM673_LOCAL_MODE | LEVELLING ROLLER 1 | LOCAL_MODE |  |  | BB1EM673_LOCAL_MODE | LEVELLING ROLLER 1 LOCAL_MODE
BB1EM673 | _LOCAL_RUN_FWD | Levelling roller 1 LOCAL_RUN_FWD |  | BB1EM673_LOCAL_RUN_FWD | LEVELLING ROLLER 1 | LOCAL_RUN_FWD |  |  | BB1EM673_LOCAL_RUN_FWD | LEVELLING ROLLER 1 LOCAL_RUN_FWD
BB1EM673 | _LOCAL_RUN_REV | Levelling roller 1 LOCAL_RUN_REV |  | BB1EM673_LOCAL_RUN_REV | LEVELLING ROLLER 1 | LOCAL_RUN_REV |  |  | BB1EM673_LOCAL_RUN_REV | LEVELLING ROLLER 1 LOCAL_RUN_REV
BB1EM673 | _ISOLATOR | Levelling roller 1 ISOLATOR |  | BB1EM673_ISOLATOR | LEVELLING ROLLER 1 | ISOLATOR |  |  | BB1EM673_ISOLATOR | LEVELLING ROLLER 1 ISOLATOR
BB1EM674 |  | Levelling roller 2 |  | BB1EM674 | LEVELLING ROLLER 2 |  |  |  | BB1EM674 | LEVELLING ROLLER 2
BB1EM674 | _LOCAL_MODE | Levelling roller 2 LOCAL_MODE |  | BB1EM674_LOCAL_MODE | LEVELLING ROLLER 2 | LOCAL_MODE |  |  | BB1EM674_LOCAL_MODE | LEVELLING ROLLER 2 LOCAL_MODE
BB1EM674 | _LOCAL_RUN_FWD | Levelling roller 2 LOCAL_RUN_FWD |  | BB1EM674_LOCAL_RUN_FWD | LEVELLING ROLLER 2 | LOCAL_RUN_FWD |  |  | BB1EM674_LOCAL_RUN_FWD | LEVELLING ROLLER 2 LOCAL_RUN_FWD
BB1EM674 | _LOCAL_RUN_REV | Levelling roller 2 LOCAL_RUN_REV |  | BB1EM674_LOCAL_RUN_REV | LEVELLING ROLLER 2 | LOCAL_RUN_REV |  |  | BB1EM674_LOCAL_RUN_REV | LEVELLING ROLLER 2 LOCAL_RUN_REV
BB1EM674 | _ISOLATOR | Levelling roller 2 ISOLATOR |  | BB1EM674_ISOLATOR | LEVELLING ROLLER 2 | ISOLATOR |  |  | BB1EM674_ISOLATOR | LEVELLING ROLLER 2 ISOLATOR
BB1EM601 |  | Dust extraction rotary feeder |  | BB1EM601 | DUST EXTRACTION | ROTARY FEEDER |  |  | BB1EM601 | DUST EXTRACTION ROTARY FEEDER
BB1EM601 | _LOCAL_MODE | Dust extraction rotary feeder LOCAL_MODE |  | BB1EM601_LOCAL_MODE | DUST EXTRACTION | ROTARY FEEDER LOCAL_MODE |  |  | BB1EM601_LOCAL_MODE | DUST EXTRACTION ROTARY FEEDER LOCAL_MODE
BB1EM601 | _LOCAL_RUN_FWD | Dust extraction rotary feeder LOCAL_RUN_FWD |  | BB1EM601_LOCAL_RUN_FWD | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_F | WD |  | BB1EM601_LOCAL_RUN_FWD | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_F WD
BB1EM601 | _LOCAL_RUN_REV | Dust extraction rotary feeder LOCAL_RUN_REV |  | BB1EM601_LOCAL_RUN_REV | DUST EXTRACTION | ROTARY FEEDER LOCAL_RUN_R | EV |  | BB1EM601_LOCAL_RUN_REV | DUST EXTRACTION ROTARY FEEDER LOCAL_RUN_R EV
BB1EM601 | _ISOLATOR | Dust extraction rotary feeder ISOLATOR |  | BB1EM601_ISOLATOR | DUST EXTRACTION | ROTARY FEEDER ISOLATOR |  |  | BB1EM601_ISOLATOR | DUST EXTRACTION ROTARY FEEDER ISOLATOR
BB1IV650 |  | Slide gate valve |  | BB1IV650 | SLIDE GATE VALVE |  |  |  | BB1IV650 | SLIDE GATE VALVE
BB1IV650 | _LOCAL_MODE | Slide gate valve LOCAL_MODE |  | BB1IV650_LOCAL_MODE | SLIDE GATE VALVE | LOCAL_MODE |  |  | BB1IV650_LOCAL_MODE | SLIDE GATE VALVE LOCAL_MODE
BB1IV650 | _LOCAL_RUN_FWD | Slide gate valve LOCAL_RUN_FWD |  | BB1IV650_LOCAL_RUN_FWD | SLIDE GATE VALVE | LOCAL_RUN_FWD |  |  | BB1IV650_LOCAL_RUN_FWD | SLIDE GATE VALVE LOCAL_RUN_FWD
BB1IV650 | _LOCAL_RUN_REV | Slide gate valve LOCAL_RUN_REV |  | BB1IV650_LOCAL_RUN_REV | SLIDE GATE VALVE | LOCAL_RUN_REV |  |  | BB1IV650_LOCAL_RUN_REV | SLIDE GATE VALVE LOCAL_RUN_REV
BB1IV650 | _ISOLATOR | Slide gate valve ISOLATOR |  | BB1IV650_ISOLATOR | SLIDE GATE VALVE | ISOLATOR |  |  | BB1IV650_ISOLATOR | SLIDE GATE VALVE ISOLATOR
BB1EM657 |  | Fuel feeding rotary valve 1 |  | BB1EM657 | FUEL FEEDING | ROTARY VALVE 1 |  |  | BB1EM657 | FUEL FEEDING ROTARY VALVE 1
BB1EM657 | _LOCAL_MODE | Fuel feeding rotary valve 1 LOCAL_MODE |  | BB1EM657_LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 1 LOCAL_MODE |  |  | BB1EM657_LOCAL_MODE | FUEL FEEDING ROTARY VALVE 1 LOCAL_MODE
BB1EM657 | _LOCAL_RUN_FWD | Fuel feeding rotary valve 1 LOCAL_RUN_FWD |  | BB1EM657_LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | FWD |  | BB1EM657_LOCAL_RUN_FWD | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ FWD
BB1EM657 | _LOCAL_RUN_REV | Fuel feeding rotary valve 1 LOCAL_RUN_REV |  | BB1EM657_LOCAL_RUN_REV | FUEL FEEDING | ROTARY VALVE 1 LOCAL_RUN_ | REV |  | BB1EM657_LOCAL_RUN_REV | FUEL FEEDING ROTARY VALVE 1 LOCAL_RUN_ REV
BB1EM657 | _ISOLATOR | Fuel feeding rotary valve 1 ISOLATOR |  | BB1EM657_ISOLATOR | FUEL FEEDING | ROTARY VALVE 1 ISOLATOR |  |  | BB1EM657_ISOLATOR | FUEL FEEDING ROTARY VALVE 1 ISOLATOR
BB1EM656 |  | Fuel feeding rotary valve 2 |  | BB1EM656 | FUEL FEEDING | ROTARY VALVE 2 |  |  | BB1EM656 | FUEL FEEDING ROTARY VALVE 2
BB1EM656 | _LOCAL_MODE | Fuel feeding rotary valve 2 LOCAL_MODE |  | BB1EM656_LOCAL_MODE | FUEL FEEDING | ROTARY VALVE 2 LOCAL_MODE |  |  | BB1EM656_LOCAL_MODE | FUEL FEEDING ROTARY VALVE 2 LOCAL_MODE
BB1EM656 | _LOCAL_RUN_FWD | Fuel feeding rotary valve 2 LOCAL_RUN_FWD |  | BB1EM656_LOCAL_RUN_FWD | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | FWD |  | BB1EM656_LOCAL_RUN_FWD | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ FWD
BB1EM656 | _LOCAL_RUN_REV | Fuel feeding rotary valve 2 LOCAL_RUN_REV |  | BB1EM656_LOCAL_RUN_REV | FUEL FEEDING | ROTARY VALVE 2 LOCAL_RUN_ | REV |  | BB1EM656_LOCAL_RUN_REV | FUEL FEEDING ROTARY VALVE 2 LOCAL_RUN_ REV
BB1EM656 | _ISOLATOR | Fuel feeding rotary valve 2 ISOLATOR |  | BB1EM656_ISOLATOR | FUEL FEEDING | ROTARY VALVE 2 ISOLATOR |  |  | BB1EM656_ISOLATOR | FUEL FEEDING ROTARY VALVE 2 ISOLATOR
BB1EM856 |  | Purified sand screw conveyor |  | BB1EM856 | PURIFIED SAND | SCREW CONVEYOR |  |  | BB1EM856 | PURIFIED SAND SCREW CONVEYOR
BB1EM856 | _LOCAL_MODE | Purified sand screw conveyor LOCAL_MODE |  | BB1EM856_LOCAL_MODE | PURIFIED SAND | SCREW CONVEYOR LOCAL_MODE |  |  | BB1EM856_LOCAL_MODE | PURIFIED SAND SCREW CONVEYOR LOCAL_MODE
BB1EM856 | _LOCAL_RUN_FWD | Purified sand screw conveyor LOCAL_RUN_FWD |  | BB1EM856_LOCAL_RUN_FWD | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | FWD |  | BB1EM856_LOCAL_RUN_FWD | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ FWD
BB1EM856 | _LOCAL_RUN_REV | Purified sand screw conveyor LOCAL_RUN_REV |  | BB1EM856_LOCAL_RUN_REV | PURIFIED SAND | SCREW CONVEYOR LOCAL_RUN_ | REV |  | BB1EM856_LOCAL_RUN_REV | PURIFIED SAND SCREW CONVEYOR LOCAL_RUN_ REV
BB1EM856 | _ISOLATOR | Purified sand screw conveyor ISOLATOR |  | BB1EM856_ISOLATOR | PURIFIED SAND | SCREW CONVEYOR ISOLATOR |  |  | BB1EM856_ISOLATOR | PURIFIED SAND SCREW CONVEYOR ISOLATOR
BB1EM850 |  | 2nd pass fly ash rotary valve |  | BB1EM850 | 2ND PASS FLY ASH | ROTARY VALVE |  |  | BB1EM850 | 2ND PASS FLY ASH ROTARY VALVE
BB1EM850 | _LOCAL_MODE | 2nd pass fly ash rotary valve LOCAL_MODE |  | BB1EM850_LOCAL_MODE | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  |  | BB1EM850_LOCAL_MODE | 2ND PASS FLY ASH ROTARY VALVE LOCAL_MODE
BB1EM850 | _LOCAL_RUN_FWD | 2nd pass fly ash rotary valve LOCAL_RUN_ FWD |  | BB1EM850_LOCAL_RUN_FWD | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD |  | BB1EM850_LOCAL_RUN_FWD | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD
BB1EM850 | _LOCAL_RUN_REV | 2nd pass fly ash rotary valve LOCAL_RUN_ REV |  | BB1EM850_LOCAL_RUN_REV | 2ND PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | REV |  | BB1EM850_LOCAL_RUN_REV | 2ND PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV
BB1EM850 | _ISOLATOR | 2nd pass fly ash rotary valve ISOLATOR |  | BB1EM850_ISOLATOR | 2ND PASS FLY ASH | ROTARY VALVE ISOLATOR |  |  | BB1EM850_ISOLATOR | 2ND PASS FLY ASH ROTARY VALVE ISOLATOR
BB1EM851 |  | 3rd pass fly ash rotary valve |  | BB1EM851 | 3RD PASS FLY ASH | ROTARY VALVE |  |  | BB1EM851 | 3RD PASS FLY ASH ROTARY VALVE
BB1EM851 | _LOCAL_MODE | 3rd pass fly ash rotary valve LOCAL_MODE |  | BB1EM851_LOCAL_MODE | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_MODE |  |  | BB1EM851_LOCAL_MODE | 3RD PASS FLY ASH ROTARY VALVE LOCAL_MODE
BB1EM851 | _LOCAL_RUN_FWD | 3rd pass fly ash rotary valve LOCAL_RUN_ FWD |  | BB1EM851_LOCAL_RUN_FWD | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | FWD |  | BB1EM851_LOCAL_RUN_FWD | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ FWD
BB1EM851 | _LOCAL_RUN_REV | 3rd pass fly ash rotary valve LOCAL_RUN_ REV |  | BB1EM851_LOCAL_RUN_REV | 3RD PASS FLY ASH | ROTARY VALVE LOCAL_RUN_ | REV |  | BB1EM851_LOCAL_RUN_REV | 3RD PASS FLY ASH ROTARY VALVE LOCAL_RUN_ REV
BB1EM851 | _ISOLATOR | 3rd pass fly ash rotary valve ISOLATOR |  | BB1EM851_ISOLATOR | 3RD PASS FLY ASH | ROTARY VALVE ISOLATOR |  |  | BB1EM851_ISOLATOR | 3RD PASS FLY ASH ROTARY VALVE ISOLATOR

## prototype V6 spec
Object Name
objPrefix | objIndex | Column1 | objDesc |  | prefix | index | seperator | attribute | suffix | delimiter | result
P | 0 |  | numbered PLC IO block placeholder |  | P | 1 | _ | NAME |  |  | P1_NAME
D | 0 |  | numbered Device block placeholder |  | D | 1
C | 0 |  | numbered Cable block placeholder |  | C | 1
X | 0 |  | numbered PANEL block place holder |  | X | 1 |  | XIO | TI | _
VS | 0 |  | numbered VSD block placeholder |  | VS | 1
SS | 0 |  | numbered Soft Starter block placeholder |  | SS | 1
IS | 0 |  | numbered ISOLATOR block placeholder |  | IS | 1
Q | 0 |  | numbered PROTECTION block placeholder |  | Q | 1
W |  |  | WIRE
M | 0 |  | numbered MOTOR block placeholder |  | M | 1
Object Attribute |  |  |  | len
Column1 | Column2 | Column3 | Column4 | 4
NAME |  | NAME |  | 4
SLOT |  | SLOT |  | 4 | DRAWING
CHAN |  | CHAN |  | 3 | PROTOTYPE
TAG |  | TAG |  | 5 | X1_PNL
DESC2 |  | DESC2 |  | 5 | X1_PDESC
DESC3 |  | DESC3 |  | 5 | X1_24DC
DESC4 |  | DESC4 |  | 3 | X1_0DC
TAG |  | TAG | 0 | 3 | X1_24ACL
PNL |  | PNL |  | 3 | X1_24ACN
MFG |  | MFG |  | 4 | X1_230ACL1
CATN |  | CATN |  | 4 | X1_230ACN
CATD |  | CATD |  | 3 | X1_XIO
XIO |  | XIO | 0 | 6 | X1_XIO_TI
XIO | TI | XIO_TI |  | 6 | X1_XIO_FI
XIO | FI | XIO_FI |  | 6 | X1_XIO_KI
XIO | KI | XIO_KI |  | 3 | X1_XDB
XDB |  | XDB |  | 6 | X1_XDB_TI
XDB | TI | XDB_TI |  | 6 | X1_XDB_FI
XDB | FI | XDB_FI |  | 6 | X1_XDB_KI
XDB | KI | XDB_KI |  | 6 | X2_PNL
XDB | QI | XDB_QI |  | 5 | X2_PDESC
24VDC |  | 24VDC |  | 4 | X2_24DC
0VDC |  | 0VDC |  | 5 | X2_0DC
24VAC |  | 24VAC |  | 7 | X2_24ACL
24VAC | N | 24VAC_N |  | 7 | X2_24ACN
230V | L1 | 230V_L1 |  | 7 | X2_230ACL1
230V | L2 | 230V_L2 |  | 7 | X2_230ACN
230V | L3 | 230V_L3 |  | 6 | X2_XIO
230V | N | 230V_N |  | #REF! | X2_XIO_TI
TYPE |  | TYPE |  | 4 | X2_XIO_FI
|  |  |  | 0 | X2_XIO_KI
|  |  |  | 0 | X2_XDB
DWG | PREFIX | DWG_PREFIX |  | 10 | X2_XDB_TI
DWG | NUMBER | DWG_NUMBER |  | 10 | X2_XDB_FI
DRAWING |  | DRAWING |  | 7 | X2_XDB_KI
PROTOTYPE |  | PROTOTYPE |  | 9 | P1_NAME
CABLE | TYPE | CABLE_TYPE |  | 10 | P1_RACK
CABLE | DESC | CABLE_DESC |  | 10 | P1_SLOT
|  | 0 |  | 1 | P1_CHAN
|  | 0 |  | 1 | P1_MFG
SET_TO |  | SET_TO |  | 6 | P1_CATN
KW |  | KW |  | 2 | P1_CATD
AMPS |  | AMPS |  | 4 | P1_TAG
VOLTS |  | VOLTS |  | 5 | P1_DESC2
|  |  |  | 0 | P1_DESC3
P1_DESC4
Generic Power Cable Spec |  |  |  |  | P1_T1
VoltageRating | insulation | Cores | Size | Column1 | P1_T2
300/500 | PVC | 1 | 1.5 | Neutral-Screen | P2_NAME
0.6/1kV | XPLE | 36 |  | VSD | P2_RACK
|  |  |  | SWA | P2_SLOT
|  |  |  | FLEX | P2_CHAN
P2_MFG
P2_CATN
P2_CATD
P2_TAG
PVC | P |  |  |  | P2_DESC2
XPLE | X |  |  |  | P2_DESC3
Neutral Screen | NS |  |  |  | P2_DESC4
Steel-Wire-Armour | S |  |  |  | P2_T1
Flex | F |  |  |  | D1_TAG
Marine | M |  |  |  | D1_DESC2
D1_DESC3
Seperator: | - |  |  |  | D1_DESC4
D1_VDESC
VoltageRating | Examples | Description | NOTES |  | D1_TYPE
0 | 120V RMS | Instrumentation/Comms cables. Use for Extra Low Voltage Only |  |  | D1_T1
1 | 300/500 0.6/1kV | Suitible for general 230/400V applications |  |  | D1_T2
2 | >1kV | MV,HV Cables |  |  | D2_TAG
D2_DESC2
Insulation | Examples | Description | NOTES |  | D2_DESC3
P | TPS, R75 | General purpose cable. 75deg max |  |  | D2_DESC4
X | XPLE, R90 | Suitible for general 230/400V applications |  |  | D2_VDESC
X+ |  | Hi temp cable suitible for eg. 120, 150 degrees |  |  | D2_TYPE
D2_T1
D2_T2
Cores | Examples | Description | NOTES |  | C1_MFG
[n]C |  | Number of cores |  |  | C1_CATN
[n]PR |  | Number of Pairs |  |  | C1_CATD
+E |  | plus earth |  |  | C1_TAG
C1_COR1
Properties | Examples | Description | NOTES |  | C1_COR2
V |  | VSD Cable | Can include any number of entries. Can be ommited if not applicible |  | C2_MFG
N |  | Neutral-Screen |  |  | C2_CATN
A |  | Steel-Wire Armour |  |  | C2_CATD
F |  | Flexible |  |  | C2_TAG
M |  | Marine Rated |  |  | C2_COR1
T |  | Twisted-Pair? |  |  | C2_COR2
S |  | Shielded?
Examples
| 0P-3PR-S-1.5 | Instrumentation PVC 3 Pair shielded cable, 1.5mm^2
| 2X-3C+E-VF-35 | Power XPLE 3C+E Flexible VSD cable, 35mm

## Sheet4
5 | 5._L0
93 | 93._L0
102 | 102._L0
103 | 103._L0
104 | 104._L0
105 | 105._L0
106 | 106._L0
107 | 107._L0
108 | 108._L0
109 | 109._L0
110 | 110._L0
111 | 111._L0
112 | 112._L0
113 | 113._L0
114 | 114._L0
115 | 115._L0
116 | 116._L0
117 | 117._L0
118 | 118._L0
119 | 119._L0
120 | 120._L0
121 | 121._L0
122 | 122._L0
123 | 123._L0
124 | 124._L0
125 | 125._L0
126 | 126._L0
127 | 127._L0
128 | 128._L0
129 | 129._L0
130 | 130._L0
131 | 131._L0
132 | 132._L0
133 | 133._L0
134 | 134._L0
135 | 135._L0
136 | 136._L0
137 | 137._L0
138 | 138._L0
139 | 139._L0
140 | 140._L0
141 | 141._L0
142 | 142._L0
143 | 143._L0
144 | 144._L0
145 | 145._L0
146 | 146._L0
150 | 150._L0
151 | 151._L0
152 | 152._L0
153 | 153._L0
154 | 154._L0
155 | 155._L0
156 | 156._L0
157 | 157._L0
158 | 158._L0
159 | 159._L0
160 | 160._L0
161 | 161._L0
162 | 162._L0
163 | 163._L0
164 | 164._L0
165 | 165._L0
166 | 166._L0
167 | 167._L0
168 | 168._L0
169 | 169._L0
170 | 170._L0
171 | 171._L0
172 | 172._L0
173 | 173._L0
174 | 174._L0
175 | 175._L0
176 | 176._L0
177 | 177._L0
178 | 178._L0
179 | 179._L0
180 | 180._L0
181 | 181._L0
182 | 182._L0
183 | 183._L0
184 | 184._L0
185 | 185._L0
186 | 186._L0
187 | 187._L0
188 | 188._L0
189 | 189._L0
190 | 190._L0
191 | 191._L0
192 | 192._L0
193 | 193._L0
194 | 194._L0
195 | 195._L0
196 | 196._L0
197 | 197._L0
198 | 198._L0
233 | 233._L0
234 | 234._L0
235 | 235._L0
236 | 236._L0
237 | 237._L0
238 | 238._L0
239 | 239._L0
240 | 240._L0
241 | 241._L0
242 | 242._L0
243 | 243._L0
244 | 244._L0
245 | 245._L0
246 | 246._L0
247 | 247._L0
248 | 248._L0
249 | 249._L0
250 | 250._L0
267 | 267._L0
268 | 268._L0
269 | 269._L0
270 | 270._L0
271 | 271._L0
272 | 272._L0
329 | 329._L0
330 | 330._L0
331 | 331._L0
332 | 332._L0
333 | 333._L0
334 | 334._L0
335 | 335._L0
336 | 336._L0
337 | 337._L0
338 | 338._L0
339 | 339._L0
340 | 340._L0
341 | 341._L0
346 | 346._L0
347 | 347._L0
348 | 348._L0
349 | 349._L0
364 | 364._L0
365 | 365._L0

## MSIO
[10 empty] | MSIO-list | [26 empty] | Date |  | Name |  |  |  | Remarks | [23 empty] | New data with green | Changes with yellow |  | Revision
Revision 3
| Basic information | [8 empty] | Motor | [8 empty] | Supply | [7 empty] | I/O | [9 empty] | Scale |  |  | PLC I/O ( Process) |  |  |  | SIS I/O (Safety) |  |  |  | Bus I/O - Register |  |  |  | Alarm threshold |  |  |  | Instrument |  |  |  | Device |  |  | Supplier | Documentation |  |  | Location |  | Revision
Adresses
Row index | Area | Process | Device | Equipment | TAG | Description | Description 2. language | Short Description (n char) | Column1 | Power (kW) | Current (A) | Speed (rpm) | Voltage (V) | Cos φ | Thermistor | ATEX | Column2 | Column3 | Electrical center | Cubicle | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Signal suffix | W | Signal TAG | Column10 | Column11 | Rack | Slot | Chan. | Addr. | Term. | Min | Max | Unit | DI | DO | AI | AO | SDI | SDO | SAI | SAO | BDI | BDO | BAI | BAO | LL | L | H | HH | Transmitter type | Type of signal | Switch state | Voltage | Manufacturer | Model | Connection | Name | P&ID | Typical | Hook-up | Electrical room | Cabinet | Remarks | Issue
0 |  | BB1 | EM | 001 | BB1EM001 | Feed water pump 1 |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Sulzer/ABB | 4001 | FRQ_DIR |  |  |  | Tag changed | 3
1 | [27 empty] | Running | BB1PU001 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
2 | [27 empty] | MCC Fault | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
3 | [27 empty] | Safety switch | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
4 | [27 empty] | VFD Alarm | BB1PU001 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
5 | [27 empty] | Run command | BB1PU001 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
6 | [27 empty] | Current | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
7 | [27 empty] | Speed reference | BB1PU001 | [21 empty] | X | [13 empty] | FRQ_DIR
8 | [27 empty] | Actual speed | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
9 | [27 empty] | Torque | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
10 | [27 empty] | RPM | BB1PU001 | [20 empty] | X | [14 empty] | FRQ_DIR
11 |  | BB1 | EM | 002 | BB1EM002 | Feed water pump 2 |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Sulzer/ABB | 4001 | FRQ_DIR |  |  |  | Tag changed | 3
12 | [27 empty] | Running | BB1PU002 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
13 | [27 empty] | MCC Fault | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
14 | [27 empty] | Safety switch | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
15 | [27 empty] | VFD Alarm | BB1PU002 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
16 | [27 empty] | Run command | BB1PU002 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
17 | [27 empty] | Current | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
18 | [27 empty] | Speed reference | BB1PU002 | [21 empty] | X | [13 empty] | FRQ_DIR
19 | [27 empty] | Actual speed | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
20 | [27 empty] | Torque | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
21 | [27 empty] | RPM | BB1PU002 | [20 empty] | X | [14 empty] | FRQ_DIR
873 |  | BB1 | EM | 703 | BB1EM703 | Chemical filling pump 1 |  | Best guess < 1kW |  |  |  |  | 240 | [26 empty] | 4 | 1 | [22 empty] | 4001 | DOL_DIRH |  |  |  | Pump added | 3
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local run command | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local mode switch | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
873 |  | BB1 | EM | 704 | BB1EM704 | Chemical filling pump 2 |  | Best guess < 1kW |  |  |  |  | 240 | [26 empty] | 4 | 1 | [22 empty] | 4001 | DOL_DIRH |  |  |  | Pump added | 3
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local run command | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
[28 empty] | Local mode switch | [11 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIRH |  |  |  | Pump added | 3
22 |  | BB1 | PU | 800 | BB1PU800 | Chemical dosing pump 1 |  |  |  | 0,37 |  |  | 230 | [29 empty] | 1 | [20 empty] | 4001 | CHEMICAL_PUMP |  | Field IO |  | Motor details | 1
23 | [27 empty] | Control signal | BB1PU800 | [13 empty] | X | [21 empty] | CHEMICAL_PUMP |  | Field IO
28 |  | BB1 | LS | 700 | BB1LS700 | Chemical tank 1 level switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | LS001 | Field IO |  | Instrument added | 1
29 | [27 empty] | Binary State | BB1LT001 | [10 empty] | X | [24 empty] | MEAS_BIN |  | Field IO
24 |  | BB1 | PU | 801 | BB1PU801 | Chemical dosing pump 2 |  |  |  | 0,37 |  |  | 230 | [29 empty] | 1 | [20 empty] | 4001 | CHEMICAL_PUMP |  | Field IO |  | Motor details | 1
25 | [27 empty] | Control signal | BB1PU801 | [13 empty] | X | [21 empty] | CHEMICAL_PUMP |  | Field IO
28 |  | BB1 | LS | 701 | BB1LS701 | Chemical tank 2 level switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | LS001 | Field IO |  | Instrument added | 1
29 | [27 empty] | Binary State | BB1LT001 | [10 empty] | X | [24 empty] | MEAS_BIN |  | Field IO
26 |  | BB1 | PT | 200 | BB1PT200 | Feed water tank pressure | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [13 empty] | Pressure |  |  |  | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
27 | [27 empty] | Measurement | BB1PT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
28 |  | BB1 | LT | 001 | BB1LT001 | Feed water tank level 1 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | LT001 | Field IO
29 | [27 empty] | Measurement | BB1LT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
30 |  | BB1 | LT | 002 | BB1LT002 | Feed water tank level 2 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | LT001 | Field IO
31 | [27 empty] | Measurement | BB1LT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
32 |  | BB1 | PT | 005 | BB1PT005 | Feed water pressure after valve | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
33 | [27 empty] | Measurement | BB1PT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
34 |  | BB1 | FT | 001 | BB1FT001 | Feed water flow and control | [35 empty] | 1 | [21 empty] | 4001 | MEAS_ANA | FT002 | Field IO
35 | [27 empty] | Measurement | BB1FT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
36 |  | BB1 | CV | 200 | BB1CV200 | Steam from drum control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
37 | [27 empty] | Setpoint position | BB1CV200 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
38 | [27 empty] | Position feedback | BB1CV200 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
39 |  | BB1 | TT | 001 | BB1TT001 | Feed water temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4001 | MEAS_ANA | TT001 | Field IO
40 | [27 empty] | Measurement | BB1TT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
41 |  | BB1 | IV | 002 | BB1IV002 | Feedwater pump 1 on-off valve |  |  |  | 0.25 | 1.9 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA10.2-22 + RWG |  | Konwell/Auma | 4001 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
43 |  | BB1 | TT | 002 | BB1TT002 | Feed water pump 2 bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
44 | [27 empty] | Measurement | BB1TT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
45 |  | BB1 | GS | 004 | BB1GS004 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
46 | [27 empty] | Binary state | BB1GS004 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
47 |  | BB1 | PT | 004 | BB1PT004 | Feed water pressure before valve | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
48 | [27 empty] | Measurement | BB1PT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
49 |  | BB1 | GS | 003 | BB1GS003 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
50 | [27 empty] | Binary state | BB1GS003 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
51 |  | BB1 | IV | 003 | BB1IV003 | Feed water pump 2 on-off valve |  |  |  | 0.25 | 1.9 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA10.2-22 + RWG |  | Konwell/Auma | 4001 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
53 |  | BB1 | PT | 002 | BB1PT002 | Feed water pump 2 pressure side pressure | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
54 | [27 empty] | Measurement | BB1PT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
55 |  | BB1 | CV | 001 | BB1CV001 | Make-up water control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
56 | [27 empty] | Setpoint position | BB1CV001 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
57 | [27 empty] | Position feedback | BB1CV001 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
58 |  | BB1 | PT | 006 | BB1PT006 | FW suction line strainer pressure diff. | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67LGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | PT004 | Field IO
59 | [27 empty] | Measurement | BB1PT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
60 |  | BB1 | GS | 001 | BB1GS001 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
61 | [27 empty] | Binary state | BB1GS001 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
62 |  | BB1 | PT | 007 | BB1PT007 | FW suction line strainer pressure diff. | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67LGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4001 | MEAS_ANA | PT004 | Field IO
63 | [27 empty] | Measurement | BB1PT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
64 |  | BB1 | TT | 005 | BB1TT005 | FW pump 2 motor winding temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
65 | [27 empty] | Measurement | BB1TT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
66 |  | BB1 | PT | 001 | BB1PT001 | Feed water pump 1 pressure side pressure | [30 empty] | 0 | 75 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1UGJGCJA1+Z1 | G1/2 |  | 4001 | MEAS_ANA | PT001.1 | Field IO
67 | [27 empty] | Measurement | BB1PT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
68 |  | BB1 | GS | 002 | BB1GS002 | Feed water pump suction side shut-off valve limit switch | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
69 | [27 empty] | Binary state | BB1GS002 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
70 |  | BB1 | CV | 002 | BB1CV002 | Feed water control valve | [35 empty] | 1 | 1 | [16 empty] | Siemens | Sipart PS2+IY-module |  |  | 4001 | CONT_VLV |  | Field IO |  | Positioner type added | 1
71 | [27 empty] | Setpoint position | BB1CV002 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
72 | [27 empty] | Position feedback | BB1CV002 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
73 |  | BB1 | TT | 004 | BB1TT004 | FW pump 1 motor winding temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA | TT005 | Field IO
74 | [27 empty] | Measurement | BB1TT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
75 |  | BB1 | TT | 003 | BB1TT003 | FW pump 1 motor bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4001 | MEAS_ANA |  | Field IO
76 | [27 empty] | Measurement | BB1TT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
77 |  | BB1 | SV | 410 | BB1SV410 | Feed water tank overflow valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4001 | BIN_VLV | AA005 | Field IO |  | tag changed | 1
78 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1IV001 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | 24 VDC feed added | 1
79 |  | BB1 | GS | 005 | BB1GS005 | FW tank overflow On-Off valve position | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
80 | [27 empty] | Binary state | BB1GS005 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
81 |  | BB1 | GS | 006 | BB1GS006 | FW tank overflow On-Off valve position | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO
82 | [27 empty] | Binary state | BB1GS006 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
83 |  | BB1 | GS | 007 | BB1GS007 | Feedwater pump 1 on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
84 | [27 empty] | Binary state | BB1GS007 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
85 |  | BB1 | GS | 008 | BB1GS008 | Feedwater pump 1 on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
86 | [27 empty] | Binary state | BB1GS008 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
87 |  | BB1 | GS | 009 | BB1GS009 | Feed water pump 2 on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
88 | [27 empty] | Binary state | BB1GS009 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
89 |  | BB1 | GS | 010 | BB1GS010 | Feed water pump 2 on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | MCC
90 | [27 empty] | Binary state | BB1GS010 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
91 |  | BB1 | LT | 101 | BB1LT101 | Steam drum level 1 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
92 | [27 empty] | Measurement SRS | BB1LS100 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
91 |  | BB1 | LS | 103 | BB1LS103 | Steam drum level switch 1 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | LS003 | SRS |  | Instrument added | 2
92 | [27 empty] | Binary state SRS | BB1LS100 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Instrument added | 2
91 |  | BB1 | LS | 104 | BB1LS104 | Steam drum level switch 2 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | LS003 | SRS |  | Instrument added | 2
92 | [27 empty] | Binary state SRS | BB1LS100 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Instrument added | 2
93 |  | BB1 | IV | 004 | BB1IV004 | Boiler bottom blow down on-off valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4002 | BIN_VLV | AA005 | Field IO
94 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1IV004 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | 24 VDC feed added | 1
83 |  | BB1 | GS | 011 | BB1GS011 | Boiler bottom blow down on-off valve limit switch open | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 1
84 | [27 empty] | Binary state | BB1GS007 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
85 |  | BB1 | GS | 012 | BB1GS012 | Boiler bottom blow down on-off valve limit switch close | [33 empty] | 1 | [23 empty] | 4001 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 1
86 | [27 empty] | Binary state | BB1GS008 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
95 |  | BB1 | PT | 203 | BB1PT203 | Steam drum pressure 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4002 | MEAS_ANA_SRS | PT001.1 | SRS
96 | [27 empty] | Measurement SRS | BB1PT203 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
97 |  | BB1 | TT | 008 | BB1TT008 | Temperature after economizer | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4002 | MEAS_ANA | TT001 | Field IO
98 | [27 empty] | Measurement | BB1TT008 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
99 |  | BB1 | LT | 102 | BB1LT102 | Steam drum level 2 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
100 | [27 empty] | Measurement SRS | BB1LS101 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
101 |  | BB1 | PT | 201 | BB1PT201 | Steam drum pressure 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4002 | MEAS_ANA_SRS | PT001.1 | SRS
102 | [27 empty] | Measurement SRS | BB1PT201 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
103 |  | BB1 | LT | 103 | BB1LT103 | Steam drum level 3 |  | SIL2 classified transmitter | [28 empty] | -300 | 300 | mm | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4002 | MEAS_ANA_SRS | LT001 | SRS |  | Tag changed | 3
104 | [27 empty] | Measurement SRS | BB1LS102 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
105 |  | BB1 | FT | 200 | BB1FT200 | Heating steam to feed water tank flow measurement | [30 empty] | 0 | 5 | t/h |  |  | 1 | [21 empty] | 4002 | MEAS_ANA | FT001 | Field IO
106 | [27 empty] | Measurement | BB1FT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
107 |  | BB1 | HS | 101 | BB1HS101 | Boiler emergency shutdown switch 1 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
108 | [27 empty] | Binary state SRS | BB1HS101 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
109 |  | BB1 | HS | 103 | BB1HS103 | Boiler emergency shutdown switch 3 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
111 |  | BB1 | TT | 009 | BB1TT009 | Temperature before economizer | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4002 | MEAS_ANA | TT001 | Field IO
112 | [27 empty] | Measurement | BB1TT009 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
113 |  | BB1 | HS | 104 | BB1HS104 | Boiler emergency shutdown switch 4 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
114 | [27 empty] | Binary state SRS | BB1HS104 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
115 |  | BB1 | HS | 102 | BB1HS102 | Boiler emergency shutdown switch 2 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
116 | [27 empty] | Binary state SRS | BB1HS102 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
117 |  | BB1 | HS | 105 | BB1HS105 | Boiler emergency shutdown switch 5 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
118 | [27 empty] | Binary state SRS | BB1HS105 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
119 |  | BB1 | HS | 106 | BB1HS106 | Boiler emergency shutdown switch 6 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
120 | [27 empty] | Binary state SRS | BB1HS106 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
121 |  | BB1 | HS | 107 | BB1HS107 | Boiler emergency shutdown switch 7 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
122 | [27 empty] | Binary state SRS | BB1HS107 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
123 |  | BB1 | HS | 108 | BB1HS108 | Boiler emergency shutdown switch 8 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
124 | [27 empty] | Binary state SRS | BB1HS108 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
125 |  | BB1 | HS | 109 | BB1HS109 | Boiler emergency shutdown switch 9 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
126 | [27 empty] | Binary state SRS | BB1HS109 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
127 |  | BB1 | HS | 110 | BB1HS110 | Boiler emergency shutdown switch 10 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
128 | [27 empty] | Binary state SRS | BB1HS110 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
129 |  | BB1 | HS | 111 | BB1HS111 | Boiler emergency shutdown switch 11 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
130 | [27 empty] | Binary state SRS | BB1HS111 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
131 |  | BB1 | HS | 112 | BB1HS112 | Boiler emergency shutdown switch 12 | [37 empty] | 1 | [19 empty] | 4002 | MEAS_BIN_SRS | CH003 | SRS
132 | [27 empty] | Binary state SRS | BB1HS112 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS
133 |  | BB1 | TT | 200 | BB1TT200 | Main steam temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4003 | MEAS_ANA | TT001 | Field IO
134 | [27 empty] | Measurement | BB1TT200 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
135 |  | BB1 | FT | 202 | BB1FT202 | Main steam flow | [30 empty] | 0 | 30 | t/h |  |  | 1 | [21 empty] | 4003 | MEAS_ANA | FT001 | Field IO
136 | [27 empty] | Measurement | BB1FT202 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
137 |  | BB1 | IV | 202 | BB1IV202 | Main steam valve by-pass valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
138 | [27 empty] | Open direction command | BB1IV202 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
139 | [27 empty] | Close direction command | BB1IV202 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
140 | [27 empty] | Torque limit open direction | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
141 | [27 empty] | Torque limit close direction | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
142 | [27 empty] | Actuator fault | BB1IV202 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
143 | [27 empty] | Position | BB1IV202 | [12 empty] | X | [22 empty] | MTR_VLV
144 |  | BB1 | CV | 201 | BB1CV201 | Start-up valve |  |  |  | 0.06 | 0.6 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SAR10.2 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
145 | [27 empty] | Open direction command | BB1CV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
146 | [27 empty] | Close direction command | BB1CV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
147 | [27 empty] | Torque limit open direction | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
148 | [27 empty] | Torque limit close direction | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
149 | [27 empty] | Actuator fault | BB1CV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
150 | [27 empty] | Position | BB1CV201 | [12 empty] | X | [22 empty] | MTR_VLV
151 |  | BB1 | IV | 201 | BB1IV201 | Main steam valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA14.2-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
152 | [27 empty] | Open direction command | BB1IV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
153 | [27 empty] | Close direction command | BB1IV201 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
154 | [27 empty] | Torque limit open direction | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
155 | [27 empty] | Torque limit close direction | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
156 | [27 empty] | Actuator fault | BB1IV201 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
157 | [27 empty] | Position | BB1IV201 | [12 empty] | X | [22 empty] | MTR_VLV
158 |  | BB1 | FT | 201 | BB1FT201 | Steam flow to sootblowing and air preheater | [30 empty] | 0 | 8 | t/h |  |  | 1 | [21 empty] | 4003 | MEAS_ANA | FT001 | Field IO
159 | [27 empty] | Measurement | BB1FT201 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
160 |  | BB1 | IV | 200 | BB1IV200 | Start-up check valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4003 | MTR_VLV | AA001 |  |  | Model added | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
167 |  | BB1 | GS | 221 | BB1GS221 | Main steam valve by-pass open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
168 | [27 empty] | Binary state | BB1GS221 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
169 |  | BB1 | GS | 222 | BB1GS222 | Main steam valve by-pass close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
170 | [27 empty] | Binary state | BB1GS222 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
171 |  | BB1 | GS | 223 | BB1GS223 | Main steam line valve open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
172 | [27 empty] | Binary state | BB1GS223 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
173 |  | BB1 | GS | 224 | BB1GS224 | Main steam line valve close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
174 | [27 empty] | Binary state | BB1GS224 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
175 |  | BB1 | GS | 225 | BB1GS225 | Start-up line ON-OFF valve open limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
176 | [27 empty] | Binary state | BB1GS225 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
177 |  | BB1 | GS | 226 | BB1GS226 | Start-up line ON-OFF valve close limit switch | [33 empty] | 1 | [23 empty] | 4003 | MEAS_BIN | XS002/XS004 | MCC
178 | [27 empty] | Binary state | BB1GS226 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
179 |  | BB1 | GS | 200 | BB1GS200 | Sootblower 1 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
180 | [27 empty] | Binary state | BB1GS200 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
181 |  | BB1 | GS | 201 | BB1GS201 | Sootblower 1 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
182 | [27 empty] | Binary state | BB1GS201 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
183 |  | BB1 | GS | 203 | BB1GS203 | Sootblower 2 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
184 | [27 empty] | Binary state | BB1GS203 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
185 |  | BB1 | GS | 204 | BB1GS204 | Sootblower 2 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
186 | [27 empty] | Binary state | BB1GS204 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
187 |  | BB1 | GS | 205 | BB1GS205 | Sootblower 3 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
188 | [27 empty] | Binary state | BB1GS205 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
189 |  | BB1 | GS | 206 | BB1GS206 | Sootblower 3 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
190 | [27 empty] | Binary state | BB1GS206 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
191 |  | BB1 | GS | 207 | BB1GS207 | Sootblower 5 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
192 | [27 empty] | Binary state | BB1GS207 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
193 |  | BB1 | GS | 208 | BB1GS208 | Sootblower 5 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
194 | [27 empty] | Binary state | BB1GS208 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
195 |  | BB1 | GS | 209 | BB1GS209 | Sootblower 6 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
196 | [27 empty] | Binary state | BB1GS209 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
197 |  | BB1 | GS | 210 | BB1GS210 | Sootblower 6 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
198 | [27 empty] | Binary state | BB1GS210 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
199 |  | BB1 | GS | 211 | BB1GS211 | Sootblower 7 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
200 | [27 empty] | Binary state | BB1GS211 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
201 |  | BB1 | GS | 212 | BB1GS212 | Sootblower 7 IN limit switch | [6 empty] | 24 | [26 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
202 | [27 empty] | Binary state | BB1GS212 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
203 |  | BB1 | GS | 213 | BB1GS213 | Sootblower 8 OUT limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
204 | [27 empty] | Binary state | BB1GS213 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
205 |  | BB1 | GS | 214 | BB1GS214 | Sootblower 8 IN limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | Field IO
206 | [27 empty] | Binary state | BB1GS214 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
207 |  | BB1 | IV | 203 | BB1IV203 | Sootblowing line on-off valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SA7.6-22 + RWG |  | Konwell/Auma | 4004 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
209 |  | BB1 | TT | 201 | BB1TT201 | Sootblowing line temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [21 empty] | 4004 | MEAS_ANA | TT001 | Field IO
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
209 |  | BB1 | TT |  |  | Electrical room temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [22 empty] | MEAS_ANA | TT007 |  |  | Instrument added | 3
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA
209 |  | BB1 | TT |  |  | PLC-cabinet temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [22 empty] | MEAS_ANA | TT007 |  |  | Instrument added | 3
210 | [27 empty] | Measurement | BB1TT201 | [12 empty] | X | [22 empty] | MEAS_ANA
211 |  | BB1 | GS | 227 | BB1GS227 | Sootblowing line on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | MCC
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 228 | BB1GS228 | Sootblowing line on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4004 | MEAS_BIN | XS002/XS004 | MCC
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
215 |  | BB1 | BL | 200 | BB1BL200 | Sootblower 1 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
221 |  | BB1 | BL | 201 | BB1BL201 | Sootblower 2 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
227 |  | BB1 | BL | 202 | BB1BL202 | Sootblower 3 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
233 |  | BB1 | BL | 203 | BB1BL203 | Sootblower 4 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
239 |  | BB1 | BL | 204 | BB1BL204 | Sootblower 5 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
245 |  | BB1 | BL | 205 | BB1BL205 | Sootblower 6 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
251 |  | BB1 | BL | 206 | BB1BL206 | Sootblower 7 |  |  |  | 0,37 |  |  | 415 | [34 empty] | 3 | 2 | 1 | [12 empty] | Rosink/SEW | 4004 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running IN | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running OUT | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command IN | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command OUT | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
257 |  | BB1 | TT | 006 | BB1TT006 | Blow down tank temperature and control | [30 empty] | 0 | 100 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4005 | MEAS_ANA | TT001 | Field IO
258 | [27 empty] | Measurement | BB1TT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
259 |  | BB1 | CV | 003 | BB1CV003 | Continuous blow down valve |  |  |  |  | 2 |  | 240 | [26 empty] | 3 | 2 | 1 | [17 empty] | Gestra | BAE 46-1-ANSI + EF10-1 + 1000 ohm |  | Konwell/Gestra | 4005 | MTR_VLV | AA001 |  |  | Model added | 1
260 | [27 empty] | Open direction command | BB1CV003 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
261 | [27 empty] | Close direction command | BB1CV003 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
262 | [27 empty] | Torque limit open direction | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
263 | [27 empty] | Torque limit close direction | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
264 | [27 empty] | Actuator fault | BB1CV003 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
265 | [7 empty] | needs R/I converter 0...10 Kohm=4..20 mA | [19 empty] | Position | BB1CV003 | [12 empty] | X | [22 empty] | MTR_VLV
266 |  | BB1 | SV | 001 | BB1SV001 | Blow down tank cooling on/off valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4005 | BIN_VLV | AA005 | Field IO
267 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1SV001 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
268 |  | BB1 | PT | 205 | BB1PT205 | Steam outlet pressure from accumulator | [30 empty] | 0 | 40 | bar(g) | [6 empty] | 1 | [13 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA_SRS | PT001.1 | SRS |  | Moved to SRS | 2
269 | [27 empty] | Measurement SRS | BB1PT205 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS |  | Moved to SRS | 2
270 |  | BB1 | TT | 202 | BB1TT202 | Steam outlet temperature from accumulator | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
271 | [27 empty] | Measurement | BB1TT202 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
272 |  | BB1 | PT | 207 | BB1PT207 | Accumulator pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
273 | [27 empty] | Measurement | BB1PT207 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
274 |  | BB1 | CV | 203 | BB1CV203 | Steam accumulator pressure control valve |  |  |  | 0.25 | 1.8 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | AUMA | SAR14.2 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 1
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV
211 |  | BB1 | GS | 231 | BB1GS231 | Steam accumulator pressure control valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | Field IO |  | Signal added | 1
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
213 |  | BB1 | GS | 230 | BB1GS230 | Steam accumulator pressure control valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | Field IO |  | Signal added | 1
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
277 |  | BB1 | TT | 007 | BB1TT007 | Accumulator temperature | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
278 | [27 empty] | Measurement | BB1TT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
279 |  | BB1 | TT | 203 | BB1TT203 | 18bar(g) steam temperature |  | Transmitter wired to energy calculator | [28 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4006 | MEAS_ANA | TT001 | Field IO
280 | [27 empty] | Measurement | BB1TT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
281 |  | BB1 | CV | 202 | BB1CV202 | Steam pressure reduction valve |  |  |  | 0.25 | 1.8 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SAR14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 233 | BB1GS233 | Steam pressure reduction valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 232 | BB1GS232 | Steam pressure reduction valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
284 |  | BB1 | PT | 204 | BB1PT204 | Main steam pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
285 | [27 empty] | Measurement | BB1PT204 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
286 |  | BB1 | LT | 004 | BB1LT004 | Steam accumulator level 2 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4006 | MEAS_ANA | LT001 | Field IO
287 | [27 empty] | Measurement | BB1LT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
288 |  | BB1 | IV | 204 | BB1IV204 | Main steam line accumulator bypass on-off valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 217 | BB1GS217 | Main steam line accumulator bypass on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 218 | BB1GS218 | Main steam line accumulator bypass on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
290 |  | BB1 | PT | 208 | BB1PT208 | Accumulator pressure | [30 empty] | 0 | 40 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1SGBGCJA1+LAZ1 | G1/2 |  | 4006 | MEAS_ANA | PT001.1 | Field IO
291 | [27 empty] | Measurement | BB1PT208 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
292 |  | BB1 | FT | 203 | BB1FT203 | Steam to existing header flow measurement | [30 empty] | 0 | 25 | t/h |  |  | 1 | [21 empty] | 4006 | MEAS_ANA | FT001 | Field IO
293 | [27 empty] | Measurement | BB1FT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
292 |  | BB1 | QT |  |  | Steam to existing header energy calculator | [6 empty] | 240 | [28 empty] | 1 | [17 empty] | E+H | RMS621-21BBA1221 |  |  | 4006 | MEAS_ANA |  | Field IO |  | Instrument added | 3
293 | [27 empty] | Measurement | BB1FT203 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
294 |  | BB1 | LT | 003 | BB1LT003 | Steam accumulator level 1 | [35 empty] | 1 | [17 empty] | E+H | PMD55-AA22AB67FGJHAJA1A+PDP3Z1 | NPT1/4-18 IEC61518 |  | 4006 | MEAS_ANA | LT001 | Field IO
295 | [27 empty] | Measurement | BB1LT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
296 |  | BB1 | IV | 205 | BB1IV205 | Steam accumualtor ON-OFF isolating valve |  |  |  | 0.45 | 3.7 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA14.2-22 + RWG |  | Konwell/Auma | 4006 | MTR_VLV |  |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
211 |  | BB1 | GS | 219 | BB1GS219 | Steam accumualtor ON-OFF isolating valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
212 | [27 empty] | Binary state | BB1GS227 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
213 |  | BB1 | GS | 220 | BB1GS220 | Steam accumualtor ON-OFF isolating valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC |  | Signal added | 3
214 | [27 empty] | Binary state | BB1GS228 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
298 |  | BB1 | GS | 217 | BB1GS217 | Steam accumulator by-pass valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
299 | [27 empty] | Binary state | BB1GS217 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
300 |  | BB1 | GS | 218 | BB1GS218 | Steam accumulator by-pass valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
301 | [27 empty] | Binary state | BB1GS218 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
302 |  | BB1 | GS | 220 | BB1GS220 | Steam accumulator ON-OFF valve close limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
303 | [27 empty] | Binary state | BB1GS220 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
304 |  | BB1 | GS | 219 | BB1GS219 | Steam accumulator ON-OFF valve open limit switch | [33 empty] | 1 | [23 empty] | 4006 | MEAS_BIN | XS002/XS004 | MCC
305 | [27 empty] | Binary state | BB1GS219 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
306 |  | BB1 | QT | 002 | BB1QT002 | pH measurement from feed water tank | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
307 | [27 empty] | Measurement | BB1QT002 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
308 |  | BB1 | QT | 006 | BB1QT006 | Conductivity measurement from main steam | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
309 | [27 empty] | Measurement | BB1QT006 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
310 |  | BB1 | QT | 005 | BB1QT005 | Conductivity measurement from saturated steam | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
311 | [27 empty] | Measurement | BB1QT005 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
312 |  | BB1 | QT | 003 | BB1QT003 | Conductivity measurement from condensate | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
313 | [27 empty] | Measurement | BB1QT003 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
314 |  | BB1 | QT | 007 | BB1QT007 | Conductivity measurement from feed water line | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
315 | [27 empty] | Measurement | BB1QT007 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
316 |  | BB1 | QT | 001 | BB1QT001 | Conductivity measurement from feed water tank | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
317 | [27 empty] | Measurement | BB1QT001 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
318 |  | BB1 | QT | 004 | BB1QT004 | Conductivity measurement from boiler water | [35 empty] | 1 | [21 empty] | 4007 | MEAS_ANA |  | Field IO
319 | [27 empty] | Measurement | BB1QT004 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
320 |  | BB1 | PT | 400 | BB1PT400 | Primary air pressure |  | SIL2 classified transmitter | [28 empty] | 0 | 16 | kPa | [6 empty] | 1 | [13 empty] | E+H | PMC51-AA22IA1EGJGCJA+LAZ1 | G1/2 |  | 4008 | MEAS_ANA_SRS | PT002 | SRS
321 | [27 empty] | Measurement SRS | BB1PT400 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
322 |  | BB1 | TT | 418 | BB1TT418 | Bed temperature 4 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
323 | [27 empty] | Measurement SRS | BB1TT418 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
324 |  | BB1 | PT | 404 | BB1PT404 | Boiler upper part pressure 1 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
325 | [27 empty] | Measurement SRS | BB1PT404 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
326 |  | BB1 | FT | 400 | BB1FT400 | Primary air flow |  | 0...11,21 mbar = 0...4,0 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
327 | [27 empty] | Measurement SRS | BB1FT400 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
328 |  | BB1 | PT | 401 | BB1PT401 | Secondary air pressure |  | SIL2 classified transmitter | [28 empty] | 0 | 6 | kPa | [6 empty] | 1 | [13 empty] | E+H | PMC51-AA22IA1CGJGCJA+LAZ1 | G1/2 |  | 4008 | MEAS_ANA_SRS | PT002 | SRS
329 | [27 empty] | Measurement SRS | BB1PT401 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
330 |  | BB1 | PT | 410 | BB1PT410 | Secondary air pressure inner front wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
331 | [27 empty] | Measurement | BB1PT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
332 |  | BB1 | TT | 551 | BB1TT551 | Flue gas temperature 2 | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
333 | [27 empty] | Measurement | BB1TT551 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
334 |  | BB1 | TT | 400 | BB1TT400 | Primary air temperature before preheater | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFG3000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
335 | [27 empty] | Measurement | BB1TT400 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
336 |  | BB1 | PT | 403 | BB1PT403 | Secondary air pressure inner back wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO
337 | [27 empty] | Measurement | BB1PT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
338 |  | BB1 | FT | 401 | BB1FT401 | Secondary air flow |  | 0...11,55 mbar = 0...4,6 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
339 | [27 empty] | Measurement SRS | BB1FT401 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
340 |  | BB1 | TT | 417 | BB1TT417 | Bed temperature 3 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
341 | [27 empty] | Measurement SRS | BB1TT417 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
342 |  | BB1 | PT | 550 | BB1PT550 | Flue gas pressure at the outlet of the boiler | [30 empty] | -35 | 35 | mbar |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO
343 | [27 empty] | Measurement | BB1PT550 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
344 |  | BB1 | TT | 012 | BB1TT012 | Condensate temperature from primary air preheater | [30 empty] | 0 | 250 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4008 | MEAS_ANA | TT001 | Field IO |  | Max scale changed | 3
345 | [27 empty] | Measurement | BB1TT012 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
346 |  | BB1 | TT | 413 | BB1TT413 | Bed temperature 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
347 | [27 empty] | Measurement SRS | BB1TT413 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
348 |  | BB1 | TT | 550 | BB1TT550 | Flue gas temperature 1 | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
349 | [27 empty] | Measurement | BB1TT550 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
350 |  | BB1 | TT | 412 | BB1TT412 | Boiler temperature after empty draft 2 | [30 empty] | 0 | 500 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
351 | [27 empty] | Measurement | BB1TT412 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
352 |  | BB1 | TT | 414 | BB1TT414 | Bed temperature 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 1200 | °C | [6 empty] | 1 | [13 empty] | E+H | TEC420-YX12GEK |  |  | 4008 | MEAS_ANA_SRS | TT004 | SRS
353 | [27 empty] | Measurement SRS | BB1TT414 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
354 |  | BB1 | PT | 405 | BB1PT405 | Boiler upper part pressure 2 |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
355 | [27 empty] | Measurement SRS | BB1PT405 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
356 |  | BB1 | TT | 411 | BB1TT411 | Boiler temperature after empty draft 1 | [30 empty] | 0 | 500 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
357 | [27 empty] | Measurement | BB1TT411 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
358 |  | BB1 | QT | 550 | BB1QT550 | Fluegas oxygen measurement 1 |  | SIL2 classified transmitter | [28 empty] | 0 | 25 | % | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | QT001/dn65 flange with counterflange. 1 meter probe | SRS
359 | [27 empty] | Measurement SRS | BB1QT550 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
360 |  | BB1 | FT | 550 | BB1FT550 | Recirculation gas flow |  | 0...10,19 mbar = 0...1,2 Nm3/s, SIL2 classified transmitter | [28 empty] | 0 | 12 | mbar | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | FT003 | SRS
361 | [27 empty] | Measurement SRS | BB1FT550 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
362 |  | BB1 | QT | 551 | BB1QT551 | Fluegas oxygen measurement 2 |  | SIL2 classified transmitter | [28 empty] | 0 | 25 | % | [6 empty] | 1 | [17 empty] | 4008 | MEAS_ANA_SRS | QT001/dn65 flange with counterflange. 1 meter probe | SRS
363 | [27 empty] | Measurement SRS | BB1QT551 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
364 |  | BB1 | QT | 552 | BB1QT552 | Fluegas CO measurement | [30 empty] | 0 | 5000 | ppm |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | QT001/dn65 flange with counterflange. 1 meter probe | Field IO
365 | [27 empty] | Measurement | BB1QT552 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
366 |  | BB1 | TT | 405 | BB1TT405 | Primary air temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFG3000 | G1/2 M / 250 mm |  | 4008 | MEAS_ANA | TT003 | Field IO
367 | [27 empty] | Measurement | BB1TT405 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
368 |  | BB1 | PT | 406 | BB1PT406 | Boiler upper part pressure |  | SIL2 classified transmitter | [28 empty] | -35 | 35 | mbar | [6 empty] | 1 | [13 empty] | E+H | PMD55-AA22AB67DGJHAJA1A+LAPDP3Z1 | NPT1/4-18 IEC61518 |  | 4008 | MEAS_ANA_SRS | PT003 | SRS
369 | [27 empty] | Measurement SRS | BB1PT406 | [16 empty] | X | [18 empty] | MEAS_ANA_SRS |  | SRS
370 |  | BB1 | TT | 415 | BB1TT415 | Boiler bed temperature middle level | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEP |  |  | 4008 | MEAS_ANA | TT004 | Field IO
371 | [27 empty] | Measurement | BB1TT415 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
372 |  | BB1 | TT | 416 | BB1TT416 | Boiler bed temperature lower level | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TEC420-YX12GEP |  |  | 4008 | MEAS_ANA | TT004 | Field IO
373 | [27 empty] | Measurement | BB1TT416 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
374 |  | BB1 | TT | 410 | BB1TT410 | Boiler 1st draft temperature | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TAF11-13ADA3GCFP+TEC420-YD12GEP |  |  | 4008 | MEAS_ANA | TT003 | Field IO
375 | [27 empty] | Measurement | BB1TT410 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
376 |  | BB1 | TT | 116 | BB1TT116 | Steam temperature to air preheater | [30 empty] | 0 | 300 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4008 | MEAS_ANA | TT001 | Field IO
377 | [27 empty] | Measurement | BB1TT116 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
378 |  | BB1 | TT | 308 | BB1TT308 | Furnace temperature connection | [30 empty] | 0 | 1200 | °C |  |  | 1 | [17 empty] | E+H | TAF11-13ADA3GCFP+TEC420-YD12GEP |  |  | 4008 | MEAS_ANA | TT003 | Field IO
379 | [27 empty] | Measurement | BB1TT308 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
380 |  | BB1 | DM | 300 | BB1DM300 | Tertiary air damper 1 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
381 | [27 empty] | Setpoint position | BB1DM300 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
382 | [27 empty] | Position feedback | BB1DM300 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
383 |  | BB1 | DM | 400 | BB1DM400 | Primary air damper | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
384 | [27 empty] | Setpoint position | BB1DM400 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
385 | [27 empty] | Position feedback | BB1DM400 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
386 |  | BB1 | DM | 550 | BB1DM550 | Recirculation gas damper | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
387 | [27 empty] | Setpoint position | BB1DM550 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
388 | [27 empty] | Position feedback | BB1DM550 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
389 |  | BB1 | DM | 301 | BB1DM301 | Secondary air damper 4 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
390 | [27 empty] | Setpoint position | BB1DM301 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
391 | [27 empty] | Position feedback | BB1DM301 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
392 |  | BB1 | DM | 302 | BB1DM302 | Secondary air damper 3 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
393 | [27 empty] | Setpoint position | BB1DM302 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
394 | [27 empty] | Position feedback | BB1DM302 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
395 |  | BB1 | DM | 304 | BB1DM304 | Secondary air damper 1 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
396 | [27 empty] | Setpoint position | BB1DM304 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
397 | [27 empty] | Position feedback | BB1DM304 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
398 |  | BB1 | DM | 303 | BB1DM303 | Secondary air damper 2 | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
399 | [27 empty] | Setpoint position | BB1DM303 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
400 | [27 empty] | Position feedback | BB1DM303 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
401 |  | BB1 | QT | 553 | BB1QT553 | Boiler room gas detector | [35 empty] | 1 | [21 empty] | 4008 | MEAS_ANA | XS001 | Field IO
402 | [27 empty] | Measurement | BB1QT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
403 |  | BB1 | TT | 408 | BB1TT408 | Secondary air fan motor bearing temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
404 | [27 empty] | Measurement | BB1TT408 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
403 |  | BB1 | TT | 423 | BB1TT423 | Secondary air fan motor bearing temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
404 | [27 empty] | Measurement | BB1TT408 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
405 |  | BB1 | TT | 406 | BB1TT406 | Secondary air fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
406 | [27 empty] | Measurement | BB1TT406 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
407 |  | BB1 | TT | 404 | BB1TT404 | Primary air fan motor bearing temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
408 | [27 empty] | Measurement | BB1TT404 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
407 |  | BB1 | TT | 409 | BB1TT409 | Primary air fan motor bearing temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
408 | [27 empty] | Measurement | BB1TT404 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
409 |  | BB1 | TT | 402 | BB1TT402 | Primary air fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
410 | [27 empty] | Measurement | BB1TT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
411 |  | BB1 | TT | 403 | BB1TT403 | Primary air fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
412 | [27 empty] | Measurement | BB1TT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
411 |  | BB1 | TT | 421 | BB1TT421 | Primary air fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
412 | [27 empty] | Measurement | BB1TT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
413 |  | BB1 | TT | 407 | BB1TT407 | Secondary air fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO
414 | [27 empty] | Measurement | BB1TT407 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
413 |  | BB1 | TT | 422 | BB1TT422 | Secondary air fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4008 | MEAS_ANA | TT005 | Field IO |  | Signal added | 3
414 | [27 empty] | Measurement | BB1TT407 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
415 |  | BB1 | IV | 206 | BB1IV206 | Primary air preheater on-off valve |  |  |  | 0.12 | 1.1 |  | 415 | [26 empty] | 3 | 2 | 1 | [17 empty] | Auma | SA07.6-22 + RWG |  | Konwell/Auma | 4008 | MTR_VLV | AA003 |  |  | Changed to motor valve | 3
161 | [27 empty] | Open direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
162 | [27 empty] | Close direction command | BB1IV200 | [11 empty] | X | [16 empty] | NO | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
163 | [27 empty] | Torque limit open direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
164 | [27 empty] | Torque limit close direction | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
165 | [27 empty] | Actuator fault | BB1IV200 | [10 empty] | X | [17 empty] | NC | [6 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
166 | [27 empty] | Position | BB1IV200 | [12 empty] | X | [22 empty] | MTR_VLV |  |  |  | Changed to motor valve | 3
417 |  | BB1 | CV | 004 | BB1CV004 | Primary air preheater control valve | [35 empty] | 1 | 1 | [20 empty] | 4008 | CONT_VLV | AA002 | Field IO
418 | [27 empty] | Setpoint position | BB1CV004 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
419 | [27 empty] | Position feedback | BB1CV004 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
420 |  | BB1 | GS | 215 | BB1GS215 | Primary air preheater on-off valve open limit switch | [33 empty] | 1 | [23 empty] | 4008 | MEAS_BIN | XS002/XS004 | MCC
421 | [27 empty] | Binary state | BB1GS215 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
422 |  | BB1 | GS | 216 | BB1GS216 | Primary air preheater on-off valve close limit switch | [33 empty] | 1 | [23 empty] | 4008 | MEAS_BIN | XS002/XS004 | MCC
423 | [27 empty] | Binary state | BB1GS216 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | MCC
424 |  | BB1 | IL | 001 | BB1IL001 | Alarm horn and light CO alarm | [34 empty] | 1 | [22 empty] | 4008 | ALM_HORN |  | Field IO |  | Description changed | 2
425 | [27 empty] | Command | BB1IL001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
426 |  | BB1 | PT | 409 | BB1PT409 | Secondary air pressure outer front wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
427 | [27 empty] | Measurement | BB1PT400 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
428 |  | BB1 | PT | 411 | BB1PT411 | Secondary air pressure outer back wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
429 | [27 empty] | Measurement | BB1PT401 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
430 |  | BB1 | PT | 407 | BB1PT407 | Tertiary air pressure right wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
431 | [27 empty] | Measurement | BB1PT402 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
432 |  | BB1 | PT | 408 | BB1PT408 | Tertiary air pressure left wall | [30 empty] | 0 | 6 | kPa |  |  | 1 | [17 empty] | E+H | PMC51-AA22IA1CGJGCJA+Z1 | G1/2 |  | 4008 | MEAS_ANA | PT002 | Field IO |  | Tag changed | 3
433 | [27 empty] | Measurement | BB1PT403 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
434 |  | BB1 | EM | 400 | BB1EM400 | Primary air fan |  |  |  | 132 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4008 | FRQ_DIR |  |  |  | Size and voltage | 1
435 | [27 empty] | Running | BB1FF400 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
436 | [27 empty] | MCC Fault | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
437 | [27 empty] | Safety switch | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
438 | [27 empty] | VFD Alarm | BB1FF400 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
439 | [27 empty] | Run command | BB1FF400 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
440 | [27 empty] | Current | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
441 | [27 empty] | Speed reference | BB1FF400 | [21 empty] | X | [13 empty] | FRQ_DIR
442 | [27 empty] | Actual speed | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
443 | [27 empty] | Torque | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
444 | [27 empty] | RPM | BB1FF400 | [20 empty] | X | [14 empty] | FRQ_DIR
445 |  | BB1 | SI | 400 | BB1SI400 | Primary air fan safety interlock | [38 empty] | 1 | [18 empty] | 4008 | FAN_SRS_DO
446 | [27 empty] | Safety interlock | BB1SI400 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 410 | BB1SI410 | Primary air fan run status SRS | [37 empty] | 1 | [19 empty] | 4008 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 400 | BB1ST400 | Primary air fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
447 |  | BB1 | EM | 401 | BB1EM401 | Secondary air fan |  |  |  | 45 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4008 | FRQ_DIR |  |  |  | Size, name and voltage | 1
448 | [27 empty] | Running | BB1FF401 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
449 | [27 empty] | MCC Fault | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
450 | [27 empty] | Safety switch | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
451 | [27 empty] | VFD Alarm | BB1FF401 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
452 | [27 empty] | Run command | BB1FF401 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
453 | [27 empty] | Current | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
454 | [27 empty] | Speed reference | BB1FF401 | [21 empty] | X | [13 empty] | FRQ_DIR
455 | [27 empty] | Actual speed | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
456 | [27 empty] | Torque | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
457 | [27 empty] | RPM | BB1FF401 | [20 empty] | X | [14 empty] | FRQ_DIR
458 |  | BB1 | SI | 401 | BB1SI401 | Secondary air fan safety interlock | [38 empty] | 1 | [18 empty] | 4008 | FAN_SRS_DO
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 411 | BB1SI411 | Secondary air fan run status SRS | [37 empty] | 1 | [19 empty] | 4008 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 401 | BB1ST401 | Secondary air fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
107 |  | BB1 | HS | 601 | BB1HS601 | Fuel system emergency shutdown switch 1 |  | Near door that leads hydraulic units | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
108 | [27 empty] | Binary state SRS | BB1HS101 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 602 | BB1HS602 | Fuel system emergency shutdown switch 2 |  | Outside near lift doors fuel receiving station | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 603 | BB1HS603 | Fuel system emergency shutdown switch 3 |  | Screening station | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
109 |  | BB1 | HS | 604 | BB1HS604 | Fuel system emergency shutdown switch 4 |  | Outside, on Fuel silo level near door | [35 empty] | 1 | [19 empty] | 4009 | MEAS_BIN_SRS | CH003 | SRS |  | Signal added | 2
110 | [27 empty] | Binary state SRS | BB1HS103 | [14 empty] | X | [20 empty] | MEAS_BIN_SRS |  | SRS |  | Signal added | 2
460 |  | BB1 | GS | 621 | BB1GS621 | Unloading station 3, block 3, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
461 | [27 empty] | Binary state | BB1GS621 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
462 |  | BB1 | GS | 611 | BB1GS611 | Unloading station 2, block 2, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
463 | [27 empty] | Binary state | BB1GS611 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
464 |  | BB1 | GS | 606 | BB1GS606 | Unloading station 1, block 1, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
465 | [27 empty] | Binary state | BB1GS606 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
466 |  | BB1 | GS | 614 | BB1GS614 | Unloading station 2, block 2, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
467 | [27 empty] | Binary state | BB1GS614 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
468 |  | BB1 | GS | 619 | BB1GS619 | Unloading station 3, block 3, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
469 | [27 empty] | Binary state | BB1GS619 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
470 |  | BB1 | GS | 651 | BB1GS651 | Disc screen by-pass damper limit switch to screen | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack | Instrument type added | 1
471 | [27 empty] | Binary state | BB1GS651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
472 |  | BB1 | PS | 602 | BB1PS602 | Hydraulics unit 1, block 3, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
473 | [27 empty] | Binary state | BB1PT602 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
474 |  | BB1 | GS | 615 | BB1GS615 | Unloading station 2, block 2, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
475 | [27 empty] | Binary state | BB1GS615 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
476 |  | BB1 | GS | 623 | BB1GS623 | Unloading station 3, block 3, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
477 | [27 empty] | Binary state | BB1GS623 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
478 |  | BB1 | ST | 651 | BB1ST651 | Scraper conveyor 2, rotation guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
479 | [27 empty] | Binary state | BB1ST651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
480 |  | BB1 | GS | 603 | BB1GS603 | Unloading station 1, block 1, feeder 2, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
481 | [27 empty] | Binary state | BB1GS603 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
482 |  | BB1 | PS | 601 | BB1PS601 | Hydraulics unit 1, block 2, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
483 | [27 empty] | Binary state | BB1PT601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
484 |  | BB1 | GS | 650 | BB1GS650 | Disc screen by-pass damper limit switch by-pass pos. | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack | Instrument type added | 1
485 | [27 empty] | Binary state | BB1GS650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
486 |  | BB1 | GS | 622 | BB1GS622 | Unloading station 3, block 3, feeder 4, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
487 | [27 empty] | Binary state | BB1GS622 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
488 |  | BB1 | GS | 602 | BB1GS602 | Unloading station 1, block 1, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
489 | [27 empty] | Binary state | BB1GS602 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
490 |  | BB1 | LS | 655 | BB1LS655 | Scraper conveyor 2, turning point blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
491 | [27 empty] | Binary state | BB1LS655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
492 |  | BB1 | GS | 607 | BB1GS607 | Unloading station 1, block 1, feeder 4, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
493 | [27 empty] | Binary state | BB1GS607 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
494 |  | BB1 | GS | 605 | BB1GS605 | Unloading station 1, block 1, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
495 | [27 empty] | Binary state | BB1GS605 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
496 |  | BB1 | LS | 652 | BB1LS652 | Unloading station 2, block 2, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
497 | [27 empty] | Binary state | BB1LS652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
498 |  | BB1 | GS | 601 | BB1GS601 | Unloading station 1, block 1, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
499 | [27 empty] | Binary state | BB1GS601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
500 |  | BB1 | LS | 608 | BB1LS608 | Hydraulics unit 1, low oil level alarm | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | LS001 | Field IO | Fuel station IO-rack
501 | [27 empty] | Binary state | BB1LS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
502 |  | BB1 | LS | 656 | BB1LS656 | Scraper conveyor 2, fuel silo side blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO
503 | [27 empty] | Binary state | BB1LS656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
504 |  | BB1 | LS | 600 | BB1LS600 | Hydraulics unit 1, leaking pool limit switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | LS001 | Field IO | Fuel station IO-rack
505 | [27 empty] | Binary state | BB1LS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
506 |  | BB1 | GS | 609 | BB1GS609 | Unloading station 2, block 2, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
507 | [27 empty] | Binary state | BB1GS609 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
508 |  | BB1 | LS | 650 | BB1LS650 | Scraper conveyor 1 bed height level switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
509 | [27 empty] | Binary state | BB1LS650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
510 |  | BB1 | GS | 617 | BB1GS617 | Unloading station 3, block 3, feeder 1, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
511 | [27 empty] | Binary state | BB1GS617 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
512 |  | BB1 | LS | 651 | BB1LS651 | Unloading station 3, block 3, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
513 | [27 empty] | Binary state | BB1LS651 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
514 |  | BB1 | GS | 612 | BB1GS612 | Unloading station 2, block 2, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
515 | [27 empty] | Binary state | BB1GS612 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
516 |  | BB1 | LS | 654 | BB1LS654 | Scraper conveyor 1, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
517 | [27 empty] | Binary state | BB1LS654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
518 |  | BB1 | GS | 613 | BB1GS613 | Unloading station 2, block 2, feeder 3, out | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
519 | [27 empty] | Binary state | BB1GS613 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
520 |  | BB1 | GS | 620 | BB1GS620 | Unloading station 3, block 3, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
521 | [27 empty] | Binary state | BB1GS620 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
522 |  | BB1 | GS | 618 | BB1GS618 | Unloading station 3, block 3, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
523 | [27 empty] | Binary state | BB1GS618 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
524 |  | BB1 | PS | 600 | BB1PS600 | Hydraulics unit 1, block 1, pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
525 | [27 empty] | Binary state | BB1PT600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
526 |  | BB1 | GS | 608 | BB1GS608 | Unloading station 2, block 2, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
527 | [27 empty] | Binary state | BB1GS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
528 |  | BB1 | GS | 604 | BB1GS604 | Unloading station 1, block 1, feeder 3, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
529 | [27 empty] | Binary state | BB1GS604 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
530 |  | BB1 | LS | 653 | BB1LS653 | Unloading station 1, block 1, blockage guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002/XS004 | Field IO | Fuel station IO-rack
531 | [27 empty] | Binary state | BB1LS653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
532 |  | BB1 | GS | 616 | BB1GS616 | Unloading station 3, block 3, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
533 | [27 empty] | Binary state | BB1GS616 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
534 |  | BB1 | GS | 600 | BB1GS600 | Unloading station 1, block 1, feeder 1, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
535 | [27 empty] | Binary state | BB1GS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
536 |  | BB1 | ST | 650 | BB1ST650 | Scraper conveyor 1, rotation guard | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
537 | [27 empty] | Binary state | BB1ST650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
538 |  | BB1 | TT | 650 | BB1TT650 | Scraper conveyor 1, temperature measurement | [30 empty] | 0 | 150 | °C |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | TT006 | Field IO | Fuel station IO-rack
539 | [27 empty] | Measurement | BB1TT650 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
540 |  | BB1 | GS | 610 | BB1GS610 | Unloading station 2, block 2, feeder 2, in | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
541 | [27 empty] | Binary state | BB1GS610 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
542 |  | BB1 | LT | 611 | BB1LT611 | Unloading station 1 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
543 | [27 empty] | Measurement | BB1LT509 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
544 |  | BB1 | LT | 612 | BB1LT612 | Unloading station 3 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
545 | [27 empty] | Measurement | BB1LT513 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
546 |  | BB1 | LT | 613 | BB1LT613 | Unloading station 2 level | [30 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4009 | MEAS_ANA | LT003 | Field IO | Fuel station IO-rack | Tag changed | 1
547 | [27 empty] | Measurement | BB1LT512 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO | Fuel station IO-rack
548 |  | BB1 | SV | 601 | BB1SV601 | Control Valve push feeders unloading station 1 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
549 | [27 empty] | Control out | BB1SV601 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
550 | [27 empty] | Control in | BB1SV601 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
551 |  | BB1 | ST | 675 | BB1ST675 | Leveling roller 3 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
552 | [27 empty] | Binary state | BB1ST703 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
553 |  | BB1 | SV | 603 | BB1SV603 | Control Valve push feeders unloading station 3 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
554 | [27 empty] | Control out | BB1SV603 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
555 | [27 empty] | Control in | BB1SV603 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
556 |  | BB1 | SV | 602 | BB1SV602 | Control Valve push feeders unloading station 2 | [34 empty] | 2 | [22 empty] | 4009 | PUSH_FEED |  | Field IO | Fuel station IO-rack
557 | [27 empty] | Control out | BB1SV602 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
558 | [27 empty] | Control in | BB1SV602 | [11 empty] | X | [23 empty] | PUSH_FEED |  | Field IO | Fuel station IO-rack
559 |  | BB1 | TS | 608 | BB1TS608 | High temperature switch hydraulic oil | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack
560 | [27 empty] | Binary state | BB1TS608 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
561 |  | BB1 | ST | 673 | BB1ST673 | Leveling roller 1 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
562 | [27 empty] | Binary state | BB1ST701 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
563 |  | BB1 | TS | 600 | BB1TS600 | Hydraulics unit, thermostat for heater | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack
564 | [27 empty] | Binary state | BB1TS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
565 |  | BB1 | ST | 674 | BB1ST674 | Leveling roller 2 speed switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack
566 | [27 empty] | Binary state | BB1ST702 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
567 |  | BB1 | PS | 605 | BB1PS605 | Hydraulic oil return block 3 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
568 | [27 empty] | Binary state | BB1PS603 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
569 |  | BB1 | PS | 603 | BB1PS603 | Hydraulic oil return block 1 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
570 | [27 empty] | Binary state | BB1PS600 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
571 |  | BB1 | PS | 604 | BB1PS604 | Hydraulic oil return block 2 filter pressure switch | [33 empty] | 1 | [23 empty] | 4009 | MEAS_BIN | XS003 | Field IO | Fuel station IO-rack | Tag changed | 3
572 | [27 empty] | Binary state | BB1PS601 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
573 |  | BB1 | EM | 603 | BB1EM603 | Fuel reception hydraulic unit 1, pump 1 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
574 | [27 empty] | Running | BB1PU603 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH |  |  |  | Motor details | 1
575 | [27 empty] | MCC Fault | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH |  |  |  | Motor details | 1
576 | [27 empty] | Safety switch | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
577 | [27 empty] | VFD Alarm | BB1PU603 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
578 | [27 empty] | Run command | BB1PU603 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
579 | [27 empty] | Current | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
580 | [27 empty] | Speed reference | BB1PU603 | [21 empty] | X | [13 empty] | FRQ_DIRH
581 | [27 empty] | Actual speed | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
582 | [27 empty] | Torque | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
583 | [27 empty] | RPM | BB1PU603 | [20 empty] | X | [14 empty] | FRQ_DIRH
584 | [27 empty] | Local run command | BB1PU603 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
585 | [27 empty] | Local mode switch | BB1PU603 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 603 | BB1SI603 | Fuel reception hydraulic unit 1, pump 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
586 |  | BB1 | EM | 604 | BB1EM604 | Fuel reception hydraulic unit 1, pump 2 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
587 | [27 empty] | Running | BB1PU604 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH
588 | [27 empty] | MCC Fault | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
589 | [27 empty] | Safety switch | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
590 | [27 empty] | VFD Alarm | BB1PU604 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
591 | [27 empty] | Run command | BB1PU604 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
592 | [27 empty] | Current | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
593 | [27 empty] | Speed reference | BB1PU604 | [21 empty] | X | [13 empty] | FRQ_DIRH
594 | [27 empty] | Actual speed | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
595 | [27 empty] | Torque | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
596 | [27 empty] | RPM | BB1PU604 | [20 empty] | X | [14 empty] | FRQ_DIRH
597 | [27 empty] | Local run command | BB1PU604 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
598 | [27 empty] | Local mode switch | BB1PU604 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 604 | BB1SI604 | Fuel reception hydraulic unit 1, pump 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
599 |  | BB1 | EM | 605 | BB1EM605 | Fuel reception hydraulic unit 1, pump 3 |  | preliminary size |  | 37 |  |  | 415 | [26 empty] | 2 | [7 empty] | 4 | 1 | 4 | 1 | [12 empty] | 4009 | FRQ_DIRH |  |  |  | Motor details | 1
600 | [27 empty] | Running | BB1PU605 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIRH
601 | [27 empty] | MCC Fault | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
602 | [27 empty] | Safety switch | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
603 | [27 empty] | VFD Alarm | BB1PU605 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIRH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_DIRH |  |  |  | Thermistor fault added | 2
604 | [27 empty] | Run command | BB1PU605 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIRH
605 | [27 empty] | Current | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
606 | [27 empty] | Speed reference | BB1PU605 | [21 empty] | X | [13 empty] | FRQ_DIRH
607 | [27 empty] | Actual speed | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
608 | [27 empty] | Torque | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
609 | [27 empty] | RPM | BB1PU605 | [20 empty] | X | [14 empty] | FRQ_DIRH
610 | [27 empty] | Local run command | BB1PU605 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
611 | [27 empty] | Local mode switch | BB1PU605 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_DIRH
458 |  | BB1 | SI | 605 | BB1SI605 | Fuel reception hydraulic unit 1, pump 3 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
612 |  | BB1 | EM | 673 | BB1EM673 | Levelling roller 1 |  |  |  | 2,2 |  |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size changed | 3
613 | [27 empty] | Running FWD | BB1EM703 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
614 | [27 empty] | Running BWD | BB1EM703 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
615 | [27 empty] | MCC Fault | BB1EM703 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
616 | [27 empty] | Local FWD command | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
617 | [27 empty] | Local BWD command | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
618 | [27 empty] | Local mode switch | BB1EM703 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
619 | [27 empty] | Run command FWD | BB1EM703 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
620 | [27 empty] | Run command BWD | BB1EM703 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
621 | [27 empty] | Current | BB1EM703 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
622 |  | BB1 | EM | 674 | BB1EM674 | Levelling roller 2 |  |  |  | 3 |  |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size changed | 3
623 | [27 empty] | Running FWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
624 | [27 empty] | Running BWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
625 | [27 empty] | MCC Fault | BB1EM704 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
626 | [27 empty] | Local FWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
627 | [27 empty] | Local BWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
628 | [27 empty] | Local mode switch | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
629 | [27 empty] | Run command FWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
630 | [27 empty] | Run command BWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
631 | [27 empty] | Current | BB1EM704 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
632 |  | BB1 | EM | 675 | BB1EM675 | Levelling roller 3 | [57 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor deleted | 2
633 | [27 empty] | Running FWD | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
634 | [27 empty] | Running BWD | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
635 | [27 empty] | MCC Fault | BB1EM703 | [28 empty] | NC | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
636 | [27 empty] | Local FWD command | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
637 | [27 empty] | Local BWD command | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
638 | [27 empty] | Local mode switch | BB1EM703 | [28 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
639 | [27 empty] | Run command FWD | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
640 | [27 empty] | Run command BWD | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
641 | [27 empty] | Current | BB1EM703 | [35 empty] | DOL_REVH_BUS |  |  |  | Motor deleted | 2
642 |  | BB1 | EM | 658 | BB1EM658 | Scraper Conveyor 1 |  |  |  | 15 |  |  | 415 | [26 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Tag changed and motor details | 1
643 | [27 empty] | Running FWD | BB1CO653 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
644 | [27 empty] | Running BWD | BB1CO653 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
645 | [27 empty] | MCC Fault | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
646 | [27 empty] | Safety switch | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
647 | [27 empty] | VFD Alarm | BB1CO653 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
648 | [27 empty] | Local FWD command | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
649 | [27 empty] | Local BWD command | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
650 | [27 empty] | Local mode switch | BB1CO653 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
651 | [27 empty] | Run command FWD | BB1CO653 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
652 | [27 empty] | Run command BWD | BB1CO653 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
653 | [27 empty] | Current | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
654 | [27 empty] | Speed reference | BB1CO653 | [21 empty] | X | [13 empty] | FRQ_REVH
655 | [27 empty] | Actual speed | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
656 | [27 empty] | Torque | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
657 | [27 empty] | RPM | BB1CO653 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 658 | BB1SI658 | Scraper Conveyor 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
658 |  | BB1 | EM | 670 | BB1EM670 | Belt magnet |  |  |  | 2.2 | 4.2 | 1500 | 415 | [26 empty] | 2 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIRH_BUS |  |  |  | Motor details and type | 1
659 | [27 empty] | Running FWD | BB1CO654 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
660 | [27 empty] | Running BWD | BB1CO654 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
661 | [27 empty] | MCC Fault | BB1CO654 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
662 | [27 empty] | Local FWD command | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
663 | [27 empty] | Local BWD command | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
664 | [27 empty] | Local mode switch | BB1CO654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
665 | [27 empty] | Run command FWD | BB1CO654 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
666 | [27 empty] | Run command BWD | BB1CO654 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
667 | [27 empty] | Current | BB1CO654 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
685 |  | BB1 | ST | 654 | BB1ST654 | Belt magnet rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 661 | BB1GS661 | Belt magnet deviation detector 1 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCRT115EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 662 | BB1GS662 | Belt magnet deviation detector 2 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCRT115EX |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
668 |  | BB1 | EM | 659 | BB1EM659 | Belt Conveyor |  |  |  | 4 | 7.6 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Motor details and type | 1
669 | [27 empty] | Running FWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
670 | [27 empty] | Running BWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
671 | [27 empty] | MCC Fault | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
672 | [27 empty] | Safety switch | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
673 | [27 empty] | VFD Alarm | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
674 | [27 empty] | Local FWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
675 | [27 empty] | Local BWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
676 | [27 empty] | Local mode switch | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
677 | [27 empty] | Run command FWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
678 | [27 empty] | Run command BWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
679 | [27 empty] | Current | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
680 | [27 empty] | Speed reference | BB1CO655 | [21 empty] | X | [13 empty] | FRQ_REVH
681 | [27 empty] | Actual speed | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
682 | [27 empty] | Torque | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
683 | [27 empty] | RPM | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
684 | [7 empty] | Brake |  |  |  |  | 240 | [55 empty] | Feed added | 1
458 |  | BB1 | SI | 659 | BB1SI659 | Belt Conveyor safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
685 |  | BB1 | ST | 652 | BB1ST652 | Belt conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 659 | BB1GS659 | Belt conveyor deviation detector 1 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Steute | Ex ES 98 SR-11-3GD |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 660 | BB1GS660 | Belt conveyor deviation detector 2 | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Steute | Ex ES 98 SR-11-3GD |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
685 |  | BB1 | GS | 663 | BB1GS663 | Belt conveyor oversize detector | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS530B1MAL2 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument added | 1
686 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
687 |  | BB1 | EM | 675 | BB1EM75 | Disc screen drive 1 |  |  |  | 7.5 | 13.7 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Tag changed | 3
688 | [27 empty] | Running FWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
689 | [27 empty] | Running BWD | BB1CO655 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
690 | [27 empty] | MCC Fault | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
691 | [27 empty] | Safety switch | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
692 | [27 empty] | VFD Alarm | BB1CO655 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
693 | [27 empty] | Local FWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
694 | [27 empty] | Local BWD command | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
695 | [27 empty] | Local mode switch | BB1CO655 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
696 | [27 empty] | Run command FWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
697 | [27 empty] | Run command BWD | BB1CO655 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
698 | [27 empty] | Current | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
699 | [27 empty] | Speed reference | BB1CO655 | [21 empty] | X | [13 empty] | FRQ_REVH
700 | [27 empty] | Actual speed | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
701 | [27 empty] | Torque | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
702 | [27 empty] | RPM | BB1CO655 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 675 | BB1SI675 | Disc screen drive 1 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
703 |  | BB1 | EM | 676 | BB1EM676 | Disc screen drive 2 |  |  |  | 7.5 | 13.7 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH | XS002 |  |  | Tag changed | 3
704 | [27 empty] | Running FWD | BB1CO656 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
705 | [27 empty] | Running BWD | BB1CO656 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
706 | [27 empty] | MCC Fault | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
707 | [27 empty] | Safety switch | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
708 | [27 empty] | VFD Alarm | BB1CO656 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
709 | [27 empty] | Local FWD command | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
710 | [27 empty] | Local BWD command | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
711 | [27 empty] | Local mode switch | BB1CO656 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
712 | [27 empty] | Run command FWD | BB1CO656 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
713 | [27 empty] | Run command BWD | BB1CO656 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
714 | [27 empty] | Current | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
715 | [27 empty] | Speed reference | BB1CO656 | [21 empty] | X | [13 empty] | FRQ_REVH
716 | [27 empty] | Actual speed | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
717 | [27 empty] | Torque | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
718 | [27 empty] | RPM | BB1CO656 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 676 | BB1SI676 | Disc screen drive 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
719 |  | BB1 | ST | 656 | BB1ST656 | Disc screen drive 1 rotation guard | [33 empty] | 1 | [19 empty] | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument type added | 1
720 | [27 empty] | Binary state | BB1ST656 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
721 |  | BB1 | ST | 657 | BB1ST657 | Disc screen drive 2 rotation guard | [33 empty] | 1 | [19 empty] | Telemechanique | XSAV-11801 |  |  | 4009 | MEAS_BIN | XS002 | Field IO | Fuel station IO-rack | Instrument type added | 1
722 | [27 empty] | Binary state | BB1ST657 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO | Fuel station IO-rack
723 |  | BB1 | EM | 672 | BB1EM672 | Scraper Conveyor 2 |  |  |  | 18,5 |  |  | 415 | [26 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4009 | FRQ_REVH |  |  |  | Motor size changed | 3
724 | [27 empty] | Running FWD | BB1CO657 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
725 | [27 empty] | Running BWD | BB1CO657 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
726 | [27 empty] | MCC Fault | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
727 | [27 empty] | Safety switch | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
728 | [27 empty] | VFD Alarm | BB1CO657 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
729 | [27 empty] | Local FWD command | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
730 | [27 empty] | Local BWD command | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
731 | [27 empty] | Local mode switch | BB1CO657 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
732 | [27 empty] | Run command FWD | BB1CO657 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
733 | [27 empty] | Run command BWD | BB1CO657 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
734 | [27 empty] | Current | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
735 | [27 empty] | Speed reference | BB1CO657 | [21 empty] | X | [13 empty] | FRQ_REVH
736 | [27 empty] | Actual speed | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
737 | [27 empty] | Torque | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
738 | [27 empty] | RPM | BB1CO657 | [20 empty] | X | [14 empty] | FRQ_REVH
458 |  | BB1 | SI | 672 | BB1SI672 | Scraper Conveyor 2 safety interlock | [38 empty] | 1 | [18 empty] | 4009 | FAN_SRS_DO |  |  |  | Signal added | 3
459 | [27 empty] | Safety interlock | BB1SI401 | [15 empty] | X | [19 empty] | FAN_SRS_DO
739 |  | BB1 | IJ | 002 | BB1IJ002 | Scraper Conveyor 1 Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4009 | ALM_HORN |  | Field IO | Fuel station IO-rack
740 | [27 empty] | Command | BB1IJ002 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO | Fuel station IO-rack
741 |  | BB1 | IJ | 001 | BB1IJ001 | Scraper Conveyor 2 Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4009 | ALM_HORN |  | Field IO
742 | [27 empty] | Command | BB1IJ001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
743 |  | BB1 | EM | 601 | BB1EM601 | Dust extraction rotary feeder |  | preliminary size |  | 0,75 | [29 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4009 | DOL_REVH_BUS |  |  |  | Motor size added | 3
744 | [27 empty] | Running FWD | BB1RV601 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
745 | [27 empty] | Running BWD | BB1RV601 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
746 | [27 empty] | MCC Fault | BB1RV601 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
747 | [27 empty] | Local FWD command | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
748 | [27 empty] | Local BWD command | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
749 | [27 empty] | Local mode switch | BB1RV601 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
750 | [27 empty] | Run command FWD | BB1RV601 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
751 | [27 empty] | Run command BWD | BB1RV601 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
752 | [27 empty] | Current | BB1RV601 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
753 |  | BB1 | EM | 606 | BB1EM606 | Dust extraction fan |  | preliminary size |  | 30 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIR_BUS |  |  |  | Tag and motor size changed | 3
754 | [27 empty] | Running | BB1FF603 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
755 | [27 empty] | MCC Fault | BB1FF603 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
756 | [27 empty] | Run command | BB1FF603 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
757 | [27 empty] | Current | BB1FF603 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
758 |  | BB1 | EH | 600 | BB1EH600 | Electric heater hydraulic unit |  | preliminary size |  | 1,5 | [37 empty] | 2 | 1 | 1 | [13 empty] | 4009 | DOL_DIR_BUS
759 | [27 empty] | Running | BB1EH600 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
760 | [27 empty] | MCC Fault | BB1EH600 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
761 | [27 empty] | Run command | BB1EH600 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
762 | [27 empty] | Current | BB1EH600 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
763 |  | BB1 | CV | 402 | BB1CV402 | Fuel chute B carrying air control valve 2 | [35 empty] | 1 | 1 | [20 empty] | 4010 | CONT_VLV | AA002 | Field IO
764 | [27 empty] | Setpoint position | BB1CV402 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
765 | [27 empty] | Position feedback | BB1CV402 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
766 |  | BB1 | CV | 403 | BB1CV403 | Fuel chute A carrying air control valve 1 | [35 empty] | 1 | 1 | [20 empty] | 4010 | CONT_VLV | AA002 | Field IO
767 | [27 empty] | Setpoint position | BB1CV403 | [13 empty] | X | [21 empty] | CONT_VLV |  | Field IO
768 | [27 empty] | Position feedback | BB1CV403 | [12 empty] | X | [22 empty] | CONT_VLV |  | Field IO
769 |  | BB1 | GS | 652 | BB1GS652 | Explosion hatch limit switch 1 | [33 empty] | 1 | [19 empty] | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
770 | [27 empty] | Binary state | BB1GS652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
771 |  | BB1 | GS | 653 | BB1GS653 | Explosion hatch limit switch 2 | [33 empty] | 1 | [19 empty] | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
772 | [27 empty] | Binary state | BB1GS653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
773 |  | BB1 | GS | 654 | BB1GS654 | Explosion hatch limit switch 3 | [33 empty] | 0 | [22 empty] | LAITEX | 4010 | MEAS_BIN | XS002 |  |  | Instrument removed | 1
774 | [27 empty] | Binary state | BB1GS654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
775 |  | BB1 | GS | 655 | BB1GS655 | Explosion hatch limit switch 4 | [33 empty] | 0 | [22 empty] | LAITEX | 4010 | MEAS_BIN | XS002 |  |  | Instrument removed | 1
776 | [27 empty] | Binary state | BB1GS655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
777 |  | BB1 | LS | 657 | BB1LS657 | Fuel silo discharge screw blockage switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument type added | 1
778 | [27 empty] | Binary state | BB1LS657 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
779 |  | BB1 | LS | 658 | BB1LS658 | Fuel silo cross conveyor blockage switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Description changed | 2
780 | [27 empty] | Binary state | BB1LS658 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
779 |  | BB1 | LS |  | BB1LS | Fuel silo cross conveyor explosion hatch limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XCKD3906P16EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | Instrument added | 2
780 | [27 empty] | Binary state | BB1LS658 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
781 |  | BB1 | LS | 659 | BB1LS659 | Fuel feeding screw 1 blockage switch | [33 empty] | 1 | [16 empty] | 3-wire |  |  | Telemechanique | XS630B1PAL10EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | 3-wire | 2
782 | [27 empty] | Binary state | BB1LS659 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
783 |  | BB1 | LS | 660 | BB1LS660 | Fuel feeding screw 2 blockage switch | [33 empty] | 1 | [16 empty] | 3-wire |  |  | Telemechanique | XS630B1PAL10EX |  | LAITEX | 4010 | MEAS_BIN | XS002/XS004 | Field IO |  | 3-wire | 2
784 | [27 empty] | Binary state | BB1LS660 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
785 |  | BB1 | LT | 650 | BB1LT650 | Fuel silo level radar 1 | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT10-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 | Field IO |  | Instrument type added | 1
786 | [27 empty] | Measurement | BB1LT650 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA |  | Field IO
785 |  | BB1 | LT | 651 | BB1LT651 | Fuel silo level radar 2 | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT10-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 |  |  | Instrument deleted | 2
786 | [27 empty] | Measurement | BB1LT650 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA
787 |  | BB1 | LT | 652 | BB1LT652 | Fuel pocket level | [6 empty] | 240 | [23 empty] | 0 | 100 | % |  |  | 1 | [13 empty] | Sensor |  |  |  | Hawk | AWRT20-S4-XXA20-C6-XX |  | LAITEX | 4010 | MEAS_ANA | LT003 | Field IO |  | Instrument type added | 1
788 | [27 empty] | Measurement | BB1LT652 | [12 empty] | X | [13 empty] | Transmitter |  |  | 240 | Hawk | AWR234-SU-XXA22X |  |  |  | MEAS_ANA |  | Field IO
789 |  | BB1 | ST | 649 | BB1ST649 | Fuel silo cross conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Description modified | 3
790 | [27 empty] | Binary state | BB1ST649 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
791 |  | BB1 | ST | 652 | BB1ST652 | Rotating fuel spreader rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
792 | [27 empty] | Binary state | BB1ST652 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
793 |  | BB1 | ST | 653 | BB1ST653 | Fuel feeding screw 2 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | 2-wire | 2
794 | [27 empty] | Binary state | BB1ST653 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
795 |  | BB1 | ST | 654 | BB1ST654 | Fuel feeding rotary feeder 1 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
796 | [27 empty] | Binary state | BB1ST654 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
797 |  | BB1 | ST | 655 | BB1ST655 | Fuel feeding rotary feeder 2 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XSAV-11801 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
798 | [27 empty] | Binary state | BB1ST655 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
799 |  | BB1 | ST | 659 | BB1ST659 | Fuel feeding screw 1 rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemechanique | XS518B1MAL2 |  | LAITEX | 4010 | MEAS_BIN | XS002 | Field IO |  | 2-wire | 2
800 | [27 empty] | Binary state | BB1ST659 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
801 |  | BB1 | SV | 400 | BB1SV400 | Sealing air to rotary feeder solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
802 | [27 empty] | Control command | BB1SV400 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
803 |  | BB1 | SV | 406 | BB1SV406 | Sealing air to rotary feeder solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
804 | [27 empty] | Control command | BB1SV406 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
805 |  | BB1 | SV | 950 | BB1SV950 | Fuel silo fire water control valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
806 | [27 empty] | Control command | BB1SV950 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
807 |  | BB1 | SV | 951 | BB1SV951 | Fuel pocket fire water control valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4010 | BIN_VLV | AA005 | Field IO
808 | [27 empty] | Control command | BB1SV951 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
809 |  | BB1 | TT | 652 | BB1TT652 | Fuel silo temperature measurement | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TST41N-MRDD82HA4P |  |  | 4010 | MEAS_ANA | TT006 | Field IO
810 | [27 empty] | Measurement | BB1TT652 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
811 |  | BB1 | TT | 653 | BB1TT653 | Fuel pocket temperature | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TST41N-MRDD82HA4P |  |  | 4010 | MEAS_ANA | TT006 | Field IO
812 | [27 empty] | Measurement | BB1TT653 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
813 |  | BB1 | IV | 650 | BB1IV650 | Slide gate valve |  |  |  | 2.2 | 4.2 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor added | 1
814 | [27 empty] | Running FWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
815 | [27 empty] | Running BWD | BB1EM704 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
816 | [27 empty] | MCC Fault | BB1EM704 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
817 | [27 empty] | Local FWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
818 | [27 empty] | Local BWD command | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
819 | [27 empty] | Local mode switch | BB1EM704 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
820 | [27 empty] | Run command FWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
821 | [27 empty] | Run command BWD | BB1EM704 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
822 | [27 empty] | Current | BB1EM704 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
823 |  | BB1 | GS | 655 | BB1GS655 | Slide gate valve open limit switch | [33 empty] | 1 | [19 empty] | Telemecanique | XSAV-11801 |  |  | 4010 | MEAS_BIN |  | Field IO |  | Instrument added | 1
824 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
825 |  | BB1 | GS | 656 | BB1GS656 | Slide gate valve close limit switch | [33 empty] | 1 | [19 empty] | Telemecanique | XSAV-11801 |  |  | 4010 | MEAS_BIN |  | Field IO |  | Instrument added | 1
826 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
827 |  | BB1 | HC | 601 | BB1HC601 | Crane feed |  | 16 A breaker |  |  |  |  | 415 | [55 empty] | Crane added | 1
828 |  | BB1 | FL | 650 | BB1FL650 | Fuel silo dust filter control box feed |  | 10 A breaker |  |  |  |  | 240 | [27 empty] | 1 | [22 empty] | 4010 | MCCB_1ph |  |  |  | Voltage level added | 1
831 | [27 empty] | Cleaning on | BB1FF650 | [11 empty] | X | [16 empty] | Pot.free | [10 empty] | Signal added | 1
829 |  | BB1 | EM | 651 | BB1EM651 | Fuel silo dust filter fan | [41 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIR_BUS
830 | [27 empty] | Running | BB1FF650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
831 | [27 empty] | MCC Fault | BB1FF650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
832 | [27 empty] | Run command | BB1FF650 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
833 | [27 empty] | Current | BB1FF650 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
834 |  | BB1 | EM | 652 | BB1EM652 | Rotating fuel spreader |  |  |  | 0.75 | 1.7 | 1500 | 415 | [26 empty] | 2 | [7 empty] | 2 | 1 | 1 | [13 empty] | 4010 | DOL_DIRH_BUS |  |  |  | Size, current and voltage | 1
835 | [27 empty] | Running | BB1SD650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIRH_BUS
836 | [27 empty] | MCC Fault | BB1SD650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIRH_BUS
837 | [27 empty] | Local run command | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
838 | [27 empty] | Local mode switch | BB1SD650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIRH_BUS
839 | [27 empty] | Run command | BB1SD650 | [19 empty] | X | [15 empty] | DOL_DIRH_BUS
840 | [27 empty] | Current | BB1SD650 | [20 empty] | X | [14 empty] | DOL_DIRH_BUS
841 |  | BB1 | EM | 662 | BB1EM662 | Fuel silo screw discharger |  |  |  | 22 | 39,5 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
842 | [27 empty] | Running FWD | BB1FD662 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
843 | [27 empty] | Running BWD | BB1FD662 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
844 | [27 empty] | MCC Fault | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
845 | [27 empty] | Safety switch | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
846 | [27 empty] | VFD Alarm | BB1FD662 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
847 | [27 empty] | Local FWD command | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
848 | [27 empty] | Local BWD command | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
849 | [27 empty] | Local mode switch | BB1FD662 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
850 | [27 empty] | Run command FWD | BB1FD662 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
851 | [27 empty] | Run command BWD | BB1FD662 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
852 | [27 empty] | Current | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
853 | [27 empty] | Speed reference | BB1FD662 | [21 empty] | X | [13 empty] | FRQ_REVH
854 | [27 empty] | Actual speed | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
855 | [27 empty] | Torque | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
856 | [27 empty] | RPM | BB1FD662 | [20 empty] | X | [14 empty] | FRQ_REVH
857 |  | BB1 | EM | 650 | BB1EM650 | Slewing motor for screw |  |  |  | 2.2 | 4.2 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
858 | [27 empty] | Running FWD | BB1EM650 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
859 | [27 empty] | Running BWD | BB1EM650 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
860 | [27 empty] | MCC Fault | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
861 | [27 empty] | Safety switch | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
862 | [27 empty] | VFD Alarm | BB1EM650 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
863 | [27 empty] | Local FWD command | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
864 | [27 empty] | Local BWD command | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
865 | [27 empty] | Local mode switch | BB1EM650 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
866 | [27 empty] | Run command FWD | BB1EM650 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
867 | [27 empty] | Run command BWD | BB1EM650 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
868 | [27 empty] | Current | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
869 | [27 empty] | Speed reference | BB1EM650 | [21 empty] | X | [13 empty] | FRQ_REVH
870 | [27 empty] | Actual speed | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
871 | [27 empty] | Torque | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
872 | [27 empty] | RPM | BB1EM650 | [20 empty] | X | [14 empty] | FRQ_REVH
873 |  | BB1 | EM | 660 | BB1EM660 | Cooling fan for slewing motor |  |  |  | 0.09 |  |  | 240 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor added | 1
874 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
875 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
876 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
877 |  | BB1 | EM | 654 | BB1EM654 | Lubrication unit |  | Fuse size C6A |  | 0.2 | 0.8 |  | 240 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Tag chanhed | 3
878 | [27 empty] | Running | BB1PU650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
879 | [27 empty] | MCC Fault | BB1PU650 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
880 | [27 empty] | Run command | BB1PU650 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
881 |  | BB1 | LS | 661 | BB1LS661 | Lubrication alarm screw discharger | [33 empty] | 1 | [19 empty] | SKF | KFGS | LAITEX |  | 4010 | MEAS_BIN |  | Field IO |  | Tag changed | 3
882 | [27 empty] | Binary state | BB1QA650 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
883 |  | BB1 | EH | 662 | BB1EH662 | Heater for slipring unit |  |  |  | 0.4 | 1.7 |  | 240 | [26 empty] | 1 | [23 empty] | 4010 | MCCB_1ph |  |  |  | Details | 1
884 |  | BB1 | EM | 663 | BB1EM663 | Fuel silo cross conveyor |  |  |  | 4 | 7.6 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
885 | [27 empty] | Running FWD | BB1FD663 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
886 | [27 empty] | Running BWD | BB1FD663 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
887 | [27 empty] | MCC Fault | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
888 | [27 empty] | Safety switch | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
889 | [27 empty] | VFD Alarm | BB1FD663 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
890 | [27 empty] | Local FWD command | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
891 | [27 empty] | Local BWD command | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
892 | [27 empty] | Local mode switch | BB1FD663 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
893 | [27 empty] | Run command FWD | BB1FD663 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
894 | [27 empty] | Run command BWD | BB1FD663 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
895 | [27 empty] | Current | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
896 | [27 empty] | Speed reference | BB1FD663 | [21 empty] | X | [13 empty] | FRQ_REVH
897 | [27 empty] | Actual speed | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
898 | [27 empty] | Torque | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
899 | [27 empty] | RPM | BB1FD663 | [20 empty] | X | [14 empty] | FRQ_REVH
900 |  | BB1 | EM | 664 | BB1EM664 | Fuel feeding screw 1 |  |  |  | 5.5 | 10 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
901 | [27 empty] | Running FWD | BB1FD664 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
902 | [27 empty] | Running BWD | BB1FD664 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
903 | [27 empty] | MCC Fault | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
904 | [27 empty] | Safety switch | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
905 | [27 empty] | VFD Alarm | BB1FD664 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
906 | [27 empty] | Local FWD command | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
907 | [27 empty] | Local BWD command | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
908 | [27 empty] | Local mode switch | BB1FD664 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
909 | [27 empty] | Run command FWD | BB1FD664 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
910 | [27 empty] | Run command BWD | BB1FD664 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
911 | [27 empty] | Current | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
912 | [27 empty] | Speed reference | BB1FD664 | [21 empty] | X | [13 empty] | FRQ_REVH
913 | [27 empty] | Actual speed | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
914 | [27 empty] | Torque | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
915 | [27 empty] | RPM | BB1FD664 | [20 empty] | X | [14 empty] | FRQ_REVH
916 |  | BB1 | EM | 653 | BB1EM653 | Cooling fan fuel feeding screw 1 |  |  |  | 0.15 | 0.33 |  | 415 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor details | 1
917 | [27 empty] | Running | BB1FF652 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
918 | [27 empty] | MCC Fault | BB1FF652 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
919 | [27 empty] | Run command | BB1FF652 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
920 |  | BB1 | EM | 665 | BB1EM665 | Fuel feeding screw 2 |  |  |  | 5.5 | 10 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4010 | FRQ_REVH |  |  |  | Motor details | 1
921 | [27 empty] | Running FWD | BB1FD665 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
922 | [27 empty] | Running BWD | BB1FD665 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
923 | [27 empty] | MCC Fault | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
924 | [27 empty] | Safety switch | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
925 | [27 empty] | VFD Alarm | BB1FD665 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
926 | [27 empty] | Local FWD command | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
927 | [27 empty] | Local BWD command | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
928 | [27 empty] | Local mode switch | BB1FD665 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
929 | [27 empty] | Run command FWD | BB1FD665 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
930 | [27 empty] | Run command BWD | BB1FD665 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
931 | [27 empty] | Current | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
932 | [27 empty] | Speed reference | BB1FD665 | [21 empty] | X | [13 empty] | FRQ_REVH
933 | [27 empty] | Actual speed | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
934 | [27 empty] | Torque | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
935 | [27 empty] | RPM | BB1FD665 | [20 empty] | X | [14 empty] | FRQ_REVH
936 |  | BB1 | EM | 655 | BB1EM655 | Cooling fan fuel feeding screw 2 |  |  |  | 0.15 | 0.33 |  | 415 | [26 empty] | 2 | 1 | [22 empty] | 4010 | DOL_DIR |  |  |  | Motor details | 1
937 | [27 empty] | Running | BB1FF654 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
938 | [27 empty] | MCC Fault | BB1FF654 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
939 | [27 empty] | Run command | BB1FF654 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
940 |  | BB1 | EM | 657 | BB1EM657 | Fuel feeding rotary valve 1 |  |  |  | 7.5 | 13.7 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor details | 1
941 | [27 empty] | Running FWD | BB1RV650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
942 | [27 empty] | Running BWD | BB1RV650 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
943 | [27 empty] | MCC Fault | BB1RV650 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
944 | [27 empty] | Local FWD command | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
945 | [27 empty] | Local BWD command | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
946 | [27 empty] | Local mode switch | BB1RV650 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
947 | [27 empty] | Run command FWD | BB1RV650 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
948 | [27 empty] | Run command BWD | BB1RV650 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
949 | [27 empty] | Current | BB1RV650 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
950 |  | BB1 | EM | 656 | BB1EM656 | Fuel feeding rotary valve 2 |  |  |  | 7.5 | 13.7 | 1500 | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4010 | DOL_REVH_BUS |  |  |  | Motor details | 1
951 | [27 empty] | Running FWD | BB1RV651 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
952 | [27 empty] | Running BWD | BB1RV651 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
953 | [27 empty] | MCC Fault | BB1RV651 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
954 | [27 empty] | Local FWD command | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
955 | [27 empty] | Local BWD command | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
956 | [27 empty] | Local mode switch | BB1RV651 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
957 | [27 empty] | Run command FWD | BB1RV651 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
958 | [27 empty] | Run command BWD | BB1RV651 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
959 | [27 empty] | Current | BB1RV651 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
960 |  | BB1 | GS | 802 | BB1GS802 | Bottom ash valve limit switch | [33 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | XS002/XS004 | Field IO
961 | [27 empty] | Binary state | BB1GS802 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
962 |  | BB1 | GS | 803 | BB1GS803 | Bottom ash dropping chute closing device limit switch | [33 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | XS002/XS004 | Field IO
963 | [27 empty] | Binary state | BB1GS803 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
964 |  | BB1 | LS | 852 | BB1LS852 | Fly ash container level switch |  | harting connector |  |  |  |  | 24 VDC | [26 empty] | 1 | [23 empty] | 4011 | MEAS_BIN | LS001 | Field IO
965 | [27 empty] | Binary state | BB1LS852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
966 |  | BB1 | PT | 552 | BB1PT552 | ESP inlet pressure transmitter |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA | PT002
967 | [27 empty] | Measurement | BB1PT552 | [12 empty] | X | [22 empty] | MEAS_ANA
968 |  | BB1 | PT | 553 | BB1PT553 | ESP outlet pressure transmitter |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA | PT002
969 | [27 empty] | Measurement | BB1PT553 | [12 empty] | X | [22 empty] | MEAS_ANA
970 |  | BB1 | QT | 554 | BB1QT554 | Opacity after ESP | [6 empty] | 24 VDC | [23 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | QT001 | Field IO
971 | [27 empty] | Measurement | BB1QT554 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
972 |  | BB1 | ST | 805 | BB1ST805 | Heated ESP collection screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
973 | [27 empty] | Binary state | BB1ST805 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
974 |  | BB1 | ST | 808 | BB1ST808 | ESP hopper 2 screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
975 | [27 empty] | Binary state | BB1ST808 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
976 |  | BB1 | ST | 809 | BB1ST809 | ESP hopper 1 screw rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
977 | [27 empty] | Binary state | BB1ST809 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
978 |  | BB1 | ST | 804 | BB1ST804 | ESP Rotary valve rotation guard |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS002
979 | [27 empty] | Binary state | BB1ST804 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
980 |  | BB1 | TT | 553 | BB1TT553 | Flue gas fan motor winding temperature 1 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
980 |  | BB1 | TT | 557 | BB1TT557 | Flue gas fan motor winding temperature 2 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO |  | signal added | 3
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
980 |  | BB1 | TT | 558 | BB1TT558 | Flue gas fan motor winding temperature 3 | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO |  | signal added | 3
981 | [27 empty] | Measurement | BB1TT553 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
982 |  | BB1 | TT | 554 | BB1TT554 | Flue gas fan bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
983 | [27 empty] | Measurement | BB1TT554 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
984 |  | BB1 | TT | 555 | BB1TT555 | Flue gas fan bearing temperature | [30 empty] | 0 | 200 | °C |  |  | 1 | [21 empty] | 4011 | MEAS_ANA | TT005 | Field IO
985 | [27 empty] | Measurement | BB1TT555 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
986 |  | BB1 | TT | 556 | BB1TT556 | Flue gas temperature before stack | [30 empty] | 0 | 400 | °C |  |  | 1 | [17 empty] | E+H | TR10-ABD3BHSFGC000 | G1/2 M / 250 mm |  | 4011 | MEAS_ANA | TT003 | Field IO
987 | [27 empty] | Measurement | BB1TT556 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
988 |  | BB1 | TT | 850 | BB1TT850 | ESP Ash hopper 1 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
989 | [27 empty] | Measurement | BB1TT850 | [12 empty] | X | [22 empty] | MEAS_ANA
990 |  | BB1 | TT | 851 | BB1TT851 | ESP Ash hopper 2 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
991 | [27 empty] | Measurement | BB1TT851 | [12 empty] | X | [22 empty] | MEAS_ANA
992 |  | BB1 | EH | 808 | BB1EH808 | ESP Ash hopper 2 heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
993 | [27 empty] | RCBO fault | BB1EH808 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
994 | [27 empty] | On command | BB1EH808 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
995 |  | BB1 | EH | 809 | BB1EH809 | ESP Ash hopper 1 heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
996 | [27 empty] | RCBO fault | BB1EH809 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
997 | [27 empty] | On command | BB1EH809 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
998 |  | BB1 | TS | 808 | BB1TS808 | ESP Ash hopper 2 overheat thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS001
999 | [27 empty] | Binary state | BB1TS808 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1000 |  | BB1 | TS | 809 | BB1TS809 | ESP Ash hopper 1 overheat thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN | XS001
1001 | [27 empty] | Binary state | BB1TS809 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1002 |  | BB1 | TS | 501 | BB1TS501 | ESP Insulator 1 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1003 | [27 empty] | Measurement | BB1TS501 | [12 empty] | X | [22 empty] | MEAS_ANA
1004 |  | BB1 | TS | 508 | BB1TS508 | ESP Insulator 2 temperature |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1005 | [27 empty] | Measurement | BB1TS508 | [12 empty] | X | [22 empty] | MEAS_ANA
1006 |  | BB1 | TT | 552 | BB1TT552 | Flue gas temperature before ESP |  | IS PLC |  |  | IS PLC | [30 empty] | 1 | [20 empty] | IS SaveEnergy | 4011 | MEAS_ANA
1007 | [27 empty] | Measurement | BB1TT552 | [12 empty] | X | [22 empty] | MEAS_ANA
1008 |  | BB1 | EM | 509 | BB1EM509 | ESP DE rapping drive 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1009 | [27 empty] | Running | BB1EM509 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1010 | [27 empty] | MCC Fault | BB1EM509 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1011 | [27 empty] | Run command | BB1EM509 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1012 |  | BB1 | EM | 510 | BB1EM510 | ESP CE rapping drive 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1013 | [27 empty] | Running | BB1EM510 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1014 | [27 empty] | MCC Fault | BB1EM510 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1015 | [27 empty] | Run command | BB1EM510 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1016 |  | BB1 | EM | 511 | BB1EM511 | ESP DE rapping drive 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1017 | [27 empty] | Running | BB1EM511 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1018 | [27 empty] | MCC Fault | BB1EM511 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1019 | [27 empty] | Run command | BB1EM511 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1020 |  | BB1 | EM | 512 | BB1EM512 | ESP CE rapping drive 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1021 | [27 empty] | Running | BB1EM512 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1022 | [27 empty] | MCC Fault | BB1EM512 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1023 | [27 empty] | Run command | BB1EM512 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1024 |  | BB1 | EH | 501 | BB1EH501 | ESP insulators heating chamber 1 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1025 | [27 empty] | Running | BB1EH501 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1026 | [27 empty] | MCC Fault | BB1EH501 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1027 | [27 empty] | Run command | BB1EH501 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1028 |  | BB1 | EH | 505 | BB1EH505 | ESP insulators heating chamber 2 |  | Supply from ESP MCC | [31 empty] | 2 | 1 | [22 empty] | 4011 | DOL_DIR
1029 | [27 empty] | Running | BB1EH505 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_DIR
1030 | [27 empty] | MCC Fault | BB1EH505 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_DIR
1031 | [27 empty] | Run command | BB1EH505 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_DIR
1032 |  | BB1 | IE | 501 | BB1IE501 | ESP HV Trafo 1 |  | Supply from ESP MCC | [55 empty] | 4011 | OESA_3ph
1033 |  | BB1 | IE | 502 | BB1IE502 | ESP HV Trafo 2 |  | Supply from ESP MCC | [55 empty] | 4011 | OESA_3ph
1034 |  | BB1 | FG | 300 | BB1FG300 | ESP hardwired signals to/from Boiler PLC | [33 empty] | 8 | 6 | [22 empty] | 4011 | ESP_DI_DO
1035 | [27 empty] | Collective Alarm | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1036 | [27 empty] | Collective Warning | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1037 | [27 empty] | ESP in Standby | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1038 | [27 empty] | ESP in Operation | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1039 | [27 empty] | ESP spare DI1 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1040 | [27 empty] | ESP spare DI2 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1041 | [27 empty] | ESP spare DI3 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1042 | [27 empty] | ESP spare DI4 | BB1FG300 | [10 empty] | X | [24 empty] | ESP_DI_DO
1043 | [27 empty] | ESP External release filter | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1044 | [27 empty] | ESP spare DO1 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1045 | [27 empty] | ESP spare DO2 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1046 | [27 empty] | ESP spare DO3 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1047 | [27 empty] | ESP spare DO4 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1048 | [27 empty] | ESP spare DO5 | BB1FG300 | [11 empty] | X | [23 empty] | ESP_DI_DO
1049 |  | BB1 | EM | 809 | BB1EM809 | ESP ash hopper 1 screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1050 | [27 empty] | Running FWD | BB1EM809 | [10 empty] | X | [24 empty] | DOL_REVH
1051 | [27 empty] | Running BWD | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1052 | [27 empty] | MCC Fault | BB1EM809 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1053 | [27 empty] | Local FWD command | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1054 | [27 empty] | Local BWD command | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1055 | [27 empty] | Local mode switch | BB1EM809 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1056 | [27 empty] | Run command FWD | BB1EM809 | [11 empty] | X | [23 empty] | DOL_REVH
1057 | [27 empty] | Run command BWD | BB1EM809 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1058 |  | BB1 | EM | 808 | BB1EM808 | ESP ash hopper 2 screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1059 | [27 empty] | Running FWD | BB1EM808 | [10 empty] | X | [24 empty] | DOL_REVH
1060 | [27 empty] | Running BWD | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1061 | [27 empty] | MCC Fault | BB1EM808 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1062 | [27 empty] | Local FWD command | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1063 | [27 empty] | Local BWD command | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1064 | [27 empty] | Local mode switch | BB1EM808 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1065 | [27 empty] | Run command FWD | BB1EM808 | [11 empty] | X | [23 empty] | DOL_REVH
1066 | [27 empty] | Run command BWD | BB1EM808 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1067 |  | BB1 | EM | 805 | BB1EM805 | ESP collection screw |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1068 | [27 empty] | Running FWD | BB1EM805 | [10 empty] | X | [24 empty] | DOL_REVH
1069 | [27 empty] | Running BWD | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1070 | [27 empty] | MCC Fault | BB1EM805 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1071 | [27 empty] | Local FWD command | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1072 | [27 empty] | Local BWD command | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1073 | [27 empty] | Local mode switch | BB1EM805 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1074 | [27 empty] | Run command FWD | BB1EM805 | [11 empty] | X | [23 empty] | DOL_REVH
1075 | [27 empty] | Run command BWD | BB1EM805 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1076 |  | BB1 | EH | 805 | BB1EH805 | ESP collection screw heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1077 | [27 empty] | RCBO fault | BB1EH805 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1078 | [27 empty] | On command | BB1EH805 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1079 |  | BB1 | TS | 805 | BB1TS805 | ESP collection screw heating thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN
1080 | [27 empty] | Binary state | BB1TS805 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1081 |  | BB1 | EM | 804 | BB1EM804 | ESP Rotary valve |  | Supply from ESP MCC | [31 empty] | 6 | 2 | [22 empty] | 4011 | DOL_REVH
1082 | [27 empty] | Running FWD | BB1EM804 | [10 empty] | X | [24 empty] | DOL_REVH
1083 | [27 empty] | Running BWD | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1084 | [27 empty] | MCC Fault | BB1EM804 | [10 empty] | X | [17 empty] | NC | [6 empty] | DOL_REVH
1085 | [27 empty] | Local FWD command | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1086 | [27 empty] | Local BWD command | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1087 | [27 empty] | Local mode switch | BB1EM804 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH
1088 | [27 empty] | Run command FWD | BB1EM804 | [11 empty] | X | [23 empty] | DOL_REVH
1089 | [27 empty] | Run command BWD | BB1EM804 | [11 empty] | X | [16 empty] | NO | [6 empty] | DOL_REVH
1090 |  | BB1 | EH | 804 | BB1EH804 | ESP Rotary valve heater |  | Supply from ESP MCC | [31 empty] | 1 | 1 | [22 empty] | 4011 | RCBO_3ph_CTRL
1091 | [27 empty] | RCBO fault | BB1EH804 | [10 empty] | X | [17 empty] | NC | [6 empty] | RCBO_3ph_CTRL
1092 | [27 empty] | On command | BB1EH804 | [11 empty] | X | [23 empty] | RCBO_3ph_CTRL
1093 |  | BB1 | TS | 804 | BB1TS804 | ESP Rotary valve heating thermostat |  | IS PLC |  |  | IS PLC | [28 empty] | 1 | [22 empty] | IS SaveEnergy | 4011 | MEAS_BIN
1094 | [27 empty] | Binary state | BB1TS804 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN
1095 |  | BB1 | EM | 815 | BB1EM815 | Fly ash container screw | [41 empty] | 3 | 2 | 1 | [13 empty] | 4011 | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1221 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1222 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1224 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1225 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS |  |  |  | Motor feed type changed | 2
1101 |  | BB1 | EM | 550 | BB1EM550 | Flue gas fan |  |  |  | 75 |  |  | 415 | [34 empty] | 4 | 1 | 4 | 1 | [11 empty] | Flebu/ABB | 4011 | FRQ_DIR |  |  |  | Size and voltage | 1
1102 | [27 empty] | Running | BB1FF550 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_DIR
1103 | [27 empty] | MCC Fault | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1104 | [27 empty] | Safety switch | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1105 | [27 empty] | VFD Alarm | BB1FF550 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_DIR
1106 | [27 empty] | Run command | BB1FF550 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_DIR
1107 | [27 empty] | Current | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1108 | [27 empty] | Speed reference | BB1FF550 | [21 empty] | X | [13 empty] | FRQ_DIR
1109 | [27 empty] | Actual speed | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1110 | [27 empty] | Torque | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1111 | [27 empty] | RPM | BB1FF550 | [20 empty] | X | [14 empty] | FRQ_DIR
1112 |  | BB1 | SI | 550 | BB1SI550 | Flue gas fan safety interlock | [38 empty] | 1 | [18 empty] | 4011 | FAN_SRS_DO
1113 | [27 empty] | Safety interlock | BB1SI550 | [15 empty] | X | [19 empty] | FAN_SRS_DO
458 |  | BB1 | SI | 560 | BB1SI560 | Flue gas fan run status SRS | [37 empty] | 1 | [19 empty] | 4011 |  |  | MCC |  | Signal added | 2
459 | [27 empty] | Run status SRS | BB1SI401 | [14 empty] | X | [22 empty] | MCC |  | Signal added | 2
458 |  | BB1 | ST | 550 | BB1ST550 | Flue gas fan rotation guard | [33 empty] | 1 | [16 empty] | 3-wire |  | 24 VDC | Telemechanique | XSAV12373 |  |  | 4008 |  |  | Field IO |  | Signal added | 3
459 | [27 empty] | Rotation guard | BB1SI401 | [10 empty] | X | [26 empty] | Field IO |  | Signal added | 3
458 |  | BB1 |  |  | BB1 | Flue gas fan heating |  | RCBO + Contactor |  |  |  |  | 240 | [27 empty] | 1 | [22 empty] | 4011 |  |  |  |  | Heater added | 3
459 | [27 empty] | Heater On control | BB1SI401 | [11 empty] | X | [27 empty] | Heater added | 3
1114 |  | BB1 | CV | 405 | BB1CV405 | Bottom ash valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1115 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV405 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1116 |  | BB1 | GS | 855 | BB1GS855 | Bottom ash valve solenoid valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1117 | [27 empty] | Binary state | BB1GS855 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1118 |  | BB1 | GS | 856 | BB1GS856 | Bottom ash valve solenoid valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1119 | [27 empty] | Binary state | BB1GS856 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1120 |  | BB1 | CV | 406 | BB1CV406 | Bottom ash valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1121 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV406 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1122 |  | BB1 | GS | 857 | BB1GS857 | Bottom ash valve solenoid valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1123 | [27 empty] | Binary state | BB1GS857 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1124 |  | BB1 | GS | 858 | BB1GS858 | Bottom ash valve solenoid valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1125 | [27 empty] | Binary state | BB1GS858 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1126 |  | BB1 | CV | 412 | BB1CV412 | Bottom ash sieve bypass solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [17 empty] | 24 VDC | SMC |  |  |  | 4012 | BIN_VLV | AA003 | Field IO |  | Details added | 1
1127 | [7 empty] | own 24 VDC fuse | [19 empty] | Control command | BB1CV412 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO |  | Details added | 1
1128 |  | BB1 | GS | 850 | BB1GS850 | Bottom ash sieve bypass valve close limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1129 | [27 empty] | Binary state | BB1GS850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1130 |  | BB1 | GS | 851 | BB1GS851 | Bottom ash sieve bypass valve open limit switch | [33 empty] | 1 | [16 empty] | 2-wire |  |  | SMC | D-A93L |  |  | 4012 | MEAS_BIN |  | Field IO |  | Instrument type added | 1
1131 | [27 empty] | Binary state | BB1GS851 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1132 |  | BB1 | CV | 413 | BB1CV413 | Control valve of pneumatic transmitter damper |  | Pneuplan PLC |  |  | Pneuplan PLC |  | 24 | [27 empty] | 2 | [21 empty] | Pneuplan | 4012 | BIN_VLV_2DO | AA004 | Field IO
1133 | [27 empty] | Open command | BB1CV413 | [11 empty] | X | [23 empty] | BIN_VLV_2DO |  | Field IO
1134 | [27 empty] | Close command | BB1CV413 | [11 empty] | X | [23 empty] | BIN_VLV_2DO |  | Field IO
1135 |  | BB1 | CV | 414 | BB1CV414 | Work air to pneumatic transmitter pneumatic valve |  | Pneuplan PLC |  |  | Pneuplan PLC |  | 24 | [27 empty] | 1 | [21 empty] | Pneuplan | 4012 | BIN_VLV | AA004 | Field IO
1136 | [27 empty] | Control command | BB1CV414 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1137 |  | BB1 | FS | 003 | BB1FS003 | Bottom ash cooling flow switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | FS001 | Field IO
1138 | [27 empty] | Binary state | BB1FS003 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1139 |  | BB1 | SV | 405 | BB1SV405 | Sand filling valve solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA003 | Field IO
1140 | [27 empty] | Control command | BB1SV405 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1141 |  | BB1 | GS | 801 | BB1GS801 | Sand filling valve position open limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | AA005 | Field IO
1142 | [27 empty] | Binary state | BB1GS801 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1143 |  | BB1 | GS | 800 | BB1GS800 | Sand filling valve position close limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS001 | Field IO
1144 | [27 empty] | Binary state | BB1GS800 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1145 |  | BB1 | GS | 854 | BB1GS854 | Bottom ash dropping chute limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO |  | Tag changed | 3
1146 | [27 empty] | Binary state | BB1GS852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1147 |  | BB1 | GS | 853 | BB1GS853 | Bottom ash dropping chute closing device limit switch | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO
1148 | [27 empty] | Binary state | BB1GS853 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1149 |  | BB1 | GS | 859 | BB1GS859 | Bottom ash to container in place |  | Harting connector (jumper in container side..> DI=1 connector in place) | [31 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002/XS004 | Field IO |  | Tag changed | 3
1150 | [27 empty] | Binary state | BB1GS854 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1151 |  | BB1 | LS | 850 | BB1LS850 | Bottom ash container level switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | LS001 | Field IO
1152 | [27 empty] | Binary state | BB1LS850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1153 |  | BB1 | LS | 851 | BB1LS851 | Bottom ash container level switch | [6 empty] | 24 VDC | [26 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | LS001 | Field IO
1154 | [27 empty] | Binary state | BB1LS851 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1155 |  | BB1 | LT | 800 | BB1LT800 | Recycled bed material hopper level switch |  | Pneuplan PLC |  |  | Pneuplan PLC | [30 empty] | 1 | [20 empty] | Pneuplan | 4012 | MEAS_ANA |  | Field IO
1156 | [27 empty] | Measurement | BB1LT800 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1157 |  | BB1 | LT | 802 | BB1LT802 | Sand silo level measurement | [6 empty] | 24 VDC | [23 empty] | 0 | 100 | % |  |  | 1 | [21 empty] | 4012 | MEAS_ANA | LT003 | Field IO
1158 | [27 empty] | Measurement | BB1LT802 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1159 |  | BB1 | PT | 009 | BB1PT009 | Cooling water pressure before pump | [30 empty] | 0 | 6 | bar(g) |  |  | 1 | [13 empty] | Pressure |  |  |  | E+H | PMP51-AA22IA1PGJGCJA1+Z1 | G1/2 |  | 4012 | MEAS_ANA | PT001.1 | Field IO
1160 | [27 empty] | Measurement | BB1PT009 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1161 |  | BB1 | PT | 800 | BB1PT800 | Recycled bed material damper pressure switch |  | Pneuplan PLC |  |  | Pneuplan PLC | [28 empty] | 1 | [22 empty] | Pneuplan | 4012 | MEAS_BIN |  | Field IO
1162 | [27 empty] | Binary state | BB1PT800 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1153 |  | BB1 | EM | 856 | BB1EM856 | Purified sand screw conveyor | [33 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor added | 2
1154 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1155 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1156 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1157 | [27 empty] | Local FWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1158 | [27 empty] | Local BWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1159 | [27 empty] | Local mode switch | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1160 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1161 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1162 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REVH_BUS |  |  |  | Motor added | 2
1151 |  | BB1 | ST | 856 | BB1ST856 | Purified sand screw conveyor rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument added | 2
1152 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO |  | Instrument added | 2
1163 |  | BB1 | EM | 852 | BB1EM852 | Bottom ash conveyor |  |  |  | 2.2 | 4.2 | 1500 | 415 |  | X | [24 empty] | 3 | [7 empty] | 5 | 2 | 4 | 1 | [12 empty] | 4012 | FRQ_REVH |  |  |  | Tag changed | 2
1164 | [27 empty] | Running FWD | BB1EM850 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1165 | [27 empty] | Running BWD | BB1EM850 | [18 empty] | X | [9 empty] | NO | [6 empty] | FRQ_REVH
1166 | [27 empty] | MCC Fault | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1167 | [27 empty] | Safety switch | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
1168 | [27 empty] | VFD Alarm | BB1EM850 | [18 empty] | X | [9 empty] | NC | [6 empty] | FRQ_REVH
[28 empty] | Thermistor fault | [19 empty] | X | [16 empty] | FRQ_REVH |  |  |  | Thermistor fault added | 2
1169 | [27 empty] | Local FWD command | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1170 | [27 empty] | Local BWD command | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1171 | [27 empty] | Local mode switch | BB1EM850 | [10 empty] | X | [17 empty] | NO | [6 empty] | FRQ_REVH
1172 | [27 empty] | Run command FWD | BB1EM850 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1173 | [27 empty] | Run command BWD | BB1EM850 | [19 empty] | X | [8 empty] | NO | [6 empty] | FRQ_REVH
1174 | [27 empty] | Current | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1175 | [27 empty] | Speed reference | BB1EM850 | [21 empty] | X | [13 empty] | FRQ_REVH
1176 | [27 empty] | Actual speed | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1177 | [27 empty] | Torque | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1178 | [27 empty] | RPM | BB1EM850 | [20 empty] | X | [14 empty] | FRQ_REVH
1179 |  | BB1 | ST | 850 | BB1ST850 | Bottom ash conveyor rotation guard | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemecanique | XSAV-11801 |  |  | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument type added | 1
1180 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1179 |  | BB1 | GS | 852 | BB1GS852 | Bottom ash conveyor blockage detector | [33 empty] | 1 | [16 empty] | 2-wire |  |  | Telemecanique | XS530B1MAL2 |  |  | 4012 | MEAS_BIN | XS002 | Field IO |  | Instrument added | 1
1180 | [27 empty] | Binary state | BB1ST850 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
741 |  | BB1 | IJ | 004 | BB1IJ004 | Bottom ash conveyor Alarm horn and lamp | [34 empty] | 1 | [22 empty] | 4012 | ALM_HORN |  | Field IO |  | Instrument added | 2
742 | [27 empty] | Command | BB1IJ001 | [11 empty] | X | [23 empty] | ALM_HORN |  | Field IO
1181 |  | BB1 | EM | 850 | BB1EM850 | 2nd pass fly ash rotary valve |  |  |  |  | 0,37 |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor details | 1
1182 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1183 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1184 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1185 | [27 empty] | Local FWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1186 | [27 empty] | Local BWD command | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1187 | [27 empty] | Local mode switch | BB1EM??? | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1188 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1189 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1190 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1191 |  | BB1 | ST | 852 | BB1ST852 | 2nd pass fly ash rotary valve rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO
1192 | [27 empty] | Binary state | BB1ST852 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1193 |  | BB1 | EM | 851 | BB1EM851 | 3rd pass fly ash rotary valve |  |  |  |  | 0,37 |  | 415 | [26 empty] | 3 | [7 empty] | 3 | 2 | 1 | [13 empty] | 4012 | DOL_REVH_BUS |  |  |  | Motor details | 1
1194 | [27 empty] | Running FWD | BB1EM851 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1195 | [27 empty] | Running BWD | BB1EM851 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REVH_BUS
1196 | [27 empty] | MCC Fault | BB1EM851 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REVH_BUS
1197 | [27 empty] | Local FWD command | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1198 | [27 empty] | Local BWD command | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1199 | [27 empty] | Local mode switch | BB1EM851 | [10 empty] | X | [17 empty] | NO | [6 empty] | DOL_REVH_BUS
1200 | [27 empty] | Run command FWD | BB1EM851 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1201 | [27 empty] | Run command BWD | BB1EM851 | [19 empty] | X | [15 empty] | DOL_REVH_BUS
1202 | [27 empty] | Current | BB1EM851 | [20 empty] | X | [14 empty] | DOL_REVH_BUS
1203 |  | BB1 | ST | 853 | BB1ST853 | 3rd pass fly ash rotary valve rotation guard | [33 empty] | 1 | [23 empty] | 4012 | MEAS_BIN | XS002 | Field IO
1204 | [27 empty] | Binary state | BB1ST853 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1205 |  | BB1 | SV | 401 | BB1SV401 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA005 | Field IO
1206 | [27 empty] | Control command | BB1SV401 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1207 |  | BB1 | SV | 402 | BB1SV402 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 1 | [22 empty] | 4012 | BIN_VLV | AA005 | Field IO
1208 | [27 empty] | Control command | BB1SV402 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  | Field IO
1209 |  | BB1 | SV | 403 | BB1SV403 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 0 | [22 empty] | 4012 | BIN_VLV | AA005 |  |  | Removed | 1
1210 | [27 empty] | Control command | BB1SV403 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  |  |  | Removed | 1
1211 |  | BB1 | SV | 404 | BB1SV404 | Bottom ash purging air solenoid valve | [6 empty] | 24 | [27 empty] | 0 | [22 empty] | 4012 | BIN_VLV | AA005 |  |  | Removed | 1
1212 | [27 empty] | Control command | BB1SV404 | [11 empty] | X | [16 empty] | NO | [6 empty] | BIN_VLV |  |  |  | Removed | 1
1213 |  | BB1 | TT | 031 | BB1TT031 | Cooling water temperature after bottom ash conveyor | [30 empty] | 0 | 150 | °C |  |  | 1 | [17 empty] | E+H | TR15-A1B181J0G3000 | D4 |  | 4012 | MEAS_ANA | TT001 | Field IO
1214 | [27 empty] | Measurement | BB1TT031 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1215 |  | BB1 | EM | 014 | BB1EM008 | Conveyor cooling pump |  |  |  | 1,1 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [12 empty] | Grundfos | 4012 | DOL_DIR_BUS |  |  |  | Motor size changed | 3
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1220 |  | BB1 | EM | 855 | BB1EM855 | Ash container screw |  |  |  | 1,5 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4012 | DOL_REV_BUS |  |  |  | Motor details | 1
1221 | [27 empty] | Running FWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1222 | [27 empty] | Running BWD | BB1EM??? | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1223 | [27 empty] | MCC Fault | BB1EM??? | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1224 | [27 empty] | Run command FWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS
1225 | [27 empty] | Run command BWD | BB1EM??? | [19 empty] | X | [15 empty] | DOL_REV_BUS
1226 | [27 empty] | Current | BB1EM??? | [20 empty] | X | [14 empty] | DOL_REV_BUS
1227 |  | BB1 | EM | 018 | BB1EM009 | Bottom ash conveyor heat exchanger fan |  | preliminary 6x0,72 kW, 1.42 A |  | 7,5 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4012 | DOL_DIR_BUS |  |  |  | Tag changed | 2
1228 | [27 empty] | Running | BB1FF009 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1229 | [27 empty] | MCC Fault | BB1FF009 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1230 | [27 empty] | Run command | BB1FF009 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1231 | [27 empty] | Current | BB1FF009 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1232 |  | BB1 | FM | 001 | BB1FM001 | Bottom ash sieve feed |  | supply fuse 16A |  | 1,4 |  |  | 415 | [26 empty] | 5 | 1 | [22 empty] | 4012 | OESA_3ph |  |  |  | Details | 1
1236 | [27 empty] | Emergency stop | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1237 | [7 empty] | ask preliminary drawings from KPA | [19 empty] | Running | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
[28 empty] | manual/auto | [11 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1238 | [27 empty] | Thermistor fault | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1239 | [27 empty] | Voltage OK | BB1BU500 | [10 empty] | X | [24 empty] | OESA_3ph |  |  |  | signals added | 1
1241 | [27 empty] | Start/stop | BB1BU500 | [11 empty] | X | [16 empty] | pot.free | [6 empty] | OESA_3ph |  |  |  | signals added | 1
1233 |  | BB1 | HC | 601 | BB1HC601 | Electrical hoist feed |  |  |  |  | 2,8 |  | 415 | [50 empty] | 4012 | OESA_3ph
1234 |  | BB1 | TN | ??? | BB1TN??? | Sand transmitter 230 Vac feed | [33 empty] | 1 | [23 empty] | 4012 | MCCB_1ph
1235 |  | BB1 | BU | 500 | BB1BU500 | Burner signals | [33 empty] | 5 | 5 | 2 | 2 |  |  |  |  | 6 | 5 | 2 | 2 | [12 empty] | 4013 | BURNER
1236 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1237 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1238 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1239 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1240 | [27 empty] | DI reservation | BB1BU500 | [10 empty] | X | [24 empty] | BURNER
1241 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1242 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1243 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1244 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1245 | [27 empty] | DO reservation | BB1BU500 | [11 empty] | X | [23 empty] | BURNER
1246 | [27 empty] | AI reservation | BB1BU500 | [12 empty] | X | [22 empty] | BURNER
1247 | [27 empty] | AI reservation | BB1BU500 | [12 empty] | X | [22 empty] | BURNER
1248 | [27 empty] | AO reservation | BB1BU500 | [13 empty] | X | [21 empty] | BURNER
1249 | [27 empty] | AO reservation | BB1BU500 | [13 empty] | X | [21 empty] | BURNER
1250 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1251 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1252 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1253 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1254 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1255 | [27 empty] | BUS DI reservation | BB1BU500 | [18 empty] | X | [16 empty] | BURNER
1256 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1257 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1258 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1259 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1260 | [27 empty] | BUS DO reservation | BB1BU500 | [19 empty] | X | [15 empty] | BURNER
1261 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1262 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1263 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1264 | [27 empty] | BUS AI reservation | BB1BU500 | [20 empty] | X | [14 empty] | BURNER
1265 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1266 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1267 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1268 | [27 empty] | BUS AO reservation | BB1BU500 | [21 empty] | X | [13 empty] | BURNER
1269 |  | BB1 | EM | 402 | BB1EM402 | Compressor 1 |  | Preliminary size |  | 30 |  |  | 415 | [26 empty] | 3 | 2 | [22 empty] | 4014 | COMPR |  | Field IO |  | Motor size and tag changed | 3
1270 | [27 empty] | Fault | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1271 | [27 empty] | Running | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1272 | [27 empty] | Reserve | BB1EM400 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1273 | [27 empty] | Remote run command | BB1EM400 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1274 | [27 empty] | Fault acknowledge | BB1EM400 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1275 |  | BB1 | EM | 403 | BB1EM403 | Compressor 2 |  | Preliminary size |  | 30 |  |  | 415 | [26 empty] | 3 | 2 | [22 empty] | 4014 | COMPR |  | Field IO |  | Motor size and tag changed | 3
1276 | [27 empty] | Fault | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1277 | [27 empty] | Running | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1278 | [27 empty] | Reserve | BB1EM402 | [10 empty] | X | [24 empty] | COMPR |  | Field IO
1279 | [27 empty] | Remote run command | BB1EM402 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1280 | [27 empty] | Fault acknowledge | BB1EM402 | [11 empty] | X | [23 empty] | COMPR |  | Field IO
1281 |  | BB1 | DR | 400 | BB1DR400 | Compressor 1 dryer |  |  |  | 4 |  |  | 415 | [26 empty] | 1 | [23 empty] | 4014 | MCCB_1ph |  |  |  | motor details | 1
1282 |  | BB1 | DR | 401 | BB1DR401 | Compressor 2 dryer |  |  |  | 4 |  |  | 415 | [26 empty] | 1 | [23 empty] | 4014 | MCCB_1ph |  |  |  | motor details | 1
1283 |  | BB1 | PT | 478 | BB1PT478 | Instrument air pressure | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4014 | MEAS_ANA | PT002 | Field IO
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1283 |  | BB1 | PT | 402 | BB1PT402 | Instrument air pressure after dryer | [30 empty] | 0 | 10 | bar(g) |  |  | 1 | [17 empty] | E+H | PMP51-AA22IA1PGBGCJA1+Z1 | G1/2 |  | 4014 | MEAS_ANA | PT002 | Field IO |  | Instrument added | 3
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
1283 |  | BB1 | TT | 430 | BB1TT430 | Instrument air tank temperature | [30 empty] | 0 | 100 | °C |  |  | 1 | [19 empty] | G1/2 |  | 4014 | MEAS_ANA | TT003 | Field IO |  | Instrument added | 3
1284 | [27 empty] | Measurement | BB1PT478 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO |  | Instrument added | 3
1285 |  | BB1 | GS | 020 | BB1GS020 | Emergency shower use switch | [33 empty] | 1 | [23 empty] | 4014 | MEAS_BIN | XS001 | Field IO
1286 | [27 empty] | Binary state | BB1GS020 | [10 empty] | X | [17 empty] | NC/NO | [6 empty] | MEAS_BIN |  | Field IO
1287 |  | BB1 | TT | 401 | BB1TT401 | Boiler room upper part temperature | [35 empty] | 1 | [17 empty] | E+H | TST434-J1A3BP | Wall mount |  | 4014 | MEAS_ANA | TT007 | Field IO
1288 | [27 empty] | Measurement | BB1TT401 | [12 empty] | X | [22 empty] | MEAS_ANA |  | Field IO
1289 |  | BB1 | EM | 401 | BB1EM401 | Exhaust fan 1 |  |  |  | 1,9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1290 | [27 empty] | Running FWD | BB1EM401 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1291 | [27 empty] | Running BWD | BB1EM401 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1292 | [27 empty] | MCC Fault | BB1EM401 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1293 | [27 empty] | Run command FWD | BB1EM401 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1294 | [27 empty] | Run command BWD | BB1EM401 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1295 | [27 empty] | Current | BB1EM401 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1296 |  | BB1 | EM | 402 | BB1EM402 | Exhaust fan 2 |  |  |  | 1,9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1297 | [27 empty] | Running FWD | BB1EM402 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1298 | [27 empty] | Running BWD | BB1EM402 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1299 | [27 empty] | MCC Fault | BB1EM402 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1300 | [27 empty] | Run command FWD | BB1EM402 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1301 | [27 empty] | Run command BWD | BB1EM402 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1302 | [27 empty] | Current | BB1EM402 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1303 |  | BB1 | EM | 403 | BB1EM403 | Exhaust fan 3 |  |  |  | 1,9 |  |  | 415 | [34 empty] | 5 | 2 | 1 | [13 empty] | 4014 | DOL_REV_BUS |  |  |  | motor details | 1
1304 | [27 empty] | Running FWD | BB1EM403 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1305 | [27 empty] | Running BWD | BB1EM403 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_REV_BUS
1306 | [27 empty] | MCC Fault | BB1EM403 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_REV_BUS
1307 | [27 empty] | Run command FWD | BB1EM403 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1308 | [27 empty] | Run command BWD | BB1EM403 | [19 empty] | X | [15 empty] | DOL_REV_BUS
1309 | [27 empty] | Current | BB1EM403 | [20 empty] | X | [14 empty] | DOL_REV_BUS
1310 |  | BB1 | EM | 405 | BB1EM405 | Air intake grill 1 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1311 |  |  |  |  | BB1GS401 | [22 empty] | Open limit switch | BB1EM405 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1312 | [27 empty] | Open command | BB1EM405 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1313 |  | BB1 | EM | 406 | BB1EM406 | Air intake grill 2 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1314 |  |  |  |  | BB1GS412 | [22 empty] | Open limit switch | BB1EM406 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1315 | [27 empty] | Open command | BB1EM406 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1316 |  | BB1 | EM | 407 | BB1EM407 | Air intake grill 3 | [33 empty] | 1 | 1 | [17 empty] | 24 VDC |  |  |  |  | 4014 | BELIMO_VLV |  | Field IO |  | Voltage added | 3
1317 |  |  |  |  | BB1GS413 | [22 empty] | Open limit switch | BB1EM407 | [10 empty] | X | [24 empty] | BELIMO_VLV |  | Field IO |  | Separate tag added | 3
1318 | [27 empty] | Open command | BB1EM407 | [11 empty] | X | [23 empty] | BELIMO_VLV |  | Field IO
1319 |  | BB1 | EM | 408 | BB1EM408 | Boiler house heater 1 |  |  |  | 15 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4014 | DOL_DIR_BUS |  |  |  | Motor feed type changed | 2
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
1323 |  | BB1 | EM | 409 | BB1EM409 | Boiler house heater 2 |  |  |  | 15 |  |  | 415 | [34 empty] | 2 | 1 | 1 | [13 empty] | 4014 | DOL_DIR_BUS |  |  |  | Motor feed type changed | 2
1216 | [27 empty] | Running | BB1PU008 | [18 empty] | X | [9 empty] | NO | [6 empty] | DOL_DIR_BUS
1217 | [27 empty] | MCC Fault | BB1PU008 | [18 empty] | X | [9 empty] | NC | [6 empty] | DOL_DIR_BUS
1218 | [27 empty] | Run command | BB1PU008 | [19 empty] | X | [15 empty] | DOL_DIR_BUS
1219 | [27 empty] | Current | BB1PU008 | [20 empty] | X | [14 empty] | DOL_DIR_BUS
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.
This shape represents a table slicer. Table slicers are not supported in this version of Excel. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2007 or earlier, the slicer can't be used.

## _Parameters
Parameter | Value
jobNumber | 38025
dwgCategory | ELE
protoPath | S:\Elecdes\prototypes\v6\INSTRUMENTATION\